Sizing Exhaust Fan for Electrical Equipment Rooms

- If an electrical equipment room has a transformer in it, then the room must either have an exhaust fan sized to dissipate the heat from the transformer, or the roommust be cooled by an AC only unit.

- 2. A heat pump or gas packaged unit cannot be used to cool the room, since in thewinter the unit would heat the room instead of cooling it.

- 3. The first step in designing the electrical room cooling system is to determine theheat generated by the transformer. The simplest method is to use the followingtable:

TRANSFORMER SIZE 		HEAT GENERATED

150 kva & smaller				50 watts/kva

151  –  500 kva				30 watts/kva

501  -  1000 kva				25 watts/kva

1001  --  2500 kva				20 watts/kva

Larger than 2500 kva			15 watts/kva

- For example: A 75 KVA transformer would give off 50 watts/KVA x 75 KVA =3750 watts

- Converting watts to BTU/hr, multiply by 3.4123750 watts x 3.412 = 12,795 BTU/hr

- Thus, 12,795 BTU/hr is the “sensible” cooling load.

- In the above example a 1 ½ ton AC unit could be used to cool the electrical room.

- However, in most cases an exhaust fan would be used in lieu of an AC unit(assuming the room is unoccupied).

- The exhaust fan is sized using the sensible heat equation: Q = 1.08 (CFM) (TC)

- In the above example, Q = 12,795 BTU/hr, TC = the temperature change of the air in the room, and CFM = the exhaust fan airflow.

- Generally, electrical equipment rooms only require ventilation to keep equipment from overheating (i.e., not for human comfort). Accordingly, electrical rooms are designed for 95 degrees Fahrenheit to 104 degrees Fahrenheit. If space temperatures below 90 degrees Fahrenheit are required by equipment, then the space will need to be air-conditioned.

- If outside air is used to ventilate the electrical room, design temperature in the room will be 10 – 15 degrees Fahrenheit above the outside design temperature.

- In Phoenix, using outside air to cool electrical rooms is generally not a good idea unless it is confirmed that the electrical equipment can operate at 125 degrees Fahrenheit. If the equipment can operate at 125 degrees Fahrenheit, then TC = 10degrees Fahrenheit, (125 – 115). Solving the sensible heat equation for CFMCFM = Q/(1.08 x TC)CFM = 12,795/(1.08 x 10) = 1185 CFM (of outside air @ 115 degrees Fahrenheit)