Grease Trap Sizing formula. The size of the interceptor is determined by the following formula:

number of meals 		waste flow 		retention storage 	interceptor size

per peak hour a	x	rateb		x	timec 		=	(liquid capacity)

______________	x	_________	x	_________	=  	______________

- Number of meals served at peak hour

- Waste flow

- With dishwashing machine					6 gallon flow

- Without dishwashing machine					5 gallon flow

- Single Service Kitchen						2 gallon flow

- Food waste disposer						1 gallon flow

- Retention times

- Commercial Kitchen waste Dishwasher				2.5 hours

- Single Service Kitchen, Single serving				1.5 hours

- Storage Factors

  - Fully equipped commercial kitchen			8 hour operation : 1

12 hour operation: 1.5

16 hour operation: 2

24 hour operation: 3

  - Single Service Kitchen  :	--------------------------------------------       1.5