  - Round Duct and Fittings:

A.  Construct ducts in accordance with Section 3 of the 2005 SMACNA Manual, “HVAC Duct Construction Standards, Metal & Flexible” Third Edition.

B.	For duct construction pressure 2” w.g. or below:

    - Round Ductwork

a.	Round low velocity ductwork shall be constructed from a minimum of 26 gauge, self-locking, pre-sealed snaplock pipe, which incorporates a factory applied gasket in the longitudinal seam and on the female end of the transverse joint.  Snaplock pipe shall be “Greenseam +”as manufactured by Ductmate Industries or approved equal.

    - Fittings

a.	All High Efficiency Take-Offs, Conicals, and Collars must have a factory applied gasket along all rivets, co-latches, and flange. All fittings shall be constructed from a minimum of 26 gauge steel. All dampered fittings must have low-leakage hardware with closed-end bearings.

Approved manufacturer: Ductmate Industries “GreenSeam Fittings” or approved equal.