MEDIUM VOLTAGE Switches (MVS)

Section 16361A


Section 16361A

MEDIUM VOLTAGE Switches (MVS)

PART 1 General

1.01 Scope

D. The Contractor shall furnish and install the medium voltage load interrupter switchgear as specified herein and as shown on the contract drawings.

1.02 Related Sections

1.03 References

D. The medium voltage load interrupter switchgear and all components shall be designed, manufactured and tested in accordance with the latest applicable standards as follows:

1. ANSI/IEEE C37.20.3 

2. ANSI/IEEE C37.20.4 

3. ANSI C37.22 

4. NEMA SG5

5. NEMA SG6

6. CSA22.2 No.31-M89 

7. EEMAC G8-3.3 

E. Listing by Underwriters Laboratories Inc. (UL) or Canadian Standards Association (CSA) shall be provided for 5 kV or 15 kV class medium voltage load interrupter switchgear.

1.04 Submittals – for Review/Approval

D. The following information shall be submitted to the Engineer:

1. Master drawing index

2. Front view elevation

3. Floor plan

4. Top view

5. Single line

6. Nameplate schedule

7. Component list

8. Conduit entry/exit locations

9. Assembly ratings including:

a. Short-circuit rating

b. Voltage

c. Continuous current

d. Basic Impulse Level

10. Major component ratings including:

a. Voltage

b. Continuous current

c. Interrupting ratings

11. Cable terminal sizes.

E. Where applicable or required by the Engineer the following additional information shall be submitted to the Engineer:

1. Busway connection

2. Connection details between close-coupled assemblies

3. Composite floor plan of close-coupled assemblies

4. Electrical schematic diagram

5. Key interlock scheme drawing and sequence of operations

6. Descriptive bulletins

7. Product data sheets.
1.05 Submittals – for construction

D. The following information shall be submitted for record purposes:

1. Final as-built drawings and information for items listed in paragraph 1.04

2. Wiring diagrams

3. Certified production test reports

4. Installation information including equipment anchorage provisions

5. Seismic certification.

1.06 Qualifications

D. The manufacturer of the assembly shall be the manufacturer of the major components within the assembly.

E. For the equipment specified herein, the manufacturer shall be ISO 9000, 9001 or 9002 certified.

F. The manufacturer of this equipment shall have produced similar electrical equipment for a minimum period of five (5) years. When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

G. The equipment and major components shall be suitable for and certified to meet all applicable seismic requirements of Uniform Building Code (UBC) for Zone 4 application. Guidelines for the installation consistent with these requirements shall be provided by the switchgear manufacturer and be based upon testing of representative equipment. The test response spectrum shall be based upon a 5% minimum damping factor, UBC: a peak of 2.15g’s (3.2 – 11 Hz), and a ZPA of 0.86g’s applied at the base of the equipment. The tests shall fully envelop this response spectrum for all equipment natural frequencies up to at least 35 Hz.

-- (OR --

A. The equipment and major components shall be suitable for and certified to meet all applicable seismic requirements of the California Building Code (CBC) through Zone 4 application. Guidelines for the installation consistent with these requirements shall be provided by the switchgear manufacturer and be based upon testing of representative equipment. The test response spectrum shall be based upon a 5% minimum damping factor, CBC: a peak of 2.15g’s, and a ZPA of 0.86g’s applied at the base of the equipment. The tests shall fully envelop this response spectrum for all equipment natural frequencies up to at least 35 Hz.

-- (OR --

D. The equipment and major components shall be suitable for and certified to meet all applicable seismic requirements of the BOCA National Building Code, paragraph 1612.6. This shall include both vertical and lateral required response spectra as specified. Alternatively, the manufacturer’s certification may be based on a detailed computer analysis of the entire assembly structure and its components. Guidelines for the installation consistent with these requirements shall be provided by the switchgear manufacturer and 
be based upon testing of representative equipment. The equipment manufacturer shall document the requirements necessary for proper seismic mounting of the equipment. The test response spectra shall meet or exceed the required response spectra peak acceleration of 1.6g’s (3.2 – 11 Hz), and a ZPA of 1.0g as specified in the BOCA National Building Code, for all equipment natural frequencies up to at least 35 Hz.

H. The following minimum mounting and installation guidelines shall be met, unless specifically modified by the above referenced standards.

1. The Contractor shall provide equipment anchorage details, coordinated with the equipment mounting provision, prepared and stamped by a licensed civil engineer in the state. Mounting recommendations shall be provided by the manufacturer based upon approved shake table tests used to verify the seismic design of the equipment.

2. The equipment manufacturer shall certify that the equipment can withstand, that is, function following the seismic event, including both vertical and lateral required response spectra as specified in above codes.

3. The equipment manufacturer shall document the requirements necessary for proper seismic mounting of the equipment. Seismic qualification shall be considered achieved when the capability of the equipment, meets or exceeds the specified response spectra.

1.07 regulatory requirements

1.08 delivery, storage and handling

D. Equipment shall be handled and stored in accordance with manufacturer’s instructions. One (1) copy of these instructions shall be included with the equipment at time of shipment.

E. Each switchgear assembly shall be split into shipping groups for handling as indicated on the drawings or per the manufacturer’s recommendations. Shipping groups shall be designed to be shipped by truck, rail or ship. Shipping groups shall be bolted to skids. Accessories shall be packaged and shipped separately. Each switchgear shipping group shall be equipped with lifting eyes for handling solely by crane.

1.09 Operation and Maintenance manuals

D. Equipment operation and maintenance manuals shall be provided with each assembly shipped, and shall include instruction leaflets and instruction bulletins for the complete assembly and each major component.
Note to Spec. Writer:

For single switch, unit substation applications see part 2, section 16361B.

PART 2 Products 

2.01 Manufacturers

D. Cutler-Hammer

E. (__________

F. (__________

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

2.02 Ratings

D. Switchgear assembly ratings shall be as follows:

1. Nominal System Voltage



(____ kV three-phase 








[three] [four] wire 

2. System Grounding




([solid] [low-resistance] 







[high-resistance] [ungrounded]

3. Available System 3-Phase Short


(____kA Symmetrical [5] [10] [15] 
 Circuit Current





[20] [25] [30] [35] [40] [50] [63]

	Note to Spec. Writer:

Fill in data below from table:

ASSEMBLY RATINGS

	Maximum
BIL
Main Cross Bus
Main Cross Bus
Design kV

Momentary Current 
2-Second Current




(10 Hz) kA rms Asymmetrical
kA rms Symmetrical

	
5
60
40
25

5
60
64
40

5
60
80
50

5
60
100
   63 A

	
15
95
40
25

15
95
64
40

15
95
80
50

15
95
100
   63 A

	
27
125
40
25

27
125
61
38

	
38
150
40
25

	A – UL and CSA listed integrated rating with a Cutler-Hammer CLE fuse as the assembly main fault current device rated 450E maximum at 5 kV and 300E maximum at 15 kV.


4. Maximum Design Voltage 



(____ kV 

5. BIL






(_____kV

6. Main Cross Bus Continuous Current


([None] [600A] [1200A] [2000A]







[3000A}

7. Main Cross Bus Momentary Current (10 Hz)

(____ kA Asymmetrical

8. Main Cross Bus 2-Second Current


(____ kA Symmetrical


	Note to Spec. Writer:

Fill in data below from table:

NON-FUSED SWITCH RATING

	
Maximum
Continuous and
Momentary
Fault Close
2-Second

Voltage
Load Break
kA rms
kA rms 
Current

            
Current
Asymmetrical
Asymmetrical
kA Symmetrical   

	
5 or 15
600 or 1200
40
40
25




64
64
40

	
27
600
40
40
25



600
61
61
38

	
38
600
40
40
25


9. Non-Fused Switch Fault close (3 times, minimum)
(____ kA Asymmetrical

10. Non-Fused Switch (Continuous and Load Break) 
(____ Amperes


	Note to Spec. Writer:

Fill in data from tables below:

FUSED SWITCH RATING

	Current Limiting Fuses

	
Maximum
Fuse Ampere
Fuse
Fault Close kA rms
2-Second

Voltage
RatingB
Type
Asymmetrical

	
5

250
CLE
100A
NA



450
CLE
100A
NA



750
CLE
 64A
NA

	
15
150
CLE
100A
NA



300
CLE
100A
NA

	
27
50
NX
40
NA

50
NX
56
NA


100
NX
40
NA


100
NX
56
NA

	
38
40
EJO-1
20
NA



80 
EJO-1
20
NA

	A – UL and CSA listed integrated rating with a Cutler-Hammer CLE fuse.
B – Fuse ampere rating is maximum for the fuse “frame size.” 5 kV ranges: 10-250, 300-450, and 600-750. 15 kV ranges: 10-150 and 175-300. 27 kV ranges: 6-50 and 60-100. 38 kV ranges: 1-40 and 50-80.

	Boric Acid Expulsion Fuses

	
Maximum
Fuse
Fuse
Fault Close
2-Second

Voltage
Ampere
Type
kA rms 



RatingC

Asymmetrical

	
5

200
RBA200
26.5
NA



400
RBA400
40
NA



400
RBA400
60
NA



720
RBA800
40
NA



720
RBA800
60
NA

	
15
200
RBA200
23
NA



400
RBA400
40
NA



400
RBA400
47
NA



720
RBA800
40
NA



720
RBA800
47
NA

	

14.4
400
HRBA400
55.6
NA



720
HRBA800
55.6
NA

	
25.8
200
RBA200
16.8
NA



300
RBA400
33.6
NA



540
RBA800
33.6
NA

	
38
200
RBA200
11
NA



300
RBA400
26.8
NA



540
RBA800
26.8
NA

	C – Fuse ampere rating is maximum for the fuse “frame size.” RBA200 range: 10 to 200, RBA400 range: 10-400, RBA800 range: 450-720 amperes.


11. Fused Switch Fault close



(____ kA Asymmetrical

12. Fused Switch Maximum (Continuous / Load Break)
(____ Amperes

2.03 5 and 15 kV Construction

D. The metal-enclosed load interrupter switchgear shall consist of deadfront, completely metal-enclosed vertical sections containing load interrupter switches and fuses (where shown) of the number, rating and type noted on the drawings or specified herein.

E. The following features shall be supplied on every vertical section containing a three-pole, two-position open-closed switch:

1. A large 8-inch x 16-inch high-impact viewing window that permits full view of the position of all three switch blades through the closed door. The window shall not be more than 58-inches above the switch pad level to allow ease of inspection.

2. The door shall be interlocked with the switch so that:

a. The switch must be opened before the door can be opened.

b. The door must be closed before the switch can be closed.

3. A hinged grounded metal barrier bolted closed in front of every switch to prevent inadvertent contact with any live part, yet allow for a full-view inspection on the switch blade position

4. Provision for padlocking the switch in the open or closed position.

5. Green OPEN, Red CLOSED switch position indicators with the words “Open” and “Closed” in French, Spanish and English.

6. A hinged cover with rustproof quarter turn nylon latches over the switch operating mechanism to discourage casual tampering.

7. The Switch shall be removable as a complete operational component.  

F. Vertical section construction shall be of the universal frame type using die-formed and bolted parts. All enclosing covers and doors shall be fabricated from steel whose thickness shall be equal to or greater than those specified in ANSI/IEEE C37.20.3. No owner removable hardware for covers or doors shall be thread-forming type. To facilitate installation and maintenance of cables and bus in each vertical section, a split removable top cover and ([split removable rear covers with rustproof nylon handles] [padlockable hinged rear door held closed by bolts] shall be provided. A G90 grade galvanized base shall isolate equipment from contact with the concrete pad providing protection from rust. Heavy-duty hot dipped galvanized anchor clips shall be provided to anchor the switchgear to the concrete pad.

G. Each vertical section containing a switch shall have a single, full-length, flanged front door and shall be equipped with two (2) rotary latch-type padlockable handles. Provision shall be made for operating the switch and storing the removable handle without opening the full length door.

H. Each load interrupter switch shall have the following features:

1. Three-pole gang-operated mechanism.

2. Manual quick-make, quick-break over-toggle-type mechanism that does not require the use of a chain or a cable for operation, and utilizes a heavy-duty coil spring to provide opening and closing energy.

3. The speed of opening and closing the switch shall be independent of the operator, and it shall be impossible to tease the switch into any intermediate position under normal operation.

4. Separate main and break contacts to provide maximum endurance for fault close and load interrupting duty.

5. Insulating barriers between each phase and between the outer phases and the enclosure.

6. A maintenance provision for slow closing the switch to check switch blade engagement and slow opening the switch to check operation of the arc interrupting contacts.

-- (OR --

2.03
27 and 38 kV Construction

A.
The metal-enclosed load interrupter switchgear shall consist of deadfront, completely metal-enclosed vertical sections containing load interrupter switches and fuses (where shown) of the number, rating and type noted on the drawings or specified herein.

B.
The following features shall be supplied on every vertical section containing a three-pole, two-position open-closed switch:

1.
A high-impact viewing window that permits full view of the position of all three switch blades through the closed door. 

2.
The door shall be interlocked with the switch so that:

a. The switch must be opened before the door can be opened.

b. The door must be closed before the switch can be closed.

3.
A hinged grounded metal barrier bolted closed in front of every switch to prevent inadvertent contact with any live part, yet allow for a full-view inspection on the switch blade position.

4.
Provision for padlocking the switch in the open or closed position.

5.
Green OPEN, Red CLOSED switch position indicators with the words “Open” and “Closed” in French, Spanish and English.

6.
A hinged cover with over the switch operating mechanism to discourage casual tampering.

C.
Vertical section construction shall be of the universal frame type using die-formed and bolted parts. All enclosing covers and doors shall be fabricated from steel whose thickness shall be equal to or greater than those specified in ANSI/IEEE C37.20.3. To facilitate installation and maintenance of cables and bus in each vertical section, a removable top cover and ([split removable rear covers with rustproof nylon handles] [hinged rear door latched closed by tamper-resistant padlockable latches] shall be provided. 

D.
Each vertical section containing a switch shall have a single, full-length, flanged front door and shall be equipped with two (2) rotary latch-type padlockable handles. Provision shall be made for operating the switch and storing the removable handle without opening the full length door.

E.
Each load interrupter switch shall have the following features:

1.
Three-pole gang-operated mechanism.

2.
Manual quick-make, quick-break over-toggle-type mechanism that does not require the use of a chain or a cable for operation, and utilizes a heavy-duty coil spring to provide opening and closing energy.

3.
The speed of opening and closing the switch shall be independent of the operator, and it shall be impossible to tease the switch into any intermediate position under normal operation.

4.
Separate main and break contacts to provide maximum endurance for fault close and load interrupting duty.

5.
Insulating barriers between each phase and between the outer phases and the enclosure.

6.
A maintenance provision for slow closing the switch to check switch blade engagement and slow opening the switch to check operation of the arc interrupting contacts.

2.04 Bus

D. All phase bus conductors shall be ([tin-plated aluminum] [silver-plated copper].

E. Ground bus conductor shall be silver-plated copper and be directly fastened to a galvanized metal surface of each vertical section, and be of a size sufficient to carry the rated 
(2-second) current of the switchgear assembly.

F. A neutral bus shall be provided only when indicated on the drawings. It shall be insulated for 1000V AC to ground. The current rating of the neutral bus shall be 600 amperes. 

2.05 Bus Insulation SYSTEM

D. All bus shall be supported utilizing a High Strength and High Creep, finned support providing 14-inch of creep distance between phases and ground. The molded fins shall be constructed of high track resistant ([Aramid Nylon] [Silicone Rubber] [Cycloaliphatic Epoxy].

E. All standoff insulators on switches and fuse mountings shall be ([Glass Polyester (for 5 and 15 kV Classes)] [Polykeram (for 27 and 38 kV Classes)] [Cycloaliphatic Epoxy].

2.06 Wiring/Terminations

D. One (1) terminal pad per phase shall be provided for attaching contractor-supplied cable terminal lugs for a maximum of two (2) conductors per phase of the sizes indicated on the drawings. Sufficient space shall be allowed for contractor supplied electrical stress relief termination devices.

E. Small wiring, fuse blocks and terminal blocks within the vertical section shall be furnished as indicated on the drawings. Each control wire shall be labeled with wire markers. Terminal blocks shall be provided for owner’s connections to other apparatus.

2.07 fuses

D. Fault protection shall be provided by fuses with continuous ratings as shown in the contract documents. The fuses shall be Cutler-Hammer ([CLE current limiting type] [RBA expulsion type]. Furnish three (3) spare ([fuses] [refills] for each fused switch. Fuse/switch integrated momentary and fault close ratings specified shall have been verified by test and UL and CSA certified.

2.08 Utility metering

D. Where indicated on the drawings, each utility metering vertical section shall contain provisions for current transformers and voltage transformers as required by the utility. The construction shall conform to the utility company’s metering standards. It shall also conform to the general electrical and construction design of the switchgear specified above.

2.09 customer metering

D. Where indicated on the drawings, provide [a separate owner metering vertical structure with a front hinged door to provide safe isolated access to meters and all associated terminal and fuse blocks for maintenance, calibration or testing while the gear is energized.] [owner metering in the switch structure on a hinged panel to provide safe isolated access to meters and all associated terminal and fuse blocks for maintenance, calibration or testing while the gear is energized].

E. Provide ring-type current transformers for each meter. Current transformers shall be wired to shorting-type terminal blocks.

F. Provide voltage transformers including primary fuses and secondary protective devices for metering as shown on the drawings.

Note to Spec. Writer: 

Select devices as required for paragraph 2.09 D.
Refer to section 16901 for detailed specification for metering.
IQ Analyzer-6000 Series (Section 16901, paragraph 2.02 A.)
IQ DP-4000 Series (Section 16901, paragraph 2.02 B.)
IQ 300 Series (Section 16901, paragraph 2.02 C.)
IQ 200 Series (Section 16901, paragraph 2.02 D.)
G. Microprocessor-Based Metering System

2.010 Accessories

D. (Supply key interlocks as shown on the drawings.

	Note to Spec. Writer:

Fill in data below from table:

Surge Arrester Selection A

	System Grounding
	Nominal System Line-to-Line Voltage

	
	2.4
	4.16
	4.8
	7.2
	12.0
	12.47
	13.2
	13.8
	14.4
	22.9
	24.9
	34.5

	Solidly Grounded System
	3
	6
	6
	6
	12
	12
	12
	12
	12
	21
	24
	30

	Low Resistance Grounded System
	3
	6
	6
	6
	12
	12
	12
	12
	12
	21
	24
	30

	High Resistance
	6
	6
	9
	12
	18
	18
	21
	21
	24
	36
	39
	54

	A – Surge arrester rating is based upon the ambient air temperature in the switchgear vertical section not exceeding 
55 degrees C.


E. ((____ kV ([station] [intermediate] [distribution] class surge arresters shall be provided connected at the incoming terminations and securely grounded to the metal structure.
2.011 enclosures

D. Enclosures shall be constructed per IEEE/ANSI C37.20.3 indoor specifications. (Meets or exceeds NEMA 1.)

E. Each vertical section shall be ventilated at the top and bottom, both front and rear, to allow airflow to provide cooling and to help prevent buildup of moisture within the structure.  

-- (OR --

B. Enclosures shall be constructed per IEEE/ANSI C37.20.3 Outdoor specifications. (Exceeds NEMA 3R.)
C. Each vertical section shall have a sloped weatherproof roof with labyrinth shaped joints. Use of gasket or caulking to make roof joints weatherproof is not permitted. All exterior openings shall be screened to prevent the entrance of small animals and barriered to inhibit the entrance of snow, sand, etc. A minimum of one (1) 250-watt, 120-volt space heater shall be provided in each vertical section. Power for the space heater(s) shall be furnished ([as indicated on the drawings] [by a control power transformer mounted in the switchgear] [by a transformer mounted within the low voltage switchboard/switchgear]. The design shall be non-walk-in type. 
F. Each vertical section shall be ventilated at the top and bottom, both front and rear, to allow airflow to provide cooling and help prevent buildup of moisture within the structure.  The ventilated covers shall be externally removable to allow safe maintenance of the filter media without providing access to live parts.

G. (Enclosure shall be Dust Resistant. All ventilated openings shall be filtered to inhibit the ingress of dust. The ventilated covers shall be externally removable to allow safe maintenance of the filter media without providing access to live parts. All external doors 
and covers shall be gasketed.
2.012 nameplates

D. A nameplate shall be mounted on the front door of each switch vertical section in accordance with the drawings.

2.013 Finish

D. Prior to assembly, all enclosing steel shall be thoroughly cleaned and phosphatized. A powder coating shall be applied electrostatically, then fused-on by baking in an oven. The coating is to have a thickness of not less than 1.5 mils. The finish shall have the following properties:

Impact resistance (ASTM D-2794)
60 direct/60 indirect
Pencil hardness (ASTM D-3363)

H
Flexibility (ASTM D-522)


Pass 1/8-inch mandrel
Salt spray (ASTM B117-85 [20])

600 hours
Color




ANSI 61 gray

2.014 Miscellaneous Devices

D. (Motor operators, where indicated on the drawings, shall have the following features:

1. All motor-operated switches shall consist of a standard manually-operated switch in combination with an electric motor driven linear actuator which charges the spring. Connection between the linear actuator and switch mechanism shall be by reliable rigid metal-to-metal linkages; not chains or cables. The linear actuator and all associated low voltage wiring shall be located in a low voltage compartment or barriered to separate it from the high voltage.

2. Operating voltage shall be 120 volts, 60 Hz available ([from a fused control transformer] [from an external source as shown on the drawings]. The switch shall be capable of manual operation should a loss of control power be encountered. 

3. The linear actuator shall be a highly repetitively manufactured item, completely sealed and weather protected, and designed for rugged industrial application. No lubrication or adjustments shall be necessary for its normal operating life. The motor shall be equipped with an automatically reset thermal overload protector.

E. (Communication equipment, where indicated on the drawings, shall have the following features:

1. The communication system network shall be Cutler-Hammer type IMPACC/PowerNet.

2. Each load interrupter switch position (open and closed), where shown, shall be communicated via an addressable relay. This relay shall communicate over a local area network (LAN). The relay shall monitor an auxiliary switch contact that monitors the primary switch position and shall be rated for the application. Each relay shall have a unique address so that it is possible to “call up” and “read” each load interrupter switch’s position from a host computer. 

3. A blown high voltage fuse condition on each set of three (3) fuses shall be monitored by an addressable relay. Any blown fuse operation shall be communicated immediately over a local area network (LAN) via the monitoring addressable relay. Each relay shall have a unique address so that it is possible to “call up” and “read” a fuse blown operation for a set of fuses with the communication system.

4. The manufacturer shall wire a LAN within the switchgear to all communication capable devices with the same protocol and wire the LAN to a set of easily accessible terminal blocks.  

5. Control power shall be 120 volts, 60 Hz available ([from a fused control transformer] [from an external source as shown on the drawings].

2.015 Special switchgear configurations

D. (Non-Loadbreak Selector Switches

1. For 5 or 15 kV ratings, furnish a two-position non-loadbreak selector switch for the selection of two incoming sources in series with the load break MVS switch where shown on contract drawing. The selector switch shall have the same continuous current rating as the load interrupter switch in the same structure. Interlocking shall be supplied so that the selector switch can only be operated with the load interrupter switch in the open position. Also, neither the main door nor the load interrupter switch shall be able to be closed without the selector switch being positively locked in one of the two source positions.

E. (Duplex Switchgear Assembly

1. Furnish, where shown on the drawings, a duplex switchgear assembly configuration consisting of two (2) load interrupter switches with common load side bus to feed one load circuit, which shall be fused or unfused as indicated on the drawings. Key interlocks shall be supplied to prevent paralleling the incoming sources, and to prevent opening the front door of each vertical section containing one of the two switches unless both switches are locked open.

C. (Automatic Transfer Control – Two-Switch Automatic Transfer Control with Common Load Bus

2. Furnish, where shown on the drawings, a switchgear assembly with microprocessor-based automatic transfer control system for two (2) main switches with a common load bus. The system shall consist of the two (2) load interrupter switches with motor operators as herein specified, and an integrated microprocessor-based automatic transfer control system containing sensing devices, low voltage logic control, and auxiliary equipment, as indicated on the drawings and specified here. The automatic transfer control system, when placed in the “automatic” mode, shall automatically transfer the load bus circuit to the alternate power source upon failure of the preferred source. 

3. The basic sequence of operation based upon two normally energized sources shall be as follows. Normal operation shall be with the preferred source main switch closed and standby main switch open. Upon detection of abnormal voltage(s) to the line side of the preferred main switch, and after a field-adjustable time delay, that main switch shall open and after an additional field-adjustable time delay, the standby main switch shall close restoring power to the facility. Upon restoration of voltage to the line side of the preferred main switch, and after a field-adjustable time delay, the standby main switch shall open, and after a field-adjustable time delay, the preferred main switch shall close.

4. The logic of the transfer shall function via a microprocessor controller.
Provide electronic transfer controller device equal to Cutler-Hammer type IQ Transfer. The set points shall be field-adjustable without the use of special tools. LED lights shall be included on the controller to show:

Normal Source Available
Emergency Source Available
Normal Source Connected
Emergency Source Connected
Load Energized.

5. A digital readout shall display each option as it is functioning. Readouts shall display actual line-to-line voltage, line frequency and timers. When timers are functioning, the microprocessor shall display the timer counting down. All set points shall be re-programmed from the front panel of the controller when it is in the program mode. In addition, the controller shall display date, time and reason of last 16 transfers; set points of timers, voltage pickup and dropout set points. When compatibility with Cutler-Hammer PowerNet communications system is specified, the microprocessor-based controller shall be compatible with it. It shall be able to communicate all values and historical data that are displayed locally, and have the capability to change settings. 

6. The transfer system shall include the following:

a. A time delay transfer from the normal power source to the standby power source and from the standby power source to the normal source, forcing a neutral position to ensure the load voltage has decayed before reconnecting to the source from which the load is to be fed (0 seconds to 30 minutes). 

b. A time delay to override a momentary power outage or voltage fluctuation (0 seconds to 120 seconds).

c. A time delay for transferring from the standby power source to the normal power source (0 seconds to 30 minutes).

d. A Form C relay contact that changes state when the power is available on the normal source.

e. A Form C relay contact that changes state when the power is available on the standby source.

f. A preferred source selection (source 1 or source 2, or none).

7. Two (2) sets of three-phase “line side” voltage transformers (open delta for 5 kV or 15 kV, wye-wye for 27 kV and 38 kV) with primary fuses and secondary supplementary protectors to provide both sensing and control power.

8. The automatic microprocessor-based control relay system which contains:

a. One selector switch with automatic and manual positions.

b. One (1) open-close control switch for manual electrical operation of each controlled load interrupter switch.

c. One (1) pushbutton to initiate manual retransfer to preferred source when the IQ Transfer Controller is functioning automatically and programmed to “Hold” after transfer.  

-- (OR --

D. (Automatic Transfer Control – Three-Switch Automatic Transfer Control with Two Mains and Normally Open Tie.

9. Furnish, where shown on the drawings, a switchgear assembly with automatic transfer control relay system for two (2) mains and normally open tie. The automatic transfer switchgear shall consist of a deadfront, metal-enclosed and integrated assembly including two (2) main load interrupter switches and one (1) tie load interrupter switch each being driven by a motor operator hereinafter specified, and an integrated microprocessor-based automatic transfer control system containing sensing devices, low voltage logic control and auxiliary equipment, as indicated on the drawings. Operation shall be such that upon loss of voltage to the line side of a main, that main shall open and then the tie shall close. The following features shall be incorporated.

10. The basic sequence of operation based upon two normally energized sources shall be as follows. Normal operation shall be with the main switches closed and the tie switch open. Upon detection of abnormal voltage(s) to the line side of a main switch, and after a field-adjustable time delay, that main switch shall open and after an additional field-adjustable time delay, the tie switch shall close restoring power to the affected portion of the facility. Upon restoration of voltage to the line side of the preferred main switch, and after a field adjustable time delay, the tie switch shall open and after a field-adjustable time delay, the open main switch shall close.

PART 3 execution

3.01 Factory Testing

D. Standard factory tests shall be performed on the equipment under this section. All tests shall be in accordance with the latest version of ANSI and NEMA standards.

E. (Factory tests as outlined above shall be witnessed by the owner’s representative.

1. The manufacturer shall notify the owner two (2) weeks prior to the date the tests are to be performed.

2. The manufacturer shall include the cost of transportation and lodging for up to three (3) owner’s representatives. The cost of meals and incidental expenses shall be the owner’s responsibility.

F. The manufacturer shall provide three (3) certified copies of factory test reports.

3.02 Field Quality Control

D. Provide the services of a qualified factory-trained manufacturer’s representative to assist the Contractor in installation and start-up of the equipment specified under this section for a period of (_______ working days. The manufacturer’s representative shall provide technical direction and assistance to the Contractor in general assembly of the equipment, connections and adjustments, and testing of the assembly and components contained therein.

E. The Contractor shall provide three (3) copies of the manufacturer’s field 
start-up report.

3.03 Manufacturer’s Certification

D. The Contractor shall provide a qualified factory-trained manufacturer’s representative shall certify in writing that the equipment has been installed, adjusted and tested in accordance with the manufacturer’s recommendations. 

E. The Contractor shall provide three (3) copies of the manufacturer’s representative’s certification.

3.04 Training

D. The Contractor shall provide a training session for up to five (5) owner’s representatives for (____ normal workdays at a jobsite location determined by the owner.

E. The training session shall be conducted by a manufacturer’s qualified representative and consist of instruction on the assembly, switches and major components.

3.05 Installation

D. The Contractors shall install all equipment per the manufacturer’s recommendations and the contract drawings.

E. All necessary hardware to secure the assembly in place shall be provided by the contractor.

3.06 Field Adjustments

3.07 Field Testing

( Note to Spec. Writer – Select one


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Insert data in blanks


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Insert data in blanks


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Insert data in blanks


( Note to Spec. Writer – Insert data in blanks


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Insert data in blanks


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Select one


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Optional


( Note to Spec. Writer – Insert data in blanks






16361A-


12/02


