1.11
BUILT-UP ROOFING
1.11.1
Scope

Furnish all labor, materials, equipment, and related items necessary and required to properly execute the roofing work shown on the attached drawings and/or specified herein but not necessarily limited to the following:



Protection of existing and new roof, mechanical equipment, and office personnel



Removal of gravel and built-up roof



Cleaning and repair of decking



Furnish and install vapor barrier



Furnish and install insulation



Furnish and install the following sheet metal accessories:


-
Coping at top of parapet walls


-
Pitch pockets


-
Metal flashing and metal flashing collars at roof penetrations, and curbs and fanhouses.



Furnish and install four-ply built-up system



Clean up, remove, and dispose of all job related litter 

1.11.2
General

Outside consulting inspection services may be employed by Lockheed Martin to monitor quality and progress and shall be included in this contract.

1.11.3
Reference Publications, Codes, and Standards


Factory Mutual Bulletin 1-28 Class I Construction



"Architectural Sheet Metal Manual" published by Sheet Metal and Air Conditioning Construction National Association, Inc., 1969 Printing



Federal Specification FS-R-556 C

1.11.4
Products
1.11.4.1
Accepted Roofing Manufacturers:



Manville



Flintkote Building Products Company



GAF Roofing Products Division



NORD BITUMI INC.



Others as approved by the Lockheed Martin Construction Engineer

1.11.4.2
Record

Contractor shall have been a manufacturer's approved roofing system applicator on two or more projects which have been completed for at least five years.

1.11.4.3
Insulation
1.11.4.3.1
Material-cellular Glass Insulation


Provide multiple sections of cellular glass block sandwiched between laminated sheets to form rigid impermeable insulation board 1 1/2 inch thick per Fed. Spec. #HH-I-551E.  Insulation used shall be one layer cellular glass block insulation 1 1/2 inch thick.

1.11.4.3.2
Acceptable Products


Acceptable products include Foamglass, cellular glass insulation by Pittsburgh Corning Corp.; Pittsburgh, PA.

1.11.4.3.3
One Layer Cellular Glass Block


Install insulation mechanically fastened to wood deck (minimum four fasteners per board) with staggered joints.  Bowed boards will be rejected.  Use only undamaged boards, except where damaged boards can be trimmed to fit at irregular areas.  Board contact and attachment will be spot checked by lifting boards.

1.11.4.4
Roofing System
1.11.4.4.1
Type


The roofing system shall have four plies, glass fiber felts with asphalt topping, emulsion, and aluminum top coating.

1.11.4.4.2
Materials



Asphalt:  Meeting ASTM D312 - Type IV Special Steep Asphalt



Ply Felts:  Asphalt saturated glass fiber felt:  ASTM D2178, Type IV



Vapor Barrier:  #43 asphalt saturated and coated felt, ASTM D2626



Emulsion:  Tremco, Tremlastic, Asphaltic Emulsion



Aluminum Top Coating:  Tremco Double Duty Aluminum (composed of processed drying oils combined in suitable proportions with light colored synthetic resins and containing aluminum flake to the extent of at least 11 percent by weight and sufficient aliphatic solvent to permit easy application characteristics)



Flashing Felt:  Glass Fiber Reinforced Flashing Felt: "Perma-Flash" by Owens-Corning



Roofing Cement:  "Gulf Seal 304" - Vitalastic Flashing Cement by Gulf States Asphalt



Cant Strip:  Wood Fiberboard, 2"x5-5/8", meeting Federal Standard #LL-1-535



Tapered Edge Strip:  Wood Fiberboard, 1-1/2"x12", meeting Federal Standard #LL-1-535



Membrane Cloth:  Tremco Impregnated Jute Fabric



Leveling Compound: lightweight, mill mixed granular material consisting of a volcanic glass aggregate and a special blend of asphaltic binder such as Therm-1-Deck, Brouk Co., St. Louis, Mo. 



Steel Plate:  ASTM A36, 1/4 inch thick

1.11.4.5
Sheet Metal Materials
1.11.4.5.1
Galvanized Metal


Galvanized metal shall be commercial grade galvanized steel having not less than 1.25 ounces of zinc per square foot and shall be chemically treated for paint adhesion.  Gauges shall be as indicated on drawings.

1.11.4.5.2
Sheet Lead


Sheet lead shall be minimum four pounds per square foot.

1.11.4.5.3
Soldering Materials



Solder:  ASTM B32, alloy grade 50A, 50 percent pig lead and 50 percent block tin



Solder Flux:  For galvanized metal, muriatic acid neutralized with zinc; for lead, non-corrosive rosin

1.11.4.5.4
Mastic


Mastic shall be fibrated asphalt flashing cement and shall conform to ASTM D2822.

1.11.4.5.5
Fasteners

1.11.4.5.5.1
Fasteners shall be of same material or compatible with the material being fastened.

1.11.4.5.5.2
Nails shall be flathead, needle point, not less than 6d and of sufficient length to penetrate substrate one inch minimum.

1.11.4.5.5.3
Screws shall be self-tapping type with roundheads.

1.11.4.5.5.4
Exposed screws shall be stainless-steel, self-tapping type with roundhead and rubber or neoprene washers.

1.11.4.5.5.5
Toggle bolts shall be furnished complete with washers.

1.11.4.5.5.6
Rivets shall conform to FS-R-556 C and be of size and type indicated on drawings. If size is not shown on the drawings, 1/8 inch standard rivets shall be used.

1.11.4.5.5.7
Insulation fasteners shall be self-tapping type with flat heads and three inch square bearing plates.

1.11.4.5.6
Pre-Fabricated Roof Equipment Supports


Acceptable products are those listed below.



Pate Company



S & L Manufacturing Company



Thybar Corporation:  Model TEMS-1, welded 18 gauge galvanized steel sheet, base plate and counterflashing, factory installed treated wood nailer

1.11.4.5.7
Sealant


The sealant shall be polysulfide based, one-part elastomeric sealant, complying with FS TT-S-00230, Class A, Type II (non-sag).

1.11.4.5.8
Dissimilar Metal Separation


Ten mil self-adhesive polyethylene tape shall be used where galvanized steel and copper come in contact.

1.11.4.5.9
Sheet Metal Fabrication

1.11.4.5.9.1
Fabricate sheet metal work in accordance with approved shop drawings and industry standards.  Form sheet metal work with clear, sharp, and uniform arises.  Hem exposed edges.

1.11.4.5.9.2
Solder sheet metal joints with heavy, well-heated coppers.  Pre-tin joints shall be not less than 1 1/2 inch wide.  Provide one inch minimum soldered joints.  After soldering, wash joints and neutralize remaining acid with alkaline solution.  Protect roofing from acid contamination.

1.11.4.5.9.3
Provide linear sheet metal items in ten foot sections except as otherwise noted.  Form flashing using single pieces for the full width.

1.11.5
Product Handling, Storage, and Delivery
1.11.5.1
Deliver materials in manufacturer's original, unopened containers and rolls with labels intact and legible.

1.11.5.2
Deliver materials requiring fire resistance classification to the job with labels attached and in the original packaging.

1.11.5.3
Deliver materials in sufficient quantity to allow continuity of work.

1.11.5.4
Handle rolled goods so as to prevent damage to edges or ends.

1.11.5.5
Select and operate material handling equipment so as not to damage existing construction or applied roofing.

1.11.5.6
Store roofing insulation, roofing felts, base, and cap sheet materials on clean raised platforms and cover with waterproof canvas to protect them from the weather.

1.11.5.7
Store rolled goods on end.

1.11.5.8
The Contractor shall make available a Delmhurst probe type moisture meter to Lockheed Martin Construction Engineer for testing of moisture content of in place materials and materials being installed.  Inability to provide moisture meter on a daily basis will be sufficient grounds to halt all construction until moisture meter is made available.  This type moisture meter is the only acceptable meter.  There are no acceptable substitutes.

1.11.5.9
Provide continuous protection of materials against wetting and moisture absorption. Acceptable moisture content is ten percent or less when tested with a Delmhurst moisture meter. Readings over ten percent may be verified by a testing laboratory at the Contractor's expense.

1.11.5.10
Store cartons level, standing in an upright position. Do not stack cartons. Protect open top containers from dirt and moisture. If material becomes wet (shows more than ten percent moisture),it shall be removed from the job site at the Contractor's expense.

1.11.5.11
Storage of materials shall be in compliance with Lockheed Martin fire and safety regulations and located as directed by the Lockheed Martin Construction Engineer.

1.11.5.12
Prior to storage, stock piling of materials on the roof (both quantity and location) shall be approved by the Lockheed Martin Construction Engineer. At no time shall more than 1/2 days supply of material needed for the job be removed from the storage area and placed on the roof.

1.11.5.13
Store solvent bearing materials in a dry, cool storage area and keep lids tight on all containers to prevent escape of vapors.  Containers to be approved by Lockheed Martin Safety.

1.11.5.14
Particular care shall be taken in handling materials to prevent damage to surfaces, edges, or ends. Damaged material shall be removed from the site by the Contractor.

1.11.6
Protection of Equipment, Personnel, and Facilities
1.11.6.1
Drop cloths, bracing, shoring, and nets shall be provided where determined by the Lockheed Martin Construction Engineer to protect the building and site from damage or defacing by roofing operations, particularly at hoisting locations.

1.11.6.2
Chutes shall be used to minimize the spread of dust and flying particles while removing debris from the roof.  Debris shall not be thrown from roof.

1.11.6.3
Gravel shall be removed from the roof by vacuum.

1.11.6.4
At no time shall more tear-off of existing built-up roof be made than can be replaced by the end of each work day.

1.11.6.5
Temporary 3/4 inch plywood runways shall be placed over roofing where traffic ways are established.  The Contractor is to supply sufficient quantities to transport all men, equipment, and materials over areas not to be torn off that day.

1.11.6.6
Limit size and weight of all mechanical equipment used on the roof to not more than 130 pounds per wheel and to remain on plywood runways at all times where roof is not to be torn off that day.

1.11.6.7
Any areas of existing roofing that are not to be replaced under this contract and that are damaged by the operations of the Contractor shall be repaired or replaced at no cost to Lockheed Martin.

1.11.6.8
The asphalt kettle shall at no time be placed on the building roof.  The kettle shall be attended at all times by a qualified operator while it is in operation or during cool down.

1.11.7
Environmental Requirements
1.11.7.1
Apply roofing in dry weather when ambient temperature is above 40°F and rising and free of ice and frost.  Do not apply when ambient temperature is 40°F and falling.

1.11.7.2
Do not install roofing over a wet surface or permit insulation or roofing felts to become wet or exposed to inclement weather before completion of the roofing.

1.11.7.3
The Contractor is responsible for the removal of all moisture from the surface over which roofing is to be applied.

1.11.7.4
Permanent water cut-offs are not required.

1.11.7.5
When the roofing installation work shall be unavoidably stopped for 24 hours or less (such as during the evening between work days) temporary roofing shall be installed, consisting of two layers of standard roofing fiberglass sheets (felt) with inter-ply mopping and coating of steep asphalt. Remove temporary roofing completely and immediately before installation of permanent roofing system.

1.11.7.6
When it is anticipated that the roofing installation work shall be stopped in excess of 24 hours due to adverse weather conditions, a break in the work schedule due to building usage, or any other condition, temporary roofing shall be installed consisting of a standard roofing fiberglass sheet (felt) mopped and folded over the insulation. A two ply temporary roofing system as described in the paragraph above shall be installed.

1.11.7.7
Do not install insulation that cannot be completely covered the same day with four plies of roofing felts mopped in place.  Insulation that is allowed to go overnight without the four ply felts in place shall be removed and disposed of off site.

1.11.7.8
Discard and remove from the site all insulation that has become wet (ten percent moisture or more).

1.11.8
Equipment Requirements

Provide thermostatic controls and a visible thermometer on the kettle, maintain them in working order, and keep them calibrated.  The kettle and application temperatures will be field checked by the Lockheed Martin Construction Engineer.  If control, meter, etc. on the kettles are broken or not in working order, the kettle shall be shut down, the kettle in question emptied, and the asphalt removed from the job site at the Contractor's expense.

1.11.9
Work To Be Performed

All new materials installed prior to inspection of all surfaces by the Lockheed Martin Construction Engineer shall be removed and surfaces made ready for reinspection.

1.11.9.1
Removal of Roofing Material
1.11.9.1.1
The sequence of operations shall be such that maximum practicable protection from inclement weather will be provided for materials and equipment located in partially dismantled structures.  Allow no structures to be exposed to inclement weather nor left in an unweathertight condition overnight or through any other work stoppage.

1.11.9.1.2
Completely remove all gravel as designated by means of power brooms, push brooms, and pneumatic transport (vacuuming).  Care should be taken not to apply more than 20 pounds per square foot pressure when wind-rowing gravel.

1.11.9.1.3
At no time shall gravel carts or power scoops be allowed on the roof.

1.11.9.1.4
The Contractor shall not allow any stock pile of removed gravel to remain on NASA property over night without prior approval of the Lockheed Martin Construction Engineer.

1.11.9.1.5
The Contractor shall inspect all items of work which are to be removed and replaced in order to facilitate the work.  Damaged or faulty work shall be reported in writing to the Lockheed Martin Construction Engineer and acknowledged prior to removal.

1.11.9.1.6
Materials shall be removed only to the extent necessary to facilitate the work required under this Contract unless otherwise indicated.

1.11.9.1.7
Materials shall be replaced using materials and methods equal to those employed in the original installation or as specified herein and shown on the design drawings. The Contractor shall furnish all necessary replacement fasteners and accessory items as required to reinstall items.

1.11.9.1.8
All operational items shall be tested for proper function and made to perform properly as part of this work.

1.11.9.2
Felt, Asphalt, and Insulation
1.11.9.2.1
Only that area that can be replaced by the end of each work day shall be allowed to be torn off.

1.11.9.2.2
Completely remove all roofing material and dispose of daily.  Clean and repair decking to receive new material.

1.11.9.2.3
Care should be taken not to contaminate new work, adjacent equipment, or personnel with the debris.

1.11.9.2.4
All debris shall be removed from site daily and disposed of unless authorized in writing by the Lockheed Martin Construction Engineer.  In no way shall such stock piles during the operation present a hazard to person or property or restrict plant operations.

1.11.9.3
Deck Inspection
1.11.9.3.1
Notification of Exposed Decking


When any area of the decking is exposed, the Lockheed Martin Construction Engineer shall be notified by the Contractor to inspect the same before any new material is placed.

1.11.9.3.2
Inspection


The Contractor shall inspect the roof deck, roof drainage, eaves, base flashing locations, expansion joints, wood nailers, pipes, and all penetrations extending through the roof before starting the roof system installation and shall inform the Lockheed Martin Construction Engineer in writing of all unsatisfactory conditions.  The Contractor shall check for a smooth and uniform level deck free of deterioration to insure proper attachment of the insulation.  If no discrepancies are reported to the Lockheed Martin Construction Engineer, the Contractor accepts the deck as suitable to receive his work procedures, equipment, and material.

1.11.9.3.3
Preparation


The surfaces on which roofing and flashings are to be applied shall be free from ice, frost, moisture, dirt, projections, and foreign materials and shall be smooth and firm.  Rigid insulation shall be securely fastened to the roof deck.  Vents and other items penetrating the roof shall be secured in position and prepared for flashing.  Cant strips shall be in place, set in a solid coat of roofing cement on top of insulation.

1.11.9.4
Repair Wood Deck
1.11.9.4.1
Wood Deck Repairs


Wood deck irregularities shall be repaired as follows:


1.
Pour dry-applied leveling compound from bag to fill irregularities between planks.


2.
Screen loose leveling compound between deck irregularities, and then tamp to approximately 75 percent of its loose thickness.  The vapor barrier can then be applied without delay.  Consult manufacturer's literature for additional application procedures.


3.
Bags of leveling compound not used in this project shall be stored on the site as directed by the Lockheed Martin Construction Engineer.

1.11.9.4.2
Roof Penetrations and Equipment To Be Removed


Where existing roof penetrations and equipment are indicated on drawings to be removed, close up openings left in roof deck as follows:


1.
For openings up to 2'-0" in size (four square feet), furnish and install 1/4 inch steel plate reinforced as detailed on drawings, set in roofing cement.  Cope out bottom of new roof insulation to fit over steel plate.  Cope cellular glass with a scoop, chisel, adze, or knife in a workmanlike manner.  Openings less than 1'-0" in size require no reinforcement.


2.
Approximately four steel plates varying in size will be required.

1.11.9.4.3
Deck Repair


The roof deck shall be considered to include but not be limited to the tongue and groove wood planking, joists, and joist girders.  The extent of work shall be as follows:


1.
Replacement operations shall not begin until personnel in office areas below have been evacuated.


2.
Furnish all labor and materials required to install the following as part of the contract:



20 - 1"x6"x20' tongue and groove wood planks



5 - 2"x10"x16' joists



3 - 8"x 14"x16' joist girders


3. 
Keep on hand a minimum of ten 1"x6"x20' wood planks, three 2"x10"x16' wood joists, and two 8"x14"x16' wood joist girders at all times.


4.
Wood decking materials not used in this project shall be stored on site in a location as directed by the Lockheed Martin Construction Engineer.

1.11.9.5
Vapor Barrier Application

Install one layer of #43 base sheet in shingle fashion, starting in valley up roof to ridge.  Lap each ply four inches.  Attach vapor barrier using roofing nails.  Nail 12 inches on center both ways.  Turn vapor barrier up on vertical surfaces.

1.11.9.6
Insulation Installation

Install insulation using mechanical fasteners (four minimum per board).  Bowed boards will be rejected.  Except where damaged ones can be trimmed to fit at irregular areas, use only undamaged boards.  Board contact and attachment will be spot checked by lifting boards.

1.11.9.7
Asphalt
1.11.9.7.1
Heat asphalt to a uniform temperature throughout the kettle.  Type IV asphalt is to be utilized throughout the entire system.  The maximum allowable temperature in the kettle is 500°F.  Kettles exceeding the maximum allowable temperature for any period of time must be emptied and the asphalt removed from the job site at Contractor's expense.

1.11.9.7.2
The minimum temperature at the time and point of application is 350°F.  Where the minimum application temperature cannot be maintained at the felt laying, do not apply roofing.  Roofing installed with asphalt below the minimum allowable temperature shall be removed from the job site at the Contractor's expense.

1.11.9.8
Applying Felts
1.11.9.8.1
Place roofing felts so that they are at a right angle to deck slope, beginning at low point of deck and also so that they are parallel to the long dimension of the roof area.  The dimensions of a roof are from edge to edge of any continuous expanse of roof deck between expansion joints or parapets.  Install the four ply shingle fashion (no phase application allowed).

1.11.9.8.2
Apply roofing felts immediately following insulation application as a continuous operation.  Lay all felts flat and "broom" them in with brooms or squeegees as wide as the felts, to insure complete bonding with the asphalt.  The asphalt must run out from the low edge of the felt (three inches minimum).  At no point shall felt contact felt.

1.11.9.8.3
Do not permit felt to "fish mouth", wrinkle, or buckle.  "Broom" ends of felt to prevent curl up.  Shingle and interlock the ends of the felt into each other.

1.11.9.8.4
Interply moppings of asphalt shall be at the rate of 30 pounds per 100 square feet per ply.

1.11.9.8.5
Carry each layer of felt to top of cant strip.

1.11.9.8.6
Install water cutoffs at the end of each day's work.  Remove cutoffs prior to resuming work.

1.11.9.8.7
The entire roofing system (vapor barrier, insulation, and four ply roof) shall be completed each day in its entirety.  No phased application will be accepted.  At the end of each day's work or if inclement weather is threatening, glaze coat the last exposed layer of felt with 15# of asphalt per square.  Work shall not begin again where there is any moisture present on the glaze coat.

1.11.9.8.8
After at least 30 days have elapsed, install an asphaltic emulsion to roof surfaces at the minimum rate of two gallons per square.  Emulsion shall be brushed on.  The Contractor shall protect building surfaces from washoff.  The Contractor shall be responsible for cleanup and/or recoating if required.

1.11.9.8.9
After at least 60 days have elapsed since the emulsion has been installed, apply the aluminum coating to all exposed surfaces at the rate of one gallon per square.

1.11.9.9
Base Flashing Application
1.11.9.9.1
Install base flashing at intersections of roof with vertical surfaces and roof penetrations.  Install immediately after placing top roofing ply.

1.11.9.9.2
Apply a uniform coating of roofing cement.  Embed one ply of glass fiber felt extending one inch out from toe of the cant, up cant and face of wall for distance shown on drawings.  Lap ends six inches and seal with roofing cement.

1.11.9.9.3
Apply a second uniform coating of roofing cement and embed a second layer of glass fiber felt the same as the first except that it shall extend two inches beyond the first layer of base flashing.  Lap ends six inches and seal with roofing cement.

1.11.9.9.4
Apply a third uniform coating of roofing cement and embed one ply of reinforced glass fiber flashing felt extending two inches beyond the toe of two plies.  Lap ends six inches and seal with roofing cement.  The length of the fiber flashing felt shall not exceed 12 feet.

1.11.9.9.5
Strip edge of reinforced flashing felt with six inches width of glass fiber felt and set in uniform coating of roofing cement.  If the vertical and horizontal edges are to be done, the horizontal edges shall be done first.

1.11.9.9.6
Secure the base flashing at top with large head fasteners six inches 1.C. sized as indicated on drawings.

1.11.9.9.7
Refer to sheet metal details on the drawings for counterflashings, pitch pockets, and roof penetration flashings.

1.11.9.10
Sheet Metal
1.11.9.10.1
Examine the roof deck surfaces designated to receive work described in this section for conditions adversely affecting the finished work.

1.11.9.10.2
Install work in accordance with approved shop drawings and industry standards.  Sheet metal items shall be true to line without buckling, creasing, warping, or binding in finished surfaces.

1.11.9.10.3
Perform field joining of lengths as specified for shop fabrication of sheet metal items.

1.11.9.10.4
Isolate dissimilar metals to prevent electrolysis.  Separate them using ten mil self-adhesive polyethylene tape.  See the design drawings for locations of all copper piping.

1.11.9.10.5
Secure sheet metal items using continuous cleats, clips, and blind fasteners as indicated.  No exposed face fastening shall be performed.  Install the sheet metal items in 10'-0" lengths where possible.

1.11.9.10.6
Install pitch pockets at roof penetrations as noted.  The pitch pocket shall be at least four inches larger on each side than the penetration and three inches high with flanges extending four inches minimum onto the roof surface.  Fill the pocket with roofing cement.  Flash the pocket onto the roof surface with two layers of felt embedded in the flashing cement.  Extend the first felt ply six inches beyond edges of flanges; the second layer three inches beyond first ply.

1.11.9.10.7
Where detailed, provide one piece of lead flashing extending seven inches onto the roof in each direction for pipe penetrating the roof membrane.  Lap the sleeve two inches inside the pipe.  Extend the flashing over the roof surface, with two layers of the ply felt embedded in the steep asphalt.

1.11.9.10.8
Fascia flashing shall be provided for roof edges.  The sheet shall be fabricated without longitudinal joints.  Provision for expansion shall be provided at the joints.  Joints shall have a concealed clip soldered or welded near one end of each sheet to hold the adjoining sheet in a lapped position.  The clip shall be continuous, shall be the full depth of the fascia less one inch each at the top and bottom, and shall be hooked 3/4 inch over an edge strip.  The lower hooked edge shall be bent outward at an angle of 30 degrees.  The edge strip shall be in continuous ten foot lengths, 18 gauge galvanized steel with butt joints spaced approximately 1/8 inch apart.   The strip shall be fastened to the supporting construction with screws 12 inches on centers.  The strip for fascia anchorage shall be installed to form a drip and to allow the flashing to be hooked over the lower edge at least 3/4 inch.  The strip shall be of sufficient width to provide adequate bearing area to insure a rigid installation.  Roof flange of the fascia shall extend out on the roof not less than four inches and shall be set in plastic bituminous cement over the roofing felt.  Roof flange shall be nailed with nails spaced not greater than three inches on centers located within one inch of the outer edge of the flange.

1.11.10
Special Conditions
1.11.10.1
Cleanliness
1.11.10.1.1
Asphalt drippage into building or down exterior walls is not permitted.  Prevention of asphalt drippage is the Contractor's responsibility.

1.11.10.1.2
Where fascias or metal counterflashings are not installed immediately, the Contractor shall make temporary waterproof closure provisions at his expense.

1.11.10.1.3
Test cuts (and patching) are not required as a part of this contract.  However, the Lockheed Martin Construction Engineer retains the right to take test cuts at Lockheed Martin's expense at any time during the progress of the job.

1.11.10.1.4
See Lockheed Martin Construction Engineer (reference Special Conditions - Unit II of this specification) for bulk bitumen tanker parking, roofing material storage, Contractor Private Owned Vehicle parking, and the gate to be used by the Contractor's forces for ingress and egress to project.

1.11.10.2
Temporary Roofing
1.11.10.2.1
Where inclement weather impedes the roof system progress, an approved type of temporary system shall be utilized.

1.11.10.2.2
Place a vapor barrier and insulation as called for.  Place one ply of glass fiber felt over the area adhering it with hot asphalt at the rate of 30 pounds per square.  The temporary single ply membrane shall overlap onto adjacent areas 2'-0" min. in all directions.  Glaze coat this felt with asphalt at the rate of 15 pounds per square.  When conditions improve, install a complete four ply glass fiber felt membrane over the temporary membrane only after verifying that the insulation is dry (a reading of less than ten percent on the moisture meter).

1.11.11
Guaranty

The Contractor shall furnish a written guaranty that the entire roof and flashing construction will be free of leaks for a period of two years after date of acceptance of work.  The guaranty shall indicate beginning and ending dates.  In event leaks occur during the guaranty period and the Contractor is so notified, the Contractor shall repair roofing and flashing so that no leakage occurs.  Also during guaranty period, "fish mouths", blisters, and felt separations which could lead to leaks shall be repaired if in the opinion of the Lockheed Martin Construction Engineer repairs would not be a detriment to roof.  Emergency repairs performed by others shall not void guaranty.

1.11.12
Submittals
1.11.12.1
For submittals see Division VI of this specification.

1.11.12.2
The Contractor must be a manufacturer's approved applicator for the roofing materials used in this job.  Copies of manufacturer's certificate of approval shall be submitted to the Lockheed Martin Construction Engineer.

RFJ507
1.11B - 3

