2.9
ELECTRIC MOTORS
2.9.1
Energy efficient electric motors supplied with mechanical equipment specified in sections 2.1 through 2.8 shall meet or exceed the operating characteristics and efficiencies as determined by IEEE 112-E Test Standard, Method B, and as set forth by NEMA MG 1-12.53a.  Motor data sheets showing all vital information for the motors shall be submitted by the Contractor and shall be included with submitted data on mechanical equipment for approval by Lockheed Martin Corporation.

2.9.2
All electrical motors specified herein, with the exception of refrigerant cooled motors in hermetic water chillers, shall be standard NEMA frame motors, available from at least two major motor suppliers.  Special purpose motors available from only one source will not be accepted.

STD SPEC
2.9 - 1

