Copyright 2011 AIA
MasterSpec Professional
12/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238219 - FAN COIL UNITS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes ductless fan coil units and accessories.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

1. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings:

1. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Include diagrams for power, signal, and control wiring.

D. Samples: For units with factory-applied color finishes.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

A. Coordination Drawings: Floor plans, reflected ceiling plans, and other details, drawn to scale and coordinated with each other based on input from installers of the items involved:

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC Piping and Equipment." See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For fan coil units, accessories, and components, from manufacturer.

C. Field quality-control reports.

D. Sample warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Comply with NFPA 70.

"ASHRAE Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

B. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

"ASHRAE/IES 90.1 Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IES 90.1.

C. ASHRAE/IES 90.1 Compliance: Applicable requirements in ASHRAE/IES 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning."

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 SYSTEM DESCRIPTION

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Factory-packaged and -tested units rated according to AHRI 440, ASHRAE 33, and UL 1995.

2.2 DUCTLESS FAN COIL UNITS

Many additional features, which vary with each manufacturer, are available for this product. Include all features for fan coil units that are required for Project, and identify additional features for specific units in the Fan Coil Unit Schedule on Drawings.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Airtherm; a Mestek Company.

2. Carrier Corporation; a UTC company.

3. DRS Marlo Coil; part of DRS Technologies, Inc.

4. Dunham-Bush.

5. Engineered Air.

6. ENVIRO-TEC; by Johnson Controls, Inc.

7. First Company Products.

8. Greenheck Fan Corporation.

9. IEC; a subsidiary of LSB Industries, Inc.

10. McQuay International; a member of Daikin Group.

11. Nailor Industries Inc.

12. Rosemex.

13. Superior Rex.

14. Titus.

15. Trane Inc.

16. USA Coil & Air.

17. YORK; by Johnson Controls, Inc.

18. <Insert manufacturer's name>.

Fan coil units come with various coil configurations, the most typical being split coil systems with one heating and three cooling coils. The coils tend to be row split rather than face split, although both configurations are available. Units can also come with either a two-pipe or a four-pipe system, depending on Project design requirements.

C. Fan Coil Unit Configurations: [Row] [Face] split.

1. Number of Heating Coils: [One] <Insert number> with two-pipe system.

2. Number of Cooling Coils: [One] [Three] with [two][four]-pipe system.

Retain one of two "Coil Section Insulation" paragraphs below for coil section insulation.

Closed-cell insulation with foil or matt facing is provided by some manufacturers to reduce the possibility of fibers from glass-fiber insulation being introduced into the conditioned space.

D. Coil Section Insulation: [1/2-inch- (13-mm-)] [1-inch- (25-mm-)] <Insert dimension> thick, [coated glass fiber] [foil-covered, closed-cell foam] [matte-finish, closed-cell foam] complying with ASTM C 1071 and attached with adhesive complying with ASTM C 916.

1. Surface-Burning Characteristics: Insulation and adhesive shall have a combined maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84 by a qualified testing agency.

"Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain subparagraph to comply with LEED Prerequisite IEQ 1.

2. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

E. Coil Section Insulation: Insulate coil section according to Section 230616 "HVAC Equipment Insulation."

1. Surface-Burning Characteristics: Insulation and adhesive shall have a combined maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84 by a qualified testing agency.

"Airstream Surfaces" Subparagraph below may be required to comply with Project requirements or authorities having jurisdiction. Retain subparagraph to comply with LEED Prerequisite IEQ 1.

2. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Removable drain pans are an extra feature with some manufacturers.

"(Main and Auxiliary )Drain Pans" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1.

F. [Main and Auxiliary ]Drain Pans: [Plastic] [Stainless steel] [Insulated galvanized steel with plastic liner]. Fabricate pans and drain connections to comply with ASHRAE 62.1.[ Drain pans shall be removable.]

G. Chassis: Galvanized steel where exposed to moisture[, with baked-enamel finish and removable access panel][, with powder-coat finish and removable access panel]. Floor-mounting units shall have leveling screws.

Coordinate custom-color requirements in "Cabinet" Paragraph below with sample submittal requirements. Coordinate field painting with Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."

H. Cabinet: Steel with [factory prime coating, ready for field painting] [baked-enamel finish in manufacturer's standard paint color as selected by Architect] [baked-enamel finish in manufacturer's custom paint color as selected by Architect].

1. Vertical Unit Front Panels: Removable, steel, with [integral stamped] [polyethylene] [steel] discharge grille and channel-formed edges, cam fasteners, and insulation on back of panel.

2. Horizontal Unit Bottom Panels: Fastened to unit with cam fasteners and hinge and attached with safety chain; with [integral stamped] [cast-aluminum] discharge grilles.

Retain "Stack Unit Discharge and Return Grille" Subparagraph below for stack-type fan coil unit.

3. Stack Unit Discharge and Return Grille: Aluminum double-deflection discharge grille, and louvered- or panel-type return grille; color as selected by Architect from manufacturer's [standard] [custom] colors. Return grille shall provide maintenance access to fan coil unit.

4. Steel recessing flanges for recessing fan coil units into ceiling or wall.

Verify available filter types with manufacturer. Indicate filter thickness in "Capacities and Characteristics" Paragraph or in the Fan Coil Unit Schedule on Drawings.

For further information on air filters and air filter ratings, see Section 234100 "Particulate Air Filtration."

I. Filters: Minimum arrestance and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2 and all addendums.

Retain "MERV Rating" Subparagraph below to require compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher. Also, retain subparagraph for LEED Prerequisite IEQ 1. LEED-NC, LEED-CI, and LEED for Schools Credit IEQ 3.1 and LEED-CS Credit IEQ 3 require that filters have a minimum MERV 13 rating for systems that deliver air to occupied spaces

1. MERV Rating: [6] [13] <Insert number> when tested according to ASHRAE 52.2.

Retain one or more of three subparagraphs below. Indicate filter type in the Fan Coil Unit Schedule on Drawings. 2-inch- (50-mm-) thick washable foam is unavailable. Retain third subparagraph if applying for LEED certification. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher.

2. Washable Foam: 70 percent arrestance and MERV[ 3].

3. Glass Fiber Treated with Adhesive: 80 percent arrestance and MERV[ 5].

4. Pleated Cotton-Polyester Media: 90 percent arrestance and MERV[ 7].

J. Hydronic Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm), rated for a minimum working pressure of 200 psig (1378 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C). Include manual air vent and drain valve.

Some manufacturers limit air-to-air heat pumps to electric supplemental heating coils.

K. Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with fuses in terminal box for overcurrent protection and limit controls for high-temperature protection. Terminate elements in stainless-steel machine-staked terminals secured with stainless-steel hardware.

L. Fan and Motor Board: Removable.

1. Fan: Forward curved, double width, centrifugal; directly connected to motor. Thermoplastic or painted-steel wheels, and aluminum, painted-steel, or galvanized-steel fan scrolls.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

2. Motor: Permanently lubricated, multispeed; resiliently mounted on motor board. Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

3. Wiring Termination: Connect motor to chassis wiring with plug connection.

Retain "Factory, Hydronic Piping Package" Paragraph below to suit Project. Delete if factory piping package is not required.

M. Factory, Hydronic Piping Package: [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M Type C)] copper tube with wrought-copper fittings and brazed joints. Label piping to indicate service, inlet, and outlet.

Retain one or more of first four subparagraphs below.

1. [Two][Three]-way, [two-position] [modulating] control valve for dual-temperature coil.

2. [Two][Three]-way, [two-position] [modulating] control valve for chilled-water coil.

3. [Two][Three]-way, [two-position] [modulating] control valve for hot-water heating coil.

4. Hose Kits: Minimum 400-psig (2758-kPa) working pressure and operating temperatures from 33 to 211 deg F (0.5 to 99 deg C). Tag hose kits to equipment designations.

a. Length: [24 inches (600 mm)] [36 inches (900 mm)] <Insert dimension>.

b. Minimum Diameter: Equal to fan coil unit connection size.

5. Two-Piece Ball Valves: Bronze body with full-port, chrome-plated bronze ball; PTFE or TFE seats; and 600-psig (4140-kPa) minimum CWP rating and blowout-proof stem.

6. Calibrated-Orifice Balancing Valves: Bronze body, ball type; 125-psig (860-kPa) working pressure, 250 deg F (121 deg C) maximum operating temperature; with calibrated orifice or venturi, connections for portable differential pressure meter with integral seals, threaded ends, and a memory stop to retain set position.

7. Automatic Flow-Control Valve: Brass or ferrous-metal body; 300-psig (2070-kPa) working pressure at 250 deg F (121 deg C); with removable, corrosion-resistant, tamperproof, self-cleaning piston spring; factory set to maintain constant indicated flow with plus or minus 10 percent over differential pressure range of 2 to 80 psig (13.8 to 552 kPa).

8. Y-Pattern Hydronic Strainers: Cast-iron body (ASTM A 126, Class B); 125-psig (860-kPa) working pressure; with threaded connections, bolted cover, perforated stainless-steel basket, and bottom drain connection. Include minimum NPS 1/2 (DN 15) hose-end, full-port, ball-type blowdown valve in drain connection.

9. Wrought-Copper Unions: ASME B16.22.

Retain "Risers" Subparagraph below for stack-type units with hydronic coils.

10. Risers: [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M Type C)] copper pipe with hose and ball valve for system flushing.

N. Control devices and operational sequences are specified in Section 230900 "Instrumentation and Control for HVAC" and Section 230993 "Sequence of Operations for HVAC Controls."

Retain last paragraph above and delete "Basic Unit Controls" Paragraph below if controls are part of overall temperature-control system.

O. Basic Unit Controls:

1. Control voltage transformer.

Verify control features with manufacturer.

2. [Wall-mounting] [Unit-mounted] thermostat with the following features:

a. Heat-cool-off switch.

b. Fan on-auto switch.

Retain first subparagraph below if multispeed motors are specified.

c. Fan-speed switch.

d. [Manual] [Automatic] changeover.

e. Adjustable deadband.

f. [Concealed] [Exposed] set point.

g. [Concealed] [Exposed] indication.

h. [Degree F] [Degree C] indication.

3. [Wall-mounting] [Unit-mounted] humidistat.

a. [Concealed] [Exposed] set point.

b. [Concealed] [Exposed] indication.

4. [Wall-mounting] [Unit-mounted] temperature sensor.

5. Unoccupied-period-override push button.

6. Data entry and access port.

a. Input data includes room temperature, and humidity set points and occupied and unoccupied periods.

b. Output data includes room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

Retain "(DDC )Terminal Controller" Paragraph below and coordinate with "Basic Unit Controls" Paragraph above or with control devices specified in Section 230900 "Instrumentation and Control for HVAC."

P. [DDC ]Terminal Controller:

1. Scheduled Operation: Occupied and unoccupied periods on seven-day clock with a minimum of four programmable periods per day.

2. Unoccupied-Period-Override Operation: [Two] <Insert number> hours.

3. Unit Supply-Air Fan Operation:

a. Occupied Periods: Fan runs continuously.

b. Unoccupied Periods: Fan cycles to maintain room setback temperature.

4. Hydronic-Cooling-Coil Operation:

a. Occupied Periods: [Open] [Modulate] control valve to maintain room temperature.

b. Unoccupied Periods: Close control valve.

5. [Supplemental ]Heating-Coil Operation:

a. Occupied Periods: [Open control valve] [Modulate control valve] [Energize electric-resistance coil] to provide heating if room temperature falls below thermostat set point.

b. Unoccupied Periods: Start fan and [open control valve] [modulate control valve] [energize electric-resistance coil] if room temperature falls below setback temperature.

6. Dual-Temperature Hydronic-Coil Operation:

a. Occupied Periods: When chilled water is available, [open] [modulate] control valve if room temperature exceeds thermostat set point. When hot water is available, open control valve if temperature falls below thermostat set point.

b. Unoccupied Periods: When chilled water is available, close control valve. When hot water is available, [open] [modulate] control valve if room temperature falls below thermostat setback temperature.

7. Controller shall have volatile-memory backup.

Q. Electrical Connection: Factory wire motors and controls for a single electrical connection.

If Project has more than one type or configuration of fan coil unit, delete "Capacities and Characteristics" Paragraph below and schedule fan coil units on Drawings.

R. Capacities and Characteristics:

1. Fan:

a. Airflow: <Insert cfm (L/s)>.

b. External Static Pressure: <Insert inches wg (kPa)>.

c. Fan Speed: <Insert rpm>.

d. Motor Speed: <Insert rpm>.

e. Motor Horsepower: <Insert horsepower>.

f. Drive: [Direct] [Belt].

2. Cooling Capacity:

a. Total: <Insert Btu/h (kW)>.

b. Sensible: <Insert Btu/h (kW)>.

c. Entering-Air Dry-Bulb Temperature: <Insert deg F (deg C)>.

d. Entering-Air Wet-Bulb Temperature: <Insert deg F (deg C)>.

3. Chilled-Water Coil:

a. Water Flow: <Insert gpm (L/s)>.

b. Water-Side Pressure Loss: <Insert feet wg (kPa)>.

c. Entering-Water Temperature: <Insert deg F (deg C)>.

d. Air-Side Pressure Drop: <Insert inches wg (kPa)>.

4. Heating Capacity:

a. Output: <Insert Btu/h (kW)>.

b. Entering-Air Temperature: <Insert deg F (deg C)>.

c. Air-Temperature Rise: <Insert deg F (deg C)>.

5. Hot-Water Heating Coil:

a. Water Flow: <Insert gpm (L/s)>.

b. Water-Side Pressure Loss: <Insert feet wg (kPa)>.

c. Air-Side Pressure Drop: <Insert inches wg (kPa)>.

d. Entering-Water Temperature: <Insert deg F (deg C)>.

6. Electric-Resistance Heating Coil:

a. Capacity: <Insert kilowatts>.

b. Number of Steps: <Indicate number>.

c. Air-Side Pressure Drop: <Insert inches wg (kPa)>.

7. Filters:

a. Face Area: <Insert sq. ft. (sq. m)>.

b. Thickness: [1 inch (25 mm)] [2 inches (50 mm)] <Insert dimension>.

8. Electrical Characteristics for Single-Point Connection:

a. Voltage/Phase/Hertz: <Insert values>.

b. Full-Load Amperes: <Insert value>.

c. Maximum Circuit Amperes: <Insert value>.

d. Maximum Overcurrent Protection: <Insert amperage>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install fan coil units level and plumb.

B. Install fan coil units to comply with NFPA 90A.

Retain first paragraph below for horizontal, suspended units.

C. Suspend fan coil units from structure with elastomeric hangers. Vibration isolators are specified in Section 230548 "Vibration and Seismic Controls for HVAC Piping and Equipment."

Verify mounting height in first paragraph below with authorities having jurisdiction to comply with requirements of the Americans with Disabilities Act.

D. Verify locations of thermostats, humidistats, and other exposed control sensors with Drawings and room details before installation. Install devices [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension> above finished floor.

E. Install new filters in each fan coil unit within two weeks after Substantial Completion.

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

F. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties. Specific connection requirements are as follows:

1. Install piping adjacent to machine to allow service and maintenance.

2. Connect piping to fan coil unit factory hydronic piping package. Install piping package if shipped loose.

3. Connect condensate drain to indirect waste.

Retain subparagraph below for concealed fan coil units.

a. Install condensate trap of adequate depth to seal against fan pressure. Install cleanouts in piping at changes of direction.

G. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

H. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.2 FIELD QUALITY CONTROL

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Retain first subparagraph below if units have electric heat.

2. Operate electric heating elements through each stage to verify proper operation and electrical connections.

3. Test and adjust controls and safety devices. Replace damaged and malfunctioning controls and equipment.

B. Remove and replace malfunctioning units and retest as specified above.

C. Prepare test and inspection reports.

3.3 ADJUSTING

Retain this article if control devices are specified in this Section; delete if they are specified in Section 230900 "Instrumentation and Control for HVAC" and Section 230993 "Sequence and Operations for HVAC Controls."

A. Adjust initial temperature and humidity set points.

B. Occupancy Adjustments: When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

END OF SECTION 238219
	FAN COIL UNITS
	238219 - 1



