Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana

Technical Specifications

SECTION 08311 – ACCESS DOORS AND FRAMES 
PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes access doors and frames for walls and ceilings.

1.2 SUBMITTALS

A. Product Data:  For each type of access door and frame indicated.

B. Shop Drawings:  Include plans, elevations, sections, details, and attachments to other work.

C. Samples:  For each door face material in specified finish.

D. Schedule:  Types, locations, sizes, latching or locking provisions, and other data pertinent to installation.

1.3 QUALITY ASSURANCE

A. Fire-Rated Access Doors and Frames:  Units complying with NFPA 80 that are identical to assemblies tested for fire-test-response characteristics per the following test method and that are listed and labeled by UL or another testing and inspecting agency acceptable to authorities having jurisdiction: 

1. NFPA 252 or UL 10B for vertical access doors and frames.

2. ASTM E 119 or UL 263 for horizontal access doors and frames.

1.4 COORDINATION

A. Verification:  Determine specific locations and sizes for access doors needed to gain access to concealed plumbing, mechanical, or other concealed work, and indicate in the schedule specified in "Submittals" Article.

PART 2 -  PRODUCTS
2.1 STEEL MATERIALS

Select materials from this Article or revise to suit Project.

A. Steel Plates, Shapes, and Bars:  ASTM A 36/A 36M.

1. ASTM A 123/A 123M, for galvanizing steel and iron products.

2. ASTM A 153/A 153M, for galvanizing steel and iron hardware.

B. Steel Sheet:  Uncoated or electrolytic zinc-coated, ASTM A 591/A 591M with cold-rolled steel sheet substrate complying with ASTM A 1008/A 1008M, Commercial Steel (CS), exposed.

C. Metallic-Coated Steel Sheet:  ASTM A 653/A 653M, Commercial Steel (CS) with A60 (ZF180) zinc-iron-alloy (galvannealed) coating or G60 (Z180) mill-phosphatized zinc coating.

Verify prime finish is acceptable (field painting is required).  If exterior locations are required, need to specify other finish.
D. Steel Finishes:  Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

1. Factory-Primed Finish:  Manufacturer's standard shop primer.

E. Drywall Beads:  0.0299-inch (0.76-mm) zinc-coated steel sheet to receive joint compound.

Verify no plaster beads required.

2.2 ACCESS DOORS AND FRAMES FOR WALLS AND CEILINGS

A. Flush Access Doors and Frames with Exposed Trim:  Fabricated from steel sheet.

Specify galvanized for exterior locations, if any.
1. Locations:  Wall and ceiling.

2. Door:  Minimum  0.0329-inch- (0.70-mm-) thick sheet metal.

3. Frame:  Minimum 0.060-inch- (1.5-mm-) thick sheet metal with 1-inch- (25-mm-) wide, surface-mounted trim.

4. Hinges:  Continuous piano.

5. Lock:  Mortise cylinder.

B. Fire-Rated, Insulated, Flush Access Doors and Frames with Exposed Trim:  Fabricated from steel sheet.

1. Locations:  Wall and ceiling surfaces.

2. Fire-Resistance Rating:  Not less than  that of adjacent construction.

3. Temperature Rise Rating:  250 deg F (139 deg C) at the end of 30 minutes.

4. Door:  Flush panel with a core of mineral-fiber insulation enclosed in sheet metal with a minimum thickness of 0.0428 inch (1.1 mm).

5. Frame:  Minimum 0.060-inch- (1.5-mm-) thick sheet metal with 1-inch- (25-mm-) wide, surface-mounted trim.

6. Hinges:  Continuous piano.

7. Automatic Closer:  Spring type.

8. Lock:  Self-latching device with  mortise cylinder lock.

2.3 FABRICATION

A. General:  Provide access door and frame assemblies manufactured as integral units ready for installation.

B. Metal Surfaces:  For metal surfaces exposed to view, provide materials with smooth, flat surfaces without blemishes.

C. Doors and Frames:  Grind exposed welds smooth and flush with adjacent surfaces.  Furnish attachment devices and fasteners of type required to secure access panels to types of supports indicated.

D. Latching Mechanisms:  Furnish number required to hold doors in flush, smooth plane when closed.

1. For cylinder lock, furnish two keys per lock and key all locks alike.

PART 3 -  EXECUTION
3.1 INSTALLATION

A. Comply with manufacturer's written instructions for installing access doors and frames.

B. Install doors flush with adjacent finish surfaces or recessed to receive finish material.

3.2 ADJUSTING AND CLEANING

A. Adjust doors and hardware after installation for proper operation.

B. Remove and replace doors and frames that are warped, bowed, or otherwise damaged.

END OF SECTION 08311

ACCESS DOORS AND FRAMES

08311 - 3

