Louisiana Army National Guard

Preliminary Review Documents

141st Readiness Center (RC)

Jackson Barracks, New Orleans, Louisiana   

Technical Specifications


MASTERSPEC Short Form Copyright 2003 (R 06/01) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16410 - ENCLOSED SWITCHES AND CIRCUIT BREAKERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following individually mounted, enclosed switches and circuit breakers:

Adjust list below to suit Project.

1. Fusible switches.

2. Nonfusible switches.

3. Molded-case circuit breakers.

4. Enclosures.

1.2 SUBMITTALS

A. Product Data:  For each type of enclosed switch, circuit breaker, accessory, and component indicated.

B. Shop Drawings:  Diagram power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and maintenance data.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2.2 FUSIBLE AND NONFUSIBLE SWITCHES

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. Manufacturers:

1. Eaton Corporation; Cutler-Hammer Products.

2. General Electric Co.; Electrical Distribution & Control Division.

3. Siemens Energy & Automation, Inc.

4. Square D/Group Schneider.

In first two paragraphs below, select "GD" option for switches for light-commercial applications, 240 V, 30 to 600 A; otherwise, select "HD" option.  See Editing Instruction No. 2 in the Evaluations.

B. Fusible Switch, 1200 A and Smaller:  NEMA KS 1, Type HD, with clips or bolt pads to accommodate specified fuses, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

C. Nonfusible Switch, 1200 A and Smaller:  NEMA KS 1, Type HD, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

D. Accessories:

Retain selected subparagraphs below with either switch paragraph above.  Verify that accessories specified are available and appropriate for switch types and ratings specified.

1. Equipment Ground Kit:  Internally mounted and labeled for copper and aluminum ground conductors.

2. Neutral Kit:  Internally mounted; insulated, capable of being grounded, and bonded; and labeled for copper and aluminum neutral conductors.

3. Auxiliary Contact Kit:  Auxiliary set of contacts arranged to open before switch blades open.

2.3 MOLDED-CASE CIRCUIT BREAKERS AND SWITCHES

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. Manufacturers:

1. Eaton Corporation; Cutler-Hammer Products.

2. General Electric Co.; Electrical Distribution & Control Division.

3. Moeller Electric Corporation.

4. Siemens Energy & Automation, Inc.

5. Square D/Group Schneider.

B. Molded-Case Circuit Breaker:  NEMA AB 1, with interrupting capacity to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Adjustable Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

3. Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller and let-through ratings less than NEMA FU 1, RK-5.

4. GFCI Circuit Breakers:  Single- and two-pole configurations with [5] [30]-mA trip sensitivity.

C. Molded-Case Circuit-Breaker Features and Accessories:

Verify that accessories retained below are available and appropriate for circuit-breaker types and ratings specified.

1. Standard frame sizes, trip ratings, and number of poles.

2. Lugs:  Mechanical style with compression lug kits suitable for number, size, trip ratings, and conductor material.

3. Application Listing:  Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

4. Ground-Fault Protection:  Integrally mounted relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

5. Shunt Trip:  120-V trip coil energized from separate circuit, set to trip at 55 percent of rated voltage.

2.4 ENCLOSURES

A. NEMA AB 1 and NEMA KS 1 to meet environmental conditions of installed location.

Identify enclosure types on Drawings.  See Evaluations and Editing Instruction No. 2 in the Evaluations for discussion of enclosures.

1. Outdoor and other Wet or Damp Indoor Locations:  NEMA 250, Type 4X stainless steel
PART 3 -  EXECUTION

3.1 INSTALLATION

A. Coordinate size and location of concrete bases.  Verify structural requirements with structural engineer.

B. Comply with applicable portions of NECA 1, NEMA PB 1.1, and NEMA PB 2.1 for installation of enclosed switches and circuit breakers.

C. Mount individual wall-mounting switches and circuit breakers with tops at uniform height, unless otherwise indicated.  Anchor floor-mounting switches to concrete base.

Retain first paragraph below if seismic controls are required for Project.  Coordinate with Drawings.

D. Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

E. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 16 Section Electrical Identification.

3.2 FIELD QUALITY CONTROL

A. Prepare for acceptance testing as follows:

1. Inspect mechanical and electrical connections.

2. Verify switch and relay type and labeling verification.

3. Verify rating of installed fuses.

B. Perform the following field tests and inspections and prepare test reports:

Tests referenced in first subparagraph below are from NETA ATS, 1999 edition, and include inspection procedures to verify proper operation.  They also include tests and measurements of insulation resistance and, for circuit breakers, trip currents to ensure proper calibration.  The cost of extensive testing may not be warranted for some projects.

1. Perform each electrical test and visual and mechanical inspection stated in NETA ATS, Section 7.5 for switches and Section 7.6 for molded-case circuit breakers.  Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

END OF SECTION 16410

ENCLOSED SWITCHES AND CIRCUIT BREAKERS
16410 - 2

