Copyright 2000 and 2005 AIA
MASTERSPEC Full Length
02/00 (R 05/06)

Copyright 2000 and 2005, The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 075400 - THERMOPLASTIC MEMBRANE ROOFING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Adhered membrane roofing system.

2. Mechanically fastened membrane roofing system.

3. Loosely laid and ballasted membrane roofing system.

4. Loosely laid and ballasted, protected membrane roofing system.

5. Vapor retarder.

6. Roof insulation.

Delete first paragraph below if no acoustical roof deck is required.

B. This Section includes the installation of acoustical roof deck rib insulation strips furnished under Division 05 Section "Steel Decking."

C. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 05 Section "Steel Decking" for furnishing acoustical deck rib insulation.

2. Division 06 Section "[Rough Carpentry] [Miscellaneous Rough Carpentry]" for wood nailers, curbs, and blocking[ and for wood-based, structural-use roof deck panels].

3. Division 07 Section "Thermal Insulation" for insulation beneath the roof deck.

4. Division 07 Section "Sheet Metal Flashing and Trim" for metal roof penetration flashings, flashings, and counterflashings.

5. Division 07 Section "Manufactured Roof Expansion Joints."

6. Division 07 Section "Joint Sealants."

7. Division 22 Section "Storm Drainage Piping Specialties" for roof drains.

Unit prices may be required in bid documents.  One example is removal and replacement of wet roof insulation that may be discovered during reroofing.

D. Unit Prices:  Refer to Division 01 Section "Unit Prices" for description of Work in this Section affected by unit prices.

If alternates or allowances apply to work of this Section, insert brief paragraphs here to alert Contractor and reference appropriate Division 01 Section for specific details.

1.3 DEFINITIONS

A. Roofing Terminology:  Refer to ASTM D 1079 and glossary of NRCA's "The NRCA Roofing and Waterproofing Manual" for definition of terms related to roofing work in this Section.

Retain two definitions below if design uplift pressure subparagraphs based on SPRI's "Wind Load Design Guide for Fully Adhered and Mechanically Fastened Roofing Systems" are retained in "Performance Requirements" Article.  The membrane roofing system must resist, at a minimum, design uplift pressure.  Design uplift pressure, multiplied by a safety factor, produces the factored design uplift pressure.

B. Design Uplift Pressure:  The uplift pressure, calculated according to procedures in SPRI's "Wind Load Design Guide for Fully Adhered and Mechanically Fastened Roofing Systems," before multiplication by a safety factor.

C. Factored Design Uplift Pressure:  The uplift pressure, calculated according to procedures in SPRI's "Wind Load Design Guide for Fully Adhered and Mechanically Fastened Roofing Systems," after multiplication by a safety factor.

1.4 PERFORMANCE REQUIREMENTS

A. General:  Provide installed roofing membrane and base flashings that remain watertight; do not permit the passage of water; and resist specified uplift pressures, thermally induced movement, and exposure to weather without failure.

B. Material Compatibility:  Provide roofing materials that are compatible with one another under conditions of service and application required, as demonstrated by roofing membrane manufacturer based on testing and field experience.

Retain paragraph and subparagraphs below if membrane roofing system is to be designed to withstand uplift pressure established by ASCE 7.  Revise design uplift pressures in subparagraphs if local building code requirements are more stringent than ASCE 7.  Retain with "FMG Listing" Paragraph and subparagraphs below if both ASCE 7 and FMG criteria may apply.  Delineate dimensions of corners, perimeter, and field of roof on Drawings.  Delete below if a loosely laid and ballasted membrane roofing system is required.

C. Roofing System Design:  Provide a membrane roofing system that is identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist uplift pressure calculated according to ASCE 7.

1. Corner Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

2. Perimeter Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

3. Field-of-Roof Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

Retain paragraph and subparagraphs below if Project is FMG insured or if FMG requirements will set a minimum quality standard.  Coordinate requirements of FMG classification with other requirements in this Section.  Loosely laid and ballasted membrane roofing systems cannot be FMG approved but may be accepted by FMG on a project-by-project basis.

D. FMG Listing:  Provide roofing membrane, base flashings, and component materials that comply with requirements in FMG 4450 and FMG 4470 as part of a membrane roofing system and that are listed in FMG's "Approval Guide" for Class 1 or noncombustible construction, as applicable.  Identify materials with FMG markings.

Select one option in first subparagraph below based on windstorm classification of Project.  FMG Loss Prevention Data Sheet 1-28 multiplies the actual field-of-roof uplift pressure by a factor of 2 to obtain the factored pressure, the number that establishes the minimum FMG approval rating.  Verify availability of roofing systems that meet these classifications.  Other options for classifications increase in increments of 15, e.g., Class 1A-135, 1A-150, 1A-165, and higher.  "Class 1A" signifies meeting ASTM E 108, Class A fire performance for FMG-approved Class 1 roof covers.  For areas having three or more hailstorms annually, FMG recommends roofing systems rated SH (severe hail) instead of MH (moderate hail).

1. Fire/Windstorm Classification:  Class 1A-[60] [75] [90] [105] [120] <Insert number>.

2. Hail Resistance:  [MH] [SH].

Retain paragraph and subparagraphs below if membrane roofing system is to be designed to withstand wind loads established from SPRI's "Wind Load Design Guide for Fully Adhered and Mechanically Fastened Roofing Systems." SPRI derives design uplift pressure using ASCE 7's wind-load procedure and increases this pressure by a safety factor.  Delete below if a loosely laid and ballasted membrane roofing system is required.

E. Roofing System Design:  Provide a membrane roofing system that is identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist the factored design uplift pressures calculated according to SPRI's "Wind Load Design Guide for Fully Adhered and Mechanically Fastened Roofing Systems."

SPRI requires the calculated design uplift pressure for each roof area to be multiplied by a safety factor to arrive at uplift resistance required of the membrane roofing system.  Delineate dimensions of corners, perimeter, and field of roof on Drawings.

1. Corner Design Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

2. Perimeter Design Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

3. Field-of-Roof Design Uplift Pressure:  <Insert number> lbf/sq. ft. (kPa/sq. m).

4. Safety Factor:  <Insert number.>

Retain paragraph below if required for LEED-NC Credit SS 7.2.  First option is minimum for roofs with slopes of 2:12 or less; second option is minimum for roofs with slopes steeper than 2:12.

F. Energy Performance:  Provide roofing system with Solar Reflectance Index not less than [78] [29] when calculated according to ASTM E 1980 based on testing identical products by a qualified testing agency.

1.5 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. LEED Submittals:

Retain subparagraph below if roof materials are required to comply with requirements for LEED-NC Credit SS 7.2; coordinate with requirements selected in Part 2 for roof materials.

1. Product Test Reports for Credit SS 7.2:  For roof materials, documentation indicating that roof materials comply with Solar Reflectance Index requirement.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1; coordinate with requirements selected in Part 2 for adhesives and sealants.

2. Product Data for Credit EQ 4.1:  For adhesives and sealants, including printed statement of VOC content.

C. Shop Drawings:  For roofing system.  Include plans, elevations, sections, details, and attachments to other Work.

Adjust list below to suit Project.

1. Base flashings and membrane terminations.

2. Tapered insulation, including slopes.

3. Insulation fastening patterns.

D. Samples for Verification:  For the following products:

Adjust list below to suit Project.

1. 12-by-12-inch (300-by-300-mm) square of sheet roofing, of color specified, including T-shaped side and end lap seam.

2. 12-by-12-inch (300-by-300-mm) square of roof insulation.

3. 10 lb (4.5 kg) of aggregate ballast in color and gradation indicated.

4. Full-size concrete roof paver in each color and texture required.

5. 12-by-12-inch (300-by-300-mm) square of walkway pads or rolls.

6. 12-inch (300-mm) length of metal termination bars.

7. 12-inch (300-mm) length of battens.

8. Six insulation fasteners of each type, length, and finish.

9. Six roof cover fasteners of each type, length, and finish.

Retain paragraph below if Installer certification is required in "Quality Assurance" Article or a special warranty is required.

E. Installer Certificates:  Signed by roofing system manufacturer certifying that Installer is approved, authorized, or licensed by manufacturer to install roofing system.

Retain paragraph and subparagraph below if "Performance Requirements" Article and either "Roofing System Design" or "FMG Listing" Paragraph are retained.

F. Manufacturer Certificates:  Signed by roofing manufacturer certifying that roofing system complies with requirements specified in "Performance Requirements" Article.

1. Submit evidence of meeting performance requirements.

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

G. Qualification Data:  For Installer and manufacturer.

H. Product Test Reports:  Based on evaluation of comprehensive tests performed by manufacturer and witnessed by a qualified testing agency, for components of roofing system.

Insert specific model code organization in first paragraph below or revise if report must be from another source.

I. Research/Evaluation Reports:  For components of membrane roofing system.

J. Maintenance Data:  For roofing system to include in maintenance manuals.

Retain paragraph below if desired.  Submittal of sample warranty provides Architect or Owner an opportunity to further verify that warranty coverage meets requirements.

K. Warranties:  Special warranties specified in this Section.

Retain below if manufacturer's final roof inspection report is required.

L. Inspection Report:  Copy of roofing system manufacturer's inspection report of completed roofing installation.

1.6 QUALITY ASSURANCE

FMG is launching a certified roofing installer program.  Add certification requirements to first paragraph below if Project is FMG insured and a certified roofing installer is required.

A. Installer Qualifications:  A qualified firm that is approved, authorized, or licensed by roofing system manufacturer to install manufacturer's product and that is eligible to receive manufacturer's warranty.

B. Manufacturer Qualifications:  A qualified manufacturer that has [UL listing] [FMG approval] for membrane roofing system identical to that used for this Project.

Retain paragraph below if Contractor selects testing agency.

C. Testing Agency Qualifications:  An independent testing agency with the experience and capability to conduct the testing indicated, as documented according to ASTM E 548.

Retain first paragraph below if required to meet provisions of special manufacturer's warranty.  Consult manufacturer's literature for requirements because they vary.

D. Source Limitations:  Obtain components for membrane roofing system [from] [or] [approved by] roofing membrane manufacturer.

E. Fire-Test-Response Characteristics:  Provide membrane roofing materials with the fire-test-response characteristics indicated as determined by testing identical products per test method below by UL, FMG, or another testing and inspecting agency acceptable to authorities having jurisdiction.  Materials shall be identified with appropriate markings of applicable testing and inspecting agency.

Retain one of three options in subparagraph below based on fire classification of roof assembly and roof covering.  Delete subparagraph if exterior fire-test exposure is included in FMG class designation in "Performance Requirements" Article above.

1. Exterior Fire-Test Exposure:  Class  [A] [B] [C]; ASTM E 108, for application and roof slopes indicated.

Delete subparagraph below if fire-resistance rating of roof assembly is not applicable.  Indicate rating, testing agency, and testing agency's design designation on Drawings.

2. Fire-Resistance Ratings:  ASTM E 119, for fire-resistance-rated roof assemblies of which roofing system is a part.

Consider retaining paragraph below if roofing installation is large and complicated.  A preliminary roofing conference would precede a preinstallation conference and focus on roof deck construction and planning activities of roofing Installer.

F. Preliminary Roofing Conference:  Before starting roof deck construction, conduct conference at Project site.  Comply with requirements for preinstallation conferences in Division 01 Section "Project Management and Coordination." Review methods and procedures related to roof deck construction and roofing system including, but not limited to, the following:

Delete subparagraphs below not required.  If retaining, revise to include Project-specific requirements.  Insert additional requirements to suit Project.

1. Meet with Owner, Architect, Owner's insurer if applicable, testing and inspecting agency representative, roofing Installer, roofing system manufacturer's representative, deck Installer, and installers whose work interfaces with or affects roofing including installers of roof accessories and roof-mounted equipment.

2. Review methods and procedures related to roofing installation, including manufacturer's written instructions.

3. Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

4. Examine deck substrate conditions and finishes for compliance with requirements, including flatness and fastening.

5. Review structural loading limitations of roof deck during and after roofing.

6. Review base flashings, special roofing details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that will affect roofing system.

7. Review governing regulations and requirements for insurance and certificates if applicable.

8. Review temporary protection requirements for roofing system during and after installation.

9. Review roof observation and repair procedures after roofing installation.

Preinstallation conference below is recommended with or without preliminary roofing conference above.

G. Preinstallation Conference:  Conduct conference at Project site.  Comply with requirements in Division 01 Section "Project Management and Coordination." Review methods and procedures related to roofing system including, but not limited to, the following:

Delete subparagraphs below not required.  If retaining, revise to include Project-specific requirements.  Insert additional requirements to suit Project.

1. Meet with Owner, Architect, Owner's insurer if applicable, testing and inspecting agency representative, roofing Installer, roofing system manufacturer's representative, deck Installer, and installers whose work interfaces with or affects roofing including installers of roof accessories and roof-mounted equipment.

2. Review methods and procedures related to roofing installation, including manufacturer's written instructions.

3. Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

4. Examine deck substrate conditions and finishes for compliance with requirements, including flatness and fastening.

5. Review structural loading limitations of roof deck during and after roofing.

6. Review base flashings, special roofing details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that will affect roofing system.

7. Review governing regulations and requirements for insurance and certificates if applicable.

8. Review temporary protection requirements for roofing system during and after installation.

9. Review roof observation and repair procedures after roofing installation.

1.7 DELIVERY, STORAGE, AND HANDLING

A. Deliver roofing materials to Project site in original containers with seals unbroken and labeled with manufacturer's name, product brand name and type, date of manufacture, and directions for storing and mixing with other components.

B. Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.  Protect stored liquid material from direct sunlight.

1. Discard and legally dispose of liquid material that cannot be applied within its stated shelf life.

C. Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Store in a dry location.  Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

D. Handle and store roofing materials and place equipment in a manner to avoid permanent deflection of deck.

1.8 PROJECT CONDITIONS

A. Weather Limitations:  Proceed with installation only when existing and forecasted weather conditions permit roofing system to be installed according to manufacturer's written instructions and warranty requirements.

1.9 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

Retain paragraph below if manufacturer's labor-and-materials warranty, covering roofing system, is required.  Verify coverage offered by manufacturers because roof insulation, fasteners, and other roofing components may be excluded unless part of roofing membrane manufacturer's roofing system warranty.  If adding special provisions, retitle paragraph "Special Roofing Manufacturer's Warranty." Verify warranty availability and coordinate choice of manufacturers in Part 2 accordingly.

A. Special Warranty:  Manufacturer's standard form, without monetary limitation, in which manufacturer agrees to repair or replace components of membrane roofing system that fail in materials or workmanship within specified warranty period.  Failure includes roof leaks.

Retain options in subparagraph below based on those used on Project.  Verify availability of manufacturer's total-system warranty and components included.

1. Special warranty includes roofing membrane, base flashings, [roofing membrane accessories] [roof insulation] [fasteners] [cover boards] [substrate board] [vapor retarder] [roof pavers] [walkway products] and other components of membrane roofing system.

Revise warranty to period required and verify availability; 10- and 15-year periods predominate.  Standard manufacturers' warranties begin on completion of roofing system.  AIA Document A201 establishes that the period begins with Substantial Completion.

2. Warranty Period:  [10] [15] years from date of Substantial Completion.

Usually delete below if retaining manufacturer's warranty above.  Manufacturer's labor-and-materials warranty typically binds Installer for the first two or three years.  If retaining special Project warranty below, use or modify sample roofing Installer's warranty form at end of this Section.  Alternatively, insert copy of local roofing contractor association's warranty form or use another form as advised by Owner's counsel.  Revise below to reflect scope of special Project warranty.

B. Special Project Warranty:  Submit roofing Installer's warranty, on warranty form at end of this Section, signed by Installer, covering Work of this Section, including all components of membrane roofing system such as roofing membrane, base flashing, roof insulation, fasteners, cover boards, substrate boards, vapor retarders, roof pavers, and walkway products, for the following warranty period:

1. Warranty Period:  [Two] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers and products, or manufacturers only, are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Products," "Products," "Available Manufacturers," and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply for product selection:

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the products specified.

2. Products:  Subject to compliance with requirements, provide one of the products specified.

3. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the manufacturers specified.

4. Manufacturers:  Subject to compliance with requirements, provide products by the manufacturers specified.

2.2 PVC ROOFING MEMBRANE

Retain one of three paragraphs and associated subparagraphs below if PVC roofing membrane is required.

Retain paragraph and subparagraphs below if requiring "Sarnafil G410" for adhered installations.

A. PVC Sheet:  ASTM D 4434, Type II, Grade 1, fiber reinforced[ and fabric backed], as follows:

Coordinate subparagraph below with Part 2 "Manufacturers" Article.

1. Product:  Subject to compliance with requirements, provide "Sarnafil G410" by Sarnafil Inc.

Select one thickness in subparagraph below or revise to suit Project.  Other thicknesses include 72, 80, and 96 mils (1.8, 2.0, and 2.4 mm); verify availability with manufacturers if required.

2. Thickness:  [48 mils (1.2 mm), minimum] [60 mils (1.5 mm), nominal] <Insert thickness>.

Verify availability of other colors with manufacturers if required.

3. Exposed Face Color:  [Gray] <Insert color>.

Retain paragraph and subparagraphs below for the most prevalent PVC roofing membrane.  Include fabric-backed option, offered by Flex Membrane International and GAF Materials Corporation, if required.

B. PVC Sheet:  ASTM D 4434, Type III, fabric reinforced[ and fabric backed].

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Duro-Last Roofing, Inc.

b. Firestone Building Products Company.

c. Flex Membrane International, Inc.

d. GAF Materials Corporation.

e. GenFlex Roofing Systems.

f. IB Roof Systems.

g. Johns Manville International, Inc.

h. Mule-Hide Products Co., Inc.

i. Sarnafil Inc.

j. <Insert manufacturer's name.>

Select one thickness in subparagraph below or revise to suit Project.  ASTM D 4434, Types II and III minimum thickness is 45 mils (1.1 mm).  Other thicknesses that may be offered include 48, 50, 72, 80, and 100 mils (1.2, 1.27, 1.8, 2.0, and 2.5 mm); verify availability with manufacturers if required.

2. Thickness:  [45 mils (1.1 mm), minimum] [60 mils (1.5 mm), nominal] <Insert thickness>.

Select color required from subparagraph below.  Although white is standard, verify availability of other colors with manufacturers if required.

3. Exposed Face Color:  [White] [Gray] <Insert color>.

Retain paragraph and subparagraphs below for Type IV group of compounded thermoplastic roofing membranes.  Often identified by primary plasticizer, compounded thermoplastics have been classified as PVCs by ASTM D 4434 and contain more than 50 percent PVC.  DuPont's "Elvaloy" (KEE or EIP) plasticizer is used by BondCote Corporation, Cooley Engineered Membranes, Ecology Roof Systems, Mule-Hide, and Seaman Corporation.  Copolymer alloy plasticizer is used by Duro-Last and ERSystems.  Except for Duro-Last, manufacturers listed below offer a fabric-backed sheet option.

C. PVC Sheet:  ASTM D 4434, Type IV, fabric reinforced[ and fabric backed].

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. BondCote Corporation.

b. Cooley Engineered Membranes; Div. of Cooley Group.

c. Duro-Last Roofing, Inc.

d. Ecology Roof Systems.

e. ERSystems.

f. Mule-Hide Products Co., Inc.

g. Seaman Corporation.

h. <Insert manufacturer's name.>

Select one thickness in subparagraph below or revise to suit Project.  ASTM D 4434, Type IV minimum thickness is 36 mils (0.9 mm).  Other thicknesses include 40, 48, 50, 72, 80, and 100 mils (1.0, 1.2, 1.27, 1.8, 2.0, and 2.5 mm); verify availability with manufacturers if required.

2. Thickness:  [36 mils (0.9 mm), minimum] [40 mils (1.0 mm), nominal] [60 mils (1.5 mm), nominal] <Insert thickness>.

Select color required from below.  Although white is standard, verify availability of other colors with manufacturers if required.

3. Exposed Face Color:  [White] [Gray] <Insert color>.

2.3 THERMOPLASTIC POLYOLEFIN ROOFING MEMBRANE

Retain this Article if fabric-reinforced thermoplastic polyolefin sheet is required.

A. Fabric-Reinforced Thermoplastic Polyolefin Sheet:  Uniform, flexible sheet formed from a thermoplastic polyolefin, internally fabric or scrim reinforced, and as follows:

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Carlisle SynTec Incorporated.

b. Firestone Building Products Company.

c. GAF Materials Corporation.

d. GenFlex Roofing Systems.

e. Johns Manville International, Inc.

f. Sarnafil Inc.

g. Stevens Roofing Systems; Div. of JPS Elastomerics.

h. Versico Inc.

i. <Insert manufacturer's name.>

Select thickness from options in subparagraph below.

2. Thickness:  [45 mils (1.1 mm)] [60 mils (1.5 mm)] <Insert thickness>, nominal.

Select color from options in subparagraph below.

3. Exposed Face Color:  [Black] [Gray] [White] <Insert color>.

Verify physical properties below with manufacturer's product data.

4. Physical Properties:

a. Breaking Strength:  225 lbf (1 kN); ASTM D 751, grab method.

b. Elongation at Break:  15 percent; ASTM D 751.

c. Tearing Strength:  55 lbf (245 N) minimum; ASTM D 751, Procedure B.

d. Brittleness Point:  Minus 22 deg F (30 deg C).

e. Ozone Resistance:  No cracks after sample, wrapped around a 3-inch- (75-mm-) diameter mandrel, is exposed for 166 hours to a temperature of 104 deg F (40 deg C) and an ozone level of 100 pphm (100 mPa); ASTM D 1149.

f. Resistance to Heat Aging:  90 percent minimum retention of breaking strength, elongation at break, and tearing strength after 166 hours at 240 deg F (116 deg C); ASTM D 573.

g. Water Absorption:  Less than 4 percent mass change after 166 hours' immersion at 158 deg F (70 deg C); ASTM D 471.

h. Linear Dimension Change:  Plus or minus 2 percent; ASTM D 1204.

Sarnafil limits use of glass-fiber-reinforced thermoplastic polyolefin below to loosely laid and ballasted installations, including loosely laid and ballasted, protected membrane roofing.

B. Glass-Fiber-Reinforced Thermoplastic Polyolefin Sheet:  Uniform, flexible sheet formed from a thermoplastic polyolefin, internally glass-fiber reinforced, and as follows:

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Sarnafil Inc.

b. <Insert manufacturer's name.>

Select thickness from options in subparagraph below.

2. Thickness:  [45 mils (1.1 mm)] [60 mils (1.5 mm)] <Insert thickness>, nominal.

Select color from options in subparagraph below.

3. Exposed Face Color:  [Black] [White] <Insert color>.

Verify physical properties below with manufacturer's product data.

4. Physical Properties:  As follows, as determined per ASTM test method indicated:

Verify test values in subparagraphs below with manufacturers whose published values usually exceed those below.

a. Tensile Strength:  1500 psi (10 MPa), machine direction; 1300 psi (9 MPa), cross-machine direction; ASTM D 412, Die C.

b. Ultimate Elongation:  500 percent; ASTM D 412, Die C.

c. Tensile Set:  15 percent, maximum; ASTM D 412, Die C, 50 percent elongation.

d. Tearing Strength:  340 lbf/in. (60 kN/m); ASTM D 624, Die C.

e. Brittleness Point:  Minus 22 deg F (30 deg C).

f. Ozone Resistance:  No cracks after sample, wrapped around a 3-inch- (75-mm-) diameter mandrel, is exposed for 166 hours to a temperature of 104 deg F (40 deg C) and an ozone level of 100 pphm (100 mPa); ASTM D 1149.

g. Resistance to Heat Aging:  90 percent minimum retention of tensile strength, ultimate elongation, and tear strength after 166 hours at 240 deg F (116 deg C); ASTM D 573.

h. Water Absorption:  Less than 4 percent mass change after 166 hours' immersion at 158 deg F (70 deg C); ASTM D 471.

i. Linear Dimension Change:  Plus or minus 2 percent; ASTM D 1204.

2.4 AUXILIARY MATERIALS

A. General:  Auxiliary materials recommended by roofing system manufacturer for intended use and compatible with membrane roofing.

1. Liquid-type auxiliary materials shall meet VOC limits of authorities having jurisdiction.

Retain subparagraph and associated subparagraphs below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

2. Adhesives and sealants that are used inside the weatherproofing system shall comply with the following limits for VOC content when calculated according to 40 CFR 59, Subpart D (EPA Method 24):

a. Plastic Foam Adhesives:  50 g/L.

b. Gypsum Board and Panel Adhesives:  50 g/L.

c. Multipurpose Construction Adhesives:  70 g/L.

d. Fiberglass Adhesives:  80 g/L.

e. Contact Adhesives:  80 g/L.

f. Plastic Cement Welding Compounds:  350 g/L.

g. PVC Welding Compounds:  510 g/L.

h. Other Adhesives:  250 g/L.

i. Single-Ply Roof Membrane Sealants:  450 g/L.

j. Nonmembrane Roof Sealants:  300 g/L.

k. Sealant Primers for Nonporous Substrates:  250 g/L.

l. Sealant Primers for Porous Substrates:  775 g/L.

Retain one of two paragraphs below depending on type of roofing membrane selected.

B. Sheet Flashing:  Manufacturer's standard sheet flashing of same material, type, reinforcement, thickness, and color as PVC sheet membrane.

C. Sheet Flashing:  Manufacturer's standard unreinforced thermoplastic polyolefin sheet flashing, [55 mils (1.4 mm)] <Insert thickness> thick, minimum, of same color as sheet membrane.

Select option in paragraph below for bonding adhesive.  Before specifying, verify that membrane roofing manufacturers offer a water-based adhesive for either PVC or thermoplastic polyolefin membrane.  Coordinate with selection of "Bonding Adhesive" Paragraph in Part 3 "Adhered Roofing Membrane Installation" Article.

D. Bonding Adhesive:  Manufacturer's standard [solvent] [water]-based bonding adhesive for membrane, and solvent-based bonding adhesive for base flashings.

Retain first paragraph below if slip sheets are required, usually for mechanically attached PVC membranes.  Slip sheets separate PVC roofing membranes from incompatible asphalt or coal-tar products and from contact with unfaced molded or extruded-polystyrene roof insulation.  Refer to roofing system manufacturer's specifications for requirements.

E. Slip Sheet:  Manufacturer's recommended slip sheet, of type required for application.

F. Metal Termination Bars:  Manufacturer's standard predrilled stainless-steel or aluminum bars, approximately 1 by 1/8 inch (25 by 3 mm) thick; with anchors.

G. Metal Battens:  Manufacturer's standard aluminum-zinc-alloy-coated or zinc-coated steel sheet, approximately 1 inch (25 mm) wide by 0.05 inch (1.3 mm) thick, prepunched.

H. Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening membrane to substrate, and acceptable to membrane roofing system manufacturer.

I. Miscellaneous Accessories:  Provide pourable sealers, preformed cone and vent sheet flashings, preformed inside and outside corner sheet flashings, T-joint covers, termination reglets, cover strips, and other accessories.

2.5 SUBSTRATE BOARDS

Select one of three substrate boards below if required or delete this Article.  Substrate boards may serve as model-building-code-required thermal barriers, separating foam insulation from steel or wood deck.  They may also be used over steel deck as part of a fire-resistance-rated roofing system or to provide a smooth substrate for a vapor retarder.

A. Substrate Board:  ASTM C 36, Type X gypsum wall board, 5/8 inch (16 mm) thick.

B. Substrate Board:  ASTM C 1177/C 1177M, glass-mat, water-resistant gypsum substrate, [1/4 inch (6 mm)] [1/2 inch (13 mm)] [Type X, 5/8 inch (16 mm)] thick.

Coordinate subparagraph below with Part 2 "Manufacturers" Article.

1. Product:  Subject to compliance with requirements, provide "Dens-Deck" by Georgia-Pacific Corporation.

C. Substrate Board:  ASTM C 728, perlite board, [3/4 inch (19 mm)] [1 inch (25 mm)] thick, seal coated.

Retain below with substrate board selected from paragraphs above.

D. Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening substrate panel to roof deck.

2.6 VAPOR RETARDER

Delete this Article if vapor retarders are not required.  Review compatibility of vapor retarder with other membrane roofing system materials.  A substrate board or layer of insulation will be needed because vapor retarders cannot be placed directly over a steel deck.  Retitle Article "Air Retarder" or "Vapor/Air Retarder" depending on function of retarder.

A. Polyethylene Vapor Retarder:  ASTM D 4397, 6 mils (0.15 mm) thick, minimum, with maximum permeance rating of 0.13 perm (7.5 ng/Pa x s x sq. m).

Retain one of two subparagraphs below with paragraph above.

1. Tape:  Pressure-sensitive tape of type recommended by vapor-retarder manufacturer for sealing joints and penetrations in vapor retarder.

2. Adhesive:  Manufacturer's standard lap adhesive, FMG approved for vapor-retarder application.

B. Laminated-Sheet Vapor Retarder:  Kraft paper, 2 layers, laminated with asphalt and edge reinforced with woven fiberglass yarn with maximum permeance rating of 0.50 perm (29 ng/Pa x s x sq. m)[ and manufacturer's standard adhesive].

C. Glass-Fiber Felts:  ASTM D 2178, Type IV, asphalt-impregnated, glass-fiber felt.

Delete vapor-retarder products above and add other products, such as self-adhering rubberized asphalt sheets, if required.

2.7 ROOF INSULATION

Delete from this Article insulation materials not required.  If retaining more than one insulation material, show location of each on Drawings or indicate where each layer is used in roofing system.  If allowing Contractor to select from more than one insulation material, limit options to insulations that will meet Project requirements and limitations.  Coordinate insulation selection and thicknesses indicated on Drawings with adjoining construction as well as HVAC design and energy program.

Roofing system manufacturers may require use of their own insulations or limit approvals to some insulation manufacturers.  Correlate lists of insulation manufacturers in subparagraphs below with insulation manufacturers approved by roofing system manufacturers, or delete lists altogether for total-system warranties.

A. General:  Provide preformed roof insulation boards that comply with requirements and referenced standards, selected from manufacturer's standard sizes and of thicknesses indicated.

B. Extruded-Polystyrene Board Insulation:  ASTM C 578, Type  [IV, 1.6-lb/cu. ft. (26-kg/cu. m)] [X, 1.3-lb/cu. ft. (21-kg/cu. m)] minimum density, square edged.

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. DiversiFoam Products.

b. Dow Chemical Company.

c. Owens Corning.

d. Tenneco Building Products.

e. <Insert manufacturer's name.>

Retain paragraph and subparagraphs below for extruded-polystyrene board insulation installed above the membrane of a protected membrane roofing system.  First option below corresponds to DiversiFoam's "Certifoam 40 Drainage Board," Dow's "Styrofoam Roofmate," Owens Corning's "Foamular 404," and Tenneco's "Amofoam-DC." Second option corresponds to DiversiFoam's "Certifoam Plaza Deck," Dow's "Styrofoam Plazamate," and Owens Corning's "Foamular 604." Usually retain Type VI; limit Type VII to roofs with heavy pedestrian traffic.

C. Extruded-Polystyrene Board Insulation:  ASTM C 578, [Type VI, 1.8 lb/cu. ft. (29 kg/cu. m)] [Type VII, 2.2 lb/cu. ft. (35 kg/cu. m)] with 2 or 4 edges rabbeted.

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. DiversiFoam Products.

b. Dow Chemical Company.

c. Owens Corning.

d. Tenneco Building Products.

e. <Insert manufacturer's name.>

Retain paragraph and subparagraph below for mortar-faced, extruded-polystyrene board insulation installed above the membrane of a protected membrane roofing system.  First option below describes "Lightguard" and second, "Heavyguard" from T. Clear Corporation.

D. Mortar-Faced, Extruded-Polystyrene Board Insulation:  ASTM C 578, Type VI, 1.8-lb/cu. ft. (29-kg/cu. m) minimum density, with tongue-and-groove edges on long dimension, and latex-modified cement mortar topping, [3/8 inch (9 mm) thick, 4 lb/sq. ft. (19.5 kg/sq. m)] [15/16 inch (23 mm) thick, 11 lb/sq. ft. (53.7 kg/sq. m)].

Coordinate subparagraph below with Part 2 "Manufacturers" Article.

1. Product:  Subject to compliance with requirements, provide "[Lightguard] [Heavyguard]" by T. Clear Corporation.

Retain paragraph and subparagraphs below for unfaced molded-polystyrene board insulation.  Select density of insulation from options in paragraph.  Higher-density insulation offers improved compressive resistance, better ability to span steel deck flutes, and more rigid substrate.  However, costs increase as density increases.

E. Molded-Polystyrene Board Insulation:  ASTM C 578 Type  [II, 1.35-lb/cu. ft. (22-kg/cu. m)] [VIII, 1.15-lb/cu. ft. (18-kg/cu. m)]   [IX, 1.8-lb/cu. ft. (29-kg/cu. m)] minimum density.

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Manufacturers with a third-party certification program satisfying model building code mandatory requirements for foam plastics[ and that produce FMG-approved molded polystyrene].

b. <Insert manufacturer's name.>

Retain paragraph and subparagraphs below for composite molded-polystyrene board insulation.

F. Composite Molded-Polystyrene Board Insulation:  ASTM C 578 Type  [II, 1.35-lb/cu. ft. (22-kg/cu. m)] [VIII, 1.15-lb/cu. ft. (18-kg/cu. m)]   [IX, 1.8-lb/cu. ft. (29-kg/cu. m)] minimum density, with factory-applied facings, as follows:

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Manufacturers with a third-party certification program satisfying model building code mandatory requirements for foam plastics[ and that produce FMG-approved molded polystyrene].

b. <Insert manufacturer's name.>

Select one of two "Facer" subparagraphs below, or revise to another board facer if required.  An example of the first product is "Perform Plus" by AFM Corp., and of the second, "R-Control SpecLam" by AFM Corp.  For adhered PVC roofing membrane, select non-asphaltic option in first subparagraph.  If a field-installed cover board is required, see "Insulation Accessories" Article for options.

2. Facer:  ASTM C 208, Type II, Grade 2, cellulosic-fiber insulation board, [non-asphaltic] [asphaltic] binders, 1/2 inch (13 mm) thick.

3. Facer:  DOC PS 2, Exposure 1, oriented strand board, 7/16 inch (11 mm) thick.

Retain paragraph and subparagraphs below for polyisocyanurate board insulation with aluminum foil facers or felt or glass-fiber mat facers.

G. Polyisocyanurate Board Insulation:  ASTM C 1289, Type  [I, Class 1 aluminum foil] [II, felt or glass-fiber mat] facer on both major surfaces.

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. AlliedSignal Inc.; Commercial Roofing Systems.

b. Apache Products Company.

c. Atlas Roofing Corporation.

d. Carlisle SynTec Incorporated.

e. Celotex Corporation.

f. Firestone Building Products Company.

g. GAF Materials Corporation.

h. GenFlex Roofing Systems.

i. Hunter Panels, LLC.

j. Johns Manville International, Inc.

k. Koppers Industries.

l. RMAX.

m. <Insert manufacturer's name.>

Retain paragraph and subparagraphs below for composite polyisocyanurate board insulation faced with insulation board on one side and felt or glass-fiber mat facer on the other.  Revise to include other facer types not yet recognized in ASTM C 1289 if applicable.

H. Composite Polyisocyanurate Board Insulation:  ASTM C 1289, faced with insulation board on one major surface, as indicated below by type, and felt or glass-fiber mat facer on the other.

Coordinate first subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Apache Products Company.

b. Atlas Roofing Corporation.

c. Celotex Corporation.

d. Firestone Building Products Company.

e. GAF Materials Corporation.

f. GenFlex Roofing Systems.

g. Hunter Panels, LLC.

h. Johns Manville International, Inc.

i. Koppers Industries.

j. RMAX.

k. <Insert manufacturer's name.>

2. Type III (perlite-insulation-board facer), [1/2 inch (13 mm)] [3/4 inch (19 mm)] thick.

For adhered PVC roofing membrane, select non-asphaltic option in subparagraph below.

3. Type IV (cellulosic-fiber-insulation-board facer), [non-asphaltic] [asphaltic] binder, Grade 2, 1/2 inch (13 mm) thick.

Delete subparagraph below if noncombustible roof construction is required.

4. Type V (oriented-strand-board facer), 7/16 inch (11 mm) thick.

Retain paragraph and subparagraphs below for perlite board insulation.

I. Perlite Board Insulation:  ASTM C 728; composed of expanded perlite, cellulosic fibers, binders, and waterproofing agents with top surface seal-coated.

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. AlliedSignal Inc.; Commercial Roofing Systems.

b. Celotex Corporation.

c. GAF Materials Corporation.

d. Johns Manville International, Inc.

e. Koppers Industries.

f. <Insert manufacturer's name.>

Retain paragraph and subparagraphs below for cellulosic-fiber board insulation.  For adhered PVC roofing membrane, select non-asphaltic option below.

J. Cellulosic-Fiber Board Insulation:  ASTM C 208, Type II, Grade 2, fibrous-felted wood fiber or other cellulosic-fiber and water-resistant [non-asphaltic] [asphaltic] binders, chemically treated for deterioration.

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. AlliedSignal Inc.; Commercial Roofing Systems.

b. Carlisle SynTec Incorporated.

c. Celotex Corporation.

d. Firestone Building Products Company.

e. GAF Materials Corporation.

f. Georgia-Pacific Corporation.

g. Homasote Company (The).

h. Huebert Fiberboard Co.

i. Koppers Industries.

j. Masonite Corp.

k. Temple - Inland Inc.

l. <Insert manufacturer's name.>

Cellular-glass board insulation is rarely used in single-ply roofing.  Board dimensions are 24 by 48 inches (600 by 1219 mm).

K. Cellular-Glass Board Insulation:  ASTM C 552, Type IV, faced on both sides with manufacturer's standard kraft-paper sheets.

Coordinate subparagraph below with Part 2 "Manufacturers" Article.

1. Product:  Subject to compliance with requirements, provide "Foamglas" by Pittsburgh Corning Corporation.

Retain paragraph below if tapered insulation is required.  Most of the commonly used insulations are available in tapered form; verify with manufacturers.  With some exceptions, codes require roof slopes to be no less than 1/4 inch per 12 inches (1:48).  Insulation is manufactured with tapers ranging from 1/8 inch per 12 inches (1:96) to 1/2 inch per 12 inches (1:24).

L. Tapered Insulation:  Provide factory-tapered insulation boards fabricated to slope of [1/4 inch per 12 inches (1:48)] <Insert slope>, unless otherwise indicated.

Retain below with or without tapered insulation above; delete if not required.

M. Provide preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for sloping to drain.  Fabricate to slopes indicated.

2.8 INSULATION ACCESSORIES

A. General:  Roof insulation accessories recommended by insulation manufacturer for intended use and compatible with membrane roofing.

Retain first paragraph below if insulation requires mechanical fastening.

B. Fasteners:  Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FMG 4470, designed for fastening roof insulation to substrate, and acceptable to roofing system manufacturer.

C. Cold Fluid-Applied Adhesive:  Manufacturer's standard cold fluid-applied adhesive formulated to adhere roof insulation to substrate.

Select one of three cover boards below if required.  Cover or overlay boards are usually needed over noncomposite foam insulation or over existing roofing before installing new roofing.

D. Cover Board:  ASTM C 208, Type II, Grade 2, cellulosic-fiber insulation board, 1/2 inch (13 mm) thick.

E. Cover Board:  DOC PS 2, Exposure 1, oriented strand board, 7/16 inch (11 mm) thick.

F. Cover Board:  ASTM C 1177/C 1177M, glass-mat, water-resistant gypsum substrate, [1/4 inch (6 mm)] [1/2 inch (13 mm)] thick.

Coordinate subparagraph below with Part 2 "Manufacturers" Article.

1. Product:  Subject to compliance with requirements, provide "Dens-Deck" by Georgia-Pacific Corporation.

Protection mats below may be placed on roofing membrane as a paver or crushed-aggregate ballast underlayment.  Sometimes called "filter fabrics" or "fabric mats," they also limit aggregate ballast movement and control insulation flotation in protected membrane systems.

G. Protection Mat:  Woven or nonwoven polypropylene, polyolefin, or polyester fabric mat, water permeable and resistant to ultraviolet degradation, type and weight as recommended by roofing system manufacturer for application.

Retain below if T. Clear's proprietary metal securement system is required for mortar-faced board insulation.  If preferred, specify gravel stop or counterflashing in Division 07 Section "Sheet Metal Flashing and Trim" or "Roof Specialties," as applicable.

H. Metal Securement System:  Perimeter securement flashing and strapping fabricated from stainless steel, a minimum of 0.031 inch (0.8 mm) thick.  Provide fasteners as recommended by mortar-faced insulation manufacturer.

2.9 ASPHALT MATERIALS

Retain this Article if adhering fabric-backed PVC roofing membrane, insulation, or vapor retarder with asphalt materials.

A. Roofing Asphalt:  [ASTM D 312, Type III or IV] [ASTM D 6152, SEBS modified].

Retain below if priming concrete roof deck.

B. Asphalt Primer:  ASTM D 41.

2.10 AGGREGATE BALLAST

Retain this Article for loosely laid and aggregate-ballasted installations.  Add requirements for color if necessary.

A. Aggregate Ballast:  Provide aggregate ballast that will withstand weather exposure without significant deterioration and will not contribute to membrane degradation, of the following type and size:

Select aggregate type from options in subparagraph below.  If smooth-faced aggregate is preferred, verify availability and cost.  A roofing membrane in contact with sharper crushed aggregate needs added protection to prevent puncturing.

1. Aggregate Type:  [Smooth, washed, riverbed gravel or other acceptable smooth-faced stone] [Crushed gravel or crushed stone].

Retain one or more "Size" subparagraphs below to suit Project.

2. Size:  ASTM D 448, Size 4, ranging from 3/4 to 1-1/2 inches (19 to 38 mm).

3. Size:  ASTM D 448, Size 2, ranging from 1-1/2 to 2-1/2 inches (38 to 63 mm).

Ballast size below is based on recommendations in FMG Loss Prevention Data Sheet 1-29.

4. Size:  ASTM D 448, Size 3, ranging from 1 to 2 inches (25 to 50 mm).

2.11 ROOF PAVERS

Retain this Article if roof-paver ballast is required.  Pavers may be used alone or with aggregate ballast for functional or decorative reasons.

Retain interlocking, lightweight roof pavers in paragraph and subparagraphs below if required.

A. Lightweight Roof Pavers:  Interlocking, lightweight concrete units, specially factory cast for use as roof ballast; grooved back, with four-way drainage capability; beveled, doweled, or otherwise profiled; and as follows:

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Hanover Architectural Products.

b. Rapid Building Systems.

c. Roofblok, Ltd.

d. Westile Roofing Products.

e. <Insert manufacturer's name.>

Coordinate size selection below with minimum paver coverage required, especially at corners, perimeter, penetrations, and above large wall openings.  Paver sizes vary with manufacturer and include 8 by 16, 12 by 12, 12 by 16-1/2, and 12 by 18 inches (200 by 400, 300 by 300, 300 by 420, and 300 by 450 mm).

2. Size:  <Insert actual size(s) of pavers.>

Insert weight of roof paver in subparagraph below.  SPRI identifies interlocking, lightweight roof pavers as weighing at least 10 lb/sq. ft. (50 kg/sq. m) but not exceeding 18 lb/sq. ft. (90 kg/sq. m).  Verify availability with manufacturers selected.

3. Weight:  <Insert weight or acceptable weight range.>

Select compressive strength from options in subparagraph below.

4. Compressive Strength:  [2500 psi (17 MPa)] [5000 psi (34 MPa)] <Insert strength>, minimum.

Retain one option in subparagraph below.  If retaining first, indicate colors and textures in a separate schedule.

5. Colors and Textures:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

Retain heavyweight roof pavers in paragraph and subparagraphs below if required.

B. Heavyweight Roof Pavers:  Heavyweight, hydraulically pressed, concrete units, [square edged] [with top edges beveled 3/16 inch (5 mm)], factory cast for use as roof pavers; absorption not greater than 5 percent, ASTM C 140; no breakage and maximum 1 percent mass loss when tested for freeze-thaw resistance, ASTM C 67; and as follows:

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Hanover Architectural Products.

b. Rapid Building Systems.

c. Roofblok, Ltd.

d. Sunny Brook Pressed Concrete Co.

e. Wausau Tile, Inc.; Terra-Paving Div.

f. Westile Roofing Products.

g. <Insert manufacturer's name.>

Coordinate size selection below with minimum paver coverage required, especially at corners, perimeter, penetrations, and above large wall openings.  Consider handling of pavers as weight increases.  Other sizes include 12 by 12 and 18 by 18 inches (300 by 300 and 450 by 450 mm).

2. Size:  [24 by 24 inches (600 by 600 mm)] <Insert size>.  Manufacture pavers to dimensional tolerances of plus or minus 1/16 inch (1.6 mm) in length, height, and thickness.

Select weight of roof paver from options in subparagraph below.  ANSI/SPRI RP-4, System 1, all locations, and System 2, field of roof, allow roof pavers weighing 18 lb/sq. ft. (90 kg/sq. m) or more.  System 3 requires roof pavers weighing 22 lb/sq. ft. (110 kg/sq. m) or more.  Verify availability with manufacturers selected.

3. Weight:  [18 lb/sq. ft. (90 kg/sq. m)] [22 lb/sq. ft. (110 kg/sq. m)] <Insert weight>.

Select compressive strength from options in subparagraph below.

4. Compressive Strength:  [7500 psi (52 MPa)] [6500 psi (45 MPa)] <Insert strength>, minimum.

Retain one option in subparagraph below.  If retaining first, indicate colors and textures in a separate schedule.

5. Colors and Textures:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

Delete paver supports, which are used to elevate pavers and facilitate drainage, in subparagraphs below if not required.  Retain first subparagraph if paver supports are integrally cast.  Retain second subparagraph if separate pedestal supports, which are used to space, level, and stabilize pavers, are required.  Pedestals may be of fixed height or adjustable for leveling pavers over a sloped substrate.  Besides roof-paver producers, pedestal manufacturers include Envirospec and Tremco.

6. Paver Supports:  Integral corner pedestals.

7. Paver Supports:  Paver manufacturer's standard SBR rubber, high-density polyethylene, or polyurethane paver support assembly, including [fixed-height] [adjustable or stackable] pedestals, shims, and spacer tabs for joint spacing of [1/8 inch (3 mm)] [3/16 inch (5 mm)] [1/8 to 3/16 inch (3 to 5 mm)].

2.12 WALKWAYS

Retain one of two paragraphs and associated subparagraphs below for preformed roof walkway products.  Revise to suit other walkway products if required.

A. Flexible Walkways:  Factory-formed, nonporous, heavy-duty, solid-rubber, slip-resisting, surface-textured walkway [pads] [rolls] [pads or rolls], approximately 3/16 inch (5 mm) thick, and acceptable to membrane roofing system manufacturer.

Retain proprietary interlocking, rubber lightweight roof walkway pavers in paragraph and subparagraphs below if required for thermoplastic polyolefin membrane roofing.

B. Rubber Roof Pavers:  Interlocking, lightweight rubber units, 24 by 24 by 2-1/4 inches (600 by 600 by 57 mm), 6 lb/sq. ft. (30 kg/sq. m); with grooved back for 4-way drainage, beveled and doweled; and as follows:

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article if multiple products are specified.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Products:

a. Carlisle SynTec Incorporated; Interlocking Rubber Paver.

b. <Insert manufacturer's name; product.>

Retain one color from options in subparagraph below

2. Color:  [Black] [Gray] [Terra cotta] <Insert color>.

Retain heavyweight roof pavers as walkways in paragraph and subparagraphs below if required.

C. Walkway Roof Pavers:  Heavyweight, hydraulically pressed, concrete units, [square edged] [with top edges beveled 3/16 inch (5 mm)], factory cast for use as roof pavers; absorption not greater than 5 percent, ASTM C 140; no breakage and maximum 1 percent mass loss when tested for freeze-thaw resistance, ASTM C 67; and as follows:

Coordinate subparagraph and associated subparagraphs below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Hanover Architectural Products.

b. Rapid Building Systems.

c. Roofblok, Ltd.

d. Sunny Brook Pressed Concrete Co.

e. Wausau Tile, Inc.; Terra-Paving Div.

f. Westile Roofing Products.

g. <Insert manufacturer's name.>

Coordinate size selection below with minimum paver coverage required, especially at corners, perimeter, penetrations, and above large wall openings.  Consider handling of pavers as weight increases.  Other sizes include 12 by 12 and 18 by 18 inches (300 by 300 and 450 by 450 mm).

2. Size:  [24 by 24 inches (600 by 600 mm)] <Insert size>.  Manufacture pavers to dimensional tolerances of plus or minus 1/16 inch (1.6 mm) in length, height, and thickness.

Select weight of walkway roof paver from options in subparagraph below.  Verify availability with manufacturers selected.

3. Weight:  [18 lb/sq. ft. (90 kg/sq. m)] [22 lb/sq. ft. (110 kg/sq. m)] <Insert weight>.

Select compressive strength from options in subparagraph below.

4. Compressive Strength:  [7500 psi (52 MPa)] [6500 psi (45 MPa)] <Insert strength>, minimum.

Retain one option below.  If retaining first, indicate colors and textures in a separate schedule.

5. Colors and Textures:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with the following requirements and other conditions affecting performance of roofing system:

1. Verify that roof openings and penetrations are in place and set and braced and that roof drains are securely clamped in place.

2. Verify that wood blocking, curbs, and nailers are securely anchored to roof deck at penetrations and terminations and that nailers match thicknesses of insulation.

Retain subparagraph below for steel roof deck.

3. Verify that surface plane flatness and fastening of steel roof deck comply with requirements in Division 05 Section "Steel Decking."

Retain or revise first three subparagraphs below for concrete roof decks.

4. Verify that minimum concrete drying period recommended by roofing system manufacturer has passed.

5. Verify that concrete substrate is visibly dry and free of moisture.  Test for capillary moisture by plastic sheet method according to ASTM D 4263.

6. Verify that concrete curing compounds that will impair adhesion of roofing components to roof deck have been removed.

7. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Clean substrate of dust, debris, moisture, and other substances detrimental to roofing installation according to roofing system manufacturer's written instructions.  Remove sharp projections.

B. Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.  Remove roof-drain plugs when no work is taking place or when rain is forecast.

C. Complete terminations and base flashings and provide temporary seals to prevent water from entering completed sections of roofing system at the end of the workday or when rain is forecast.  Remove and discard temporary seals before beginning work on adjoining roofing.

Retain below if acoustical roof deck rib insulation, shaped to fit into topside ribs of acoustical roof deck, is installed in this Section.

D. Install acoustical roof deck rib insulation strips, specified in Division 05 Section "Steel Decking," according to acoustical roof deck manufacturer's written instructions.

3.3 SUBSTRATE BOARD INSTALLATION

Delete this Article if not required.

A. Install substrate board with long joints in continuous straight lines, perpendicular to roof slopes with end joints staggered between rows.  Tightly butt substrate boards together.

Retain one of two subparagraphs below if mechanical fastening is required.

1. Fasten substrate board to top flanges of steel deck according to recommendations in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

2. Fasten substrate board to top flanges of steel deck to resist uplift pressure at corners, perimeter, and field of roof according to membrane roofing system manufacturer's written instructions.

3.4 VAPOR-RETARDER INSTALLATION

Delete this Article if not required.  Retain selected vapor-retarder material from paragraphs below.  Retitle Article "Air Barrier" if that is primary function and revise installation requirements if necessary.  Vapor retarder must be fully supported by substrate.  Steel deck requires substrate board.

A. Loosely lay polyethylene-sheet vapor retarder in a single layer over area to receive vapor retarder, side and end lapping each sheet a minimum of 2 inches (50 mm) and 6 inches (150 mm), respectively.

Select one of two options in subparagraph below.

1. Seal side and end laps with [tape] [adhesive].

B. Install laminated-sheet vapor retarder in a single layer over area to receive vapor retarder, side and end lapping each sheet a minimum of 2 inches (50 mm) and 6 inches (150 mm), respectively.  Bond vapor retarder to deck as follows:

Select one of two subparagraphs below.

1. Apply adhesive at rate recommended by vapor-retarder manufacturer.  Seal laps with adhesive.

2. Apply ribbons of hot roofing asphalt at spacing, temperature, and rate recommended by vapor-retarder manufacturer.  Seal laps with hot roofing asphalt.

C. Install 2 glass-fiber felt plies lapping each sheet 19 inches (483 mm) over preceding sheet.  Embed each sheet in a solid mopping of hot roofing asphalt.  Glaze-coat completed surface with hot roofing asphalt.  Apply hot roofing asphalt at a rate of 20 lb/100 sq. ft. (1 kg/sq. m), plus or minus 25 percent.

Always retain below.  To function effectively, vapor retarders or air barriers must prevent air movement into membrane roofing system.

D. Completely seal vapor retarder at terminations, obstructions, and penetrations to prevent air movement into membrane roofing system.

3.5 INSULATION INSTALLATION

A. Coordinate installing membrane roofing system components so insulation is not exposed to precipitation or left exposed at the end of the workday.

B. Comply with membrane roofing system manufacturer's written instructions for installing roof insulation.

Retain paragraph below if tapered insulation is required.

C. Install tapered insulation under area of roofing to conform to slopes indicated.

Revise thickness in first paragraph below to suit Project.  NRCA recommendations for maximum thickness of a single layer vary with insulation material; 1-1/2 inches (38 mm) for perlite and glass fiber, 2 inches (50 mm) for polyisocyanurate and molded and extruded polystyrene, and 3 inches (75 mm) for cellular glass.

D. Install one or more layers of insulation under area of roofing to achieve required thickness.  Where overall insulation thickness is [1-1/2 inches (38 mm)] [2 inches (50 mm)] or greater, install 2 or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches (150 mm) in each direction.

E. Trim surface of insulation where necessary at roof drains so completed surface is flush and does not restrict flow of water.

F. Install insulation with long joints of insulation in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch (6 mm) with insulation.

1. Cut and fit insulation within 1/4 inch (6 mm) of nailers, projections, and penetrations.

Retain paragraph below for loosely laid and ballasted roofing membranes.

G. Loosely Laid Insulation:  Loosely lay insulation units.

Retain paragraph below if adhering each layer of insulation.

H. Adhered Insulation:  Install each layer of insulation and adhere to substrate as follows:

Retain applicable subparagraphs below.

1. Prime surface of concrete deck with asphalt primer at a rate of 3/4 gal./100 sq. ft. (0.3 L/sq. m) and allow primer to dry.

2. Set each layer of insulation in a solid mopping of hot roofing asphalt, applied within plus or minus 25 deg F (14 deg C) of equiviscous temperature.

3. Set each layer of insulation in a cold fluid-applied adhesive.

Retain paragraph below if mechanically fastening each insulation layer.

I. Mechanically Fastened Insulation:  Install each layer of insulation and secure to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof insulation to deck type.

Retain first subparagraph below when Project is FMG insured or FMG requirements are proposed as a performance standard.  Retain second subparagraph if number of fasteners will be based on ASCE 7's uplift pressure or SPRI's factored design uplift pressure.  Coordinate with Part 1 "Performance Requirements" Article.  Fastener numbers will increase at corners and perimeter over number required for field of roof.

1. Fasten insulation according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

2. Fasten insulation to resist uplift pressure at corners, perimeter, and field of roof.

Retain paragraph below if mechanically fastening the first layer of insulation and adhering the remaining layers.  This is the most common application method.

J. Mechanically Fastened and Adhered Insulation:  Install each layer of insulation and secure first layer of insulation to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof insulation to deck type.

Retain first subparagraph below when Project is FMG insured or FMG requirements are proposed as a performance standard.  Retain second subparagraph if fastening is calculated from ASCE 7's uplift pressure or SPRI's factored design uplift pressure.  Coordinate with Part 1 "Performance Requirements" Article.  Fastener numbers will increase at corners and perimeter over number required for field of roof.

1. Fasten first layer of insulation according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

2. Fasten first layer of insulation to resist uplift pressure at corners, perimeter, and field of roof.

Select one of two subparagraphs below.

3. Install subsequent layers of insulation in a solid mopping of hot roofing asphalt, applied within plus or minus 25 deg F (14 deg C) of equiviscous temperature.

4. Install subsequent layers of insulation in a cold fluid-applied adhesive.

Retain below if cover boards will be field installed over roof insulation and immediately below roofing membrane.

K. Install cover boards over insulation with long joints in continuous straight lines with end joints staggered between rows.  Stagger joints from joints in insulation below a minimum of 6 inches (150 mm) in each direction.  Loosely butt cover boards together and fasten to roof deck.

1. Fasten according to requirements in FMG's "Approval Guide" for specified Windstorm Resistance Classification.

2. Fasten to resist uplift pressure at corners, perimeter, and field of roof.

3.6 ADHERED ROOFING MEMBRANE INSTALLATION

Retain this Article for adhered roofing membrane installations.

A. Install roofing membrane over area to receive roofing according to membrane roofing system manufacturer's written instructions.  Unroll roofing membrane and allow to relax before installing.

For PVC roofing membranes, retain subparagraph below with paragraph above.  Delete below for thermoplastic polyolefins.

1. Install sheet according to ASTM D 5036.

Delete first paragraph below if not applicable.

B. Start installation of roofing membrane in presence of membrane roofing system manufacturer's technical personnel.

C. Accurately align roofing membrane and maintain uniform side and end laps of minimum dimensions required by manufacturer.  Stagger end laps.

Retain one of two paragraphs below for adhering membrane to substrate.  Retain first paragraph for solvent-based bonding adhesive, second for water-based bonding adhesive.

D. Bonding Adhesive:  Apply solvent-based bonding adhesive to substrate and underside of roofing membrane at rate required by manufacturer and allow to partially dry before installing roofing membrane.  Do not apply bonding adhesive to splice area of roofing membrane.

E. Bonding Adhesive:  Apply water-based bonding adhesive to substrate at rate required by manufacturer and immediately install roofing membrane.  Do not apply bonding adhesive to splice area of roofing membrane.

Retain first paragraph below for bonding fabric-backed PVC roofing membrane with hot roofing asphalt.

F. Hot Roofing Asphalt:  Apply a solid mopping of hot roofing asphalt to substrate at temperature and rate required by manufacturer and install fabric-backed roofing membrane.  Do not apply roofing asphalt to splice area of roofing membrane.

G. Mechanically or adhesively fasten roofing membrane securely at terminations, penetrations, and perimeter of roofing.

H. Apply roofing membrane with side laps shingled with slope of roof deck where possible.

I. Seams:  Clean seam areas, overlap roofing membrane, and hot-air weld side and end laps of roofing membrane according to manufacturer's written instructions to ensure a watertight seam installation.

1. Test lap edges with probe to verify seam weld continuity.  Apply lap sealant to seal cut edges of roofing membrane.

Revise number of seam tests in first subparagraph below to suit Project.

2. Verify field strength of seams a minimum of twice daily and repair seam sample areas.

3. Repair tears, voids, and lapped seams in roofing membrane that does not meet requirements.

J. Spread sealant or mastic bed over deck drain flange at deck drains and securely seal roofing membrane in place with clamping ring.

Retain below if tie-ins to existing roofing are required.

K. Install roofing membrane and auxiliary materials to tie in to existing roofing.

3.7 MECHANICALLY FASTENED ROOFING MEMBRANE INSTALLATION

Retain this Article for mechanically fastened roofing membrane installations.

A. Install roofing membrane over area to receive roofing according to roofing system manufacturer's written instructions.  Unroll roofing membrane and allow to relax before installing.

For PVC roofing membranes, retain subparagraph below with paragraph above.  Delete below for thermoplastic polyolefins.

1. Install sheet according to ASTM D 5082.

Delete first paragraph below if not applicable.

B. Start installation of roofing membrane in presence of roofing system manufacturer's technical personnel.

C. Accurately align roofing membranes and maintain uniform side and end laps of minimum dimensions required by manufacturer.  Stagger end laps.

D. Mechanically or adhesively fasten roofing membrane securely at terminations, penetrations, and perimeter of roofing.

E. Apply roofing membrane with side laps shingled with slope of roof deck where possible.

F. Seams:  Clean seam areas, overlap roofing membrane, and hot-air weld side and end laps of roofing membrane according to manufacturer's written instructions to ensure a watertight seam installation.

1. Test lap edges with probe to verify seam weld continuity.  Apply lap sealant to seal cut edges of roofing membrane.

Revise number of seam tests in first subparagraph below to suit Project.

2. Verify field strength of seams a minimum of twice daily and repair seam sample areas.

3. Repair tears, voids, and lapped seams in roofing membrane that does not meet requirements.

G. Spread sealant or mastic bed over deck drain flange at deck drains and securely seal roofing membrane in place with clamping ring.

Select one of two methods of mechanical fastening described in two paragraphs below.  Classification of attachment methods follows SPRI guidelines.  First paragraph conceals fasteners within seams of roofing membranes.  Second paragraph fastens roofing membrane independent of seam locations and requires a cover strip to conceal fasteners.  Revise to describe the seldom used "under membrane attachment" method or another method if applicable.

H. In-Splice Attachment:  Secure one edge of roofing membrane using fastening plates or metal battens centered within membrane splice and mechanically fasten roofing membrane to roof deck.  Field-splice seam.

I. Through-Membrane Attachment:  Secure roofing membrane using fastening plates or metal battens and mechanically fasten roofing membrane to roof deck.  Cover battens and fasteners with a continuous cover strip.

Retain below if tie-ins to existing roofing are required.

J. Install roofing membrane and auxiliary materials to tie in to existing roofing.

3.8 LOOSELY LAID AND BALLASTED ROOFING MEMBRANE INSTALLATION

Retain this Article for loosely laid and ballasted roofing membrane installations.

A. Install roofing membrane over area to receive roofing according to roofing system manufacturer's written instructions.  Unroll roofing membrane and allow to relax before installing.

Delete first paragraph below if not applicable.

B. Start installation of roofing membrane in presence of roofing system manufacturer's technical personnel.

C. Accurately align roofing membranes, without stretching, and maintain uniform side and end laps of minimum dimensions required by manufacturer.  Stagger end laps.

Retain one of two options in first paragraph below.  Perimeter attachment of loosely laid and ballasted roofing membrane is required.  First option includes general perimeter attachment requirements in ANSI/SPRI RP-4 that satisfy Systems 1 and 2.  Second option sets more stringent requirements for System 3.

D. [Mechanically fasten or adhere perimeter of roofing membrane] [Adhere roofing membrane at corners, perimeters, and transitions] according to requirements in ANSI/SPRI RP-4.

E. Apply roofing membrane with side laps shingled with slope of deck where possible.

F. Seams:  Clean seam areas, overlap roofing membrane, and hot-air weld side and end laps of roofing membrane according to manufacturer's written instructions to ensure a watertight seam installation.

1. Test lap edges with probe to verify seam weld continuity.  Apply lap sealant to seal cut edges of roofing membrane.

Revise number of seam tests in first subparagraph below to suit Project.

2. Verify field strength of seams a minimum of twice daily and repair seam sample areas.

3. Repair tears, voids, and lapped seams in roofing membrane that does not meet requirements.

G. Spread sealant or mastic bed over deck drain flange at deck drains and securely seal roofing membrane in place with clamping ring.

Retain paragraph below if tie-ins to existing roofing are required.

H. Install roofing membrane and auxiliary materials to tie in to existing roofing.

Retain paragraph below under pavers or if crushed stone or a more angular ballast must be used.  Consult roofing manufacturers for recommendations because one or more layers of protection mat may be required.  Revise below to suit Project.

I. Install protection mat over roofing membrane, overlapping a minimum of 6 inches (150 mm).  Install an additional protection mat layer at projections, pipes, vents, and drains, overlapping a minimum of 12 inches (300 mm).

Retain paragraph and subparagraphs below if using aggregate ballast.

J. Aggregate Ballast:  Apply aggregate ballast uniformly over roofing membrane at rate required by membrane roofing system manufacturer, but not less than the following, spreading with care to minimize possibility of damage to membrane roofing system.  Lay ballast as roofing membrane is installed, leaving roofing membrane ballasted at the end of the workday.

Two subparagraphs below are based on ANSI/SPRI RP-4.  First corresponds to System 1, second to System 2.  More ballast may be required to fully conceal membrane.  Delineate dimensions of corners, perimeter, and field of roof on Drawings.

1. Ballast Weight:  Size 4 aggregate, 10 lb/sq. ft. (50 kg/sq. m).

2. Ballast Weight:  Size 2 aggregate, 13 lb/sq. ft. (65 kg/sq. m), at corners and perimeter; Size 4 aggregate, 10 lb/sq. ft. (50 kg/sq. m), elsewhere.

Delete both subparagraphs above and retain subparagraph below if FMG recommendations apply.  Insert weight of aggregate for each part of roof, based on recommendations in FMG Loss Prevention Data Sheet 1-29.  Delineate dimensions of corners, perimeter, and field of roof on Drawings, based on FMG requirements.

3. Ballast Weight:  Size 3 aggregate, <Insert weight>, at corners, <Insert weight> at perimeter, and <Insert weight>, elsewhere.

Retain one of two paragraphs below if roof-paver ballast is required.  Retain first for lightweight roof pavers.  Retain second if combining roof-paver and aggregate ballast based on ANSI/SPRI RP-4, System 3.

K. Roof-Paver Ballast:  Install lightweight roof-paver ballast according to manufacturer's written instructions.

L. Roof-Paver and Aggregate Ballast:  Install heavyweight roof pavers according to manufacturer's written instructions on roof corners and perimeter.  Install Size 2 aggregate ballast elsewhere on roofing at a minimum rate of 13 lb/sq. ft. (65 kg/sq. m).

3.9 LOOSELY LAID AND BALLASTED, PROTECTED MEMBRANE ROOFING INSTALLATION

Retain this Article for loosely laid and ballasted, protected membrane roofing installations.

A. Install roofing membrane over area to receive roofing according to roofing system manufacturer's written instructions.  Unroll roofing membrane and allow to relax for a minimum of 30 minutes.

Delete first paragraph below if not applicable.

B. Start installation of roofing membrane in presence of roofing system manufacturer's technical personnel.

C. Accurately align roofing membranes, without stretching, and maintain uniform side and end laps of minimum dimensions required.  Stagger end laps.

Retain one of two options in first paragraph below.  Perimeter attachment of loosely laid and ballasted roofing membrane is required.  First option includes general perimeter attachment requirements in ANSI/SPRI RP-4 that satisfy Systems 1 and 2.  Second option sets more stringent requirements for System 3.

D. [Mechanically fasten or adhere perimeter of roofing membrane] [Adhere roofing membrane at corners, perimeters, and transitions] according to requirements in ANSI/SPRI RP-4.

E. Apply roofing membrane with side laps shingled with slope of deck where possible.

F. Seams:  Clean seam areas, overlap roofing membrane, and hot-air weld side and end laps of roofing membrane according to manufacturer's written instructions to ensure a watertight seam installation.

1. Test lap edges with probe to verify seam weld continuity.  Apply lap sealant to seal cut edges of roofing membrane.

Revise number of seam tests in first subparagraph below to suit Project.

2. Verify field strength of seams a minimum of twice daily and repair seam sample areas.

3. Repair tears, voids, and lapped seams in roofing membrane that does not meet requirements.

G. Spread sealant or mastic bed over deck drain flange at deck drains and securely seal roofing membrane in place with clamping ring.

Retain paragraph below if tie-ins to existing roofing are required.

H. Install roofing membrane and auxiliary materials to tie in to existing roofing.

Retain paragraph and subparagraphs below for extruded-polystyrene insulation loosely laid over membrane.

I. Insulation:  Loosely lay board insulation units over roofing membrane, with long joints of insulation in continuous straight line and with end joints staggered between rows.  Abut edges and ends between units.  Install to achieve required insulation thickness over roofing membrane.  Cut and fit to within 3/4 inch (19 mm) of projections and penetrations.

Delete subparagraph below if not required or revise to suit Project.  Revise if one or more insulation layers are topped with a final layer of mortar-faced board insulation.

1. Where overall insulation thickness is 2 inches (50 mm) or more, install required thickness in 2 or more layers with joints of each succeeding layer staggered over joints of previous layer a minimum of 6 inches (150 mm) in each direction.

Retain subparagraph below for aggregate ballast.  Protection mat is usually omitted under roof-paver ballast.

2. Install protection mat over insulation, overlapping edges and ends at least 12 inches (300 mm).  Do not lap ends of fabric sheets within 72 inches (1800 mm) of roof perimeter.  Extend fabric 2 to 3 inches (50 to 75 mm) above ballast at perimeter and penetrations.  Apply additional protection mat layer around penetrations to prevent aggregate from getting between penetrations and insulation.  Do not cover drains or restrict water flow to drains.

Retain paragraph and subparagraphs below if using aggregate ballast over protection mat and insulation.

J. Aggregate Ballast:  Apply aggregate ballast uniformly over protection mat at roofing system manufacturer's recommended rate, but not less than the following, spreading with care to minimize possibility of damage to membrane.  Lay ballast as membrane and insulation are installed, leaving roofing membrane insulated and ballasted at the end of the workday.

Two subparagraphs below are based on ANSI/SPRI RP-4.  First corresponds to System 1, second to System 2.  More ballast may be required to fully conceal membrane.  Delineate dimensions of corners, perimeter, and field of roof on Drawings.

1. Ballast Weight:  Size 4 aggregate, 10 lb/sq. ft. (50 kg/sq. m).

2. Ballast Weight:  Size 2 aggregate, 13 lb/sq. ft. (65 kg/sq. m), at corners and perimeter; Size 4 aggregate, 10 lb/sq. ft. (50 kg/sq. m), elsewhere.

Delete both subparagraphs above and retain subparagraph below if FMG recommendations apply.  Insert weight of aggregate for each part of roof, based on recommendations in FMG Loss Prevention Data Sheet 1-29.  Delineate dimensions of corners, perimeter, and field of roof on Drawings, based on FMG requirements.

3. Ballast Weight:  Size 3 aggregate, <Insert weight>, at corners, <Insert weight> at perimeter, and <Insert weight>, elsewhere.

Retain one of two paragraphs below if roof-paver ballast is required.  Retain first for lightweight roof pavers.  Retain second if combining roof-paver and aggregate ballast based on ANSI/SPRI RP-4, System 3.

K. Roof-Paver Ballast:  Install lightweight roof-paver ballast according to manufacturer's written instructions

L. Roof-Paver and Aggregate Ballast:  Install heavyweight roof pavers according to manufacturer's written instructions, on roof corners and perimeter as defined by ANSI/SPRI RP-4.  Install Size 2 aggregate ballast elsewhere on roofing at a minimum rate of 13 lb/sq. ft. (65 kg/sq. m).

Retain subparagraph below if using separate pedestal assemblies beneath heavyweight roof pavers.

1. Install roof pavers on pedestals set according to pedestal manufacturer's written instructions.

Retain paragraph and applicable subparagraph below if using mortar-faced insulation over roofing membrane.

M. Mortar-Faced Insulation:  Install mortar-faced board insulation loosely laid, according to manufacturer's written instructions, with tongue-and-groove joints nested.  Stagger end joints of adjoining rows and abut insulation.

Retain subparagraph below if ANSI/SPRI RP-4, System 1 design is required.  Heavyweight roof pavers of not less than 22 lb/sq. ft. (110 kg/sq. m) are required.

1. Install heavyweight roof pavers over mortar-faced insulation to a width not less than 24 inches (600 mm) on roof perimeter as defined by ANSI/SPRI RP-4.

Retain subparagraph below if ANSI/SPRI RP-4, System 2 design is required.  Heavyweight roof pavers of not less than 22 lb/sq. ft. (110 kg/sq. m) are required.

2. Install heavyweight roof pavers over mortar-faced insulation on roof corners and perimeter as defined by ANSI/SPRI RP-4.

Retain below and delete both subparagraphs above if perimeter mechanical securement is required.  Revise description of perimeter edge conditions below if requirements differ, depending on whether a parapet wall or a gravel stop is detailed on Drawings.  Coordinate inclusion of gravel stop or counterflashing for parapet with Division 07 Section "Sheet Metal Flashing and Trim" or "Roof Specialties," as applicable.

3. Mechanically fasten strapping and perimeter edge securement system over mortar-faced insulation according to manufacturer's written instructions.

3.10 BASE FLASHING INSTALLATION

A. Install sheet flashings and preformed flashing accessories and adhere to substrates according to membrane roofing system manufacturer's written instructions.

B. Apply solvent-based bonding adhesive to substrate and underside of sheet flashing at required rate and allow to partially dry.  Do not apply bonding adhesive to seam area of flashing.

C. Flash penetrations and field-formed inside and outside corners with sheet flashing.

D. Clean seam areas and overlap and firmly roll sheet flashings into the adhesive.  Weld side and end laps to ensure a watertight seam installation.

Select option below if mechanically anchoring sheet flashings.

E. Terminate and seal top of sheet flashings[ and mechanically anchor to substrate through termination bars].

3.11 WALKWAY INSTALLATION

Delete this Article if walkways are not required.

A. Flexible Walkways:  Install walkway products in locations indicated.  Heat weld to substrate or adhere walkway products to substrate with compatible adhesive according to roofing system manufacturer's written instructions.

B. Rubber Roof-Paver Walkways:  Install rubber roof-paver walkways according to manufacturer's written instructions, loosely laid, in locations indicated.

C. Roof-Paver Walkways:  Install heavyweight walkway roof pavers according to manufacturer's written instructions in locations indicated, to form walkways.  Leave 3 inches (75 mm) of space between adjacent roof pavers.

3.12 FIELD QUALITY CONTROL

A. Testing Agency:  Owner will engage a qualified independent testing and inspecting agency to perform roof tests and inspections and to prepare test reports.

A roof inspection is required by manufacturer before warranty issue.  Revise scope of inspection and source of report to a qualified roofing consultant or an independent testing and inspecting agency if preferred.

B. Final Roof Inspection:  Arrange for roofing system manufacturer's technical personnel to inspect roofing installation on completion and submit report to Architect.

Retain subparagraph below if Architect or Owner wants to be present during manufacturer's final inspection.

1. Notify Architect or Owner 48 hours in advance of date and time of inspection.

C. Repair or remove and replace components of membrane roofing system where test results or inspections indicate that they do not comply with specified requirements.

D. Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

3.13 PROTECTING AND CLEANING

A. Protect membrane roofing system from damage and wear during remainder of construction period.  When remaining construction will not affect or endanger roofing, inspect roofing for deterioration and damage, describing its nature and extent in a written report, with copies to Architect and Owner.

B. Correct deficiencies in or remove membrane roofing system that does not comply with requirements, repair substrates, and repair or reinstall membrane roofing system to a condition free of damage and deterioration at time of Substantial Completion and according to warranty requirements.

Retain below if coating membrane or if using fluid-applied bonding materials.

C. Clean overspray and spillage from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

3.14 ROOFING INSTALLER'S WARRANTY

Delete this Article, retain this warranty, or include another roofing Installer's warranty form if required.  Coordinate with Part 1 "Warranty" Article.  Another sample layout of this warranty is included in the Evaluations.

A. WHEREAS <Insert name> of <Insert address>, herein called the "Roofing Installer," has performed roofing and associated work ("work") on the following project:

1. Owner:  <Insert name of Owner.>

2. Address:  <Insert address.>

3. Building Name/Type:  <Insert information.>

4. Address:  <Insert address.>

5. Area of Work:  <Insert information.>

6. Acceptance Date:  <Insert date.>

7. Warranty Period:  <Insert time.>

8. Expiration Date:  <Insert date.>

B. AND WHEREAS Roofing Installer has contracted (either directly with Owner or indirectly as a subcontractor) to warrant said work against leaks and faulty or defective materials and workmanship for designated Warranty Period,

C. NOW THEREFORE Roofing Installer hereby warrants, subject to terms and conditions herein set forth, that during Warranty Period he will, at his own cost and expense, make or cause to be made such repairs to or replacements of said work as are necessary to correct faulty and defective work and as are necessary to maintain said work in a watertight condition.

D. This Warranty is made subject to the following terms and conditions:

1. Specifically excluded from this Warranty are damages to work and other parts of the building, and to building contents, caused by:

a. lightning;

Insert required wind speed below.

b. peak gust wind speed exceeding <Insert wind speed> mph (m/sec);

c. fire;

d. failure of roofing system substrate, including cracking, settlement, excessive deflection, deterioration, and decomposition;

e. faulty construction of parapet walls, copings, chimneys, skylights, vents, equipment supports, and other edge conditions and penetrations of the work;

f. vapor condensation on bottom of roofing; and

g. activity on roofing by others, including construction contractors, maintenance personnel, other persons, and animals, whether authorized or unauthorized by Owner.

2. When work has been damaged by any of foregoing causes, Warranty shall be null and void until such damage has been repaired by Roofing Installer and until cost and expense thereof have been paid by Owner or by another responsible party so designated.

3. Roofing Installer is responsible for damage to work covered by this Warranty but is not liable for consequential damages to building or building contents resulting from leaks or faults or defects of work.

4. During Warranty Period, if Owner allows alteration of work by anyone other than Roofing Installer, including cutting, patching, and maintenance in connection with penetrations, attachment of other work, and positioning of anything on roof, this Warranty shall become null and void on date of said alterations, but only to the extent said alterations affect work covered by this Warranty.  If Owner engages Roofing Installer to perform said alterations, Warranty shall not become null and void unless Roofing Installer, before starting said work, shall have notified Owner in writing, showing reasonable cause for claim, that said alterations would likely damage or deteriorate work, thereby reasonably justifying a limitation or termination of this Warranty.

5. During Warranty Period, if original use of roof is changed and it becomes used for, but was not originally specified for, a promenade, work deck, spray-cooled surface, flooded basin, or other use or service more severe than originally specified, this Warranty shall become null and void on date of said change, but only to the extent said change affects work covered by this Warranty.

6. Owner shall promptly notify Roofing Installer of observed, known, or suspected leaks, defects, or deterioration and shall afford reasonable opportunity for Roofing Installer to inspect work and to examine evidence of such leaks, defects, or deterioration.

7. This Warranty is recognized to be the only warranty of Roofing Installer on said work and shall not operate to restrict or cut off Owner from other remedies and resources lawfully available to Owner in cases of roofing failure.  Specifically, this Warranty shall not operate to relieve Roofing Installer of responsibility for performance of original work according to requirements of the Contract Documents, regardless of whether Contract was a contract directly with Owner or a subcontract with Owner's General Contractor.

E. IN WITNESS THEREOF, this instrument has been duly executed this <Insert day>  day of <Insert month>, <Insert year>.

1. Authorized Signature:  <Insert signature.>

2. Name:  <Insert name.>

3. Title:  <Insert title.>

END OF SECTION 075400

THERMOPLASTIC MEMBRANE ROOFING
075400 - 1

