Copyright 2006 AIA
MASTERSPEC Full Length
02/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 083323 - OVERHEAD COILING DOORS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Service doors[ with integral pass doors].

2. Insulated service doors[ with integral pass doors].

3. Counter doors.

4. Fire-rated service doors[ with integral pass doors].

5. Fire-rated, insulated service doors[ with integral pass doors].

6. Fire-rated counter doors.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 05 Section "Metal Fabrications" for miscellaneous steel supports.

2. Division 09 Section ["Exterior Painting"] [and] ["Interior Painting"] for finish painting of factory-primed doors.

3. Division 11 Section "Parking Control Equipment" for parking control equipment interlocked to overhead coiling doors.

4. Division 26 Sections for electrical service and connections for powered operators and accessories.

1.3 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design:  Design overhead coiling doors, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain first paragraph below for exterior doors.

B. Structural Performance, Exterior Doors:  Exterior overhead coiling doors shall withstand the wind loads, the effects of gravity loads, and loads and stresses within limits and under conditions indicated according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraphs below for design loads and load combinations.  Insert subparagraph for blast resistance if required.

Indicate wind loads, as determined by Project's structural engineer, on Drawings or in first subparagraph below.  Verify requirements of authorities having jurisdiction.  "Uniform pressure" option is minimum design pressure advertised by manufacturers.  See Evaluations.

1. Wind Loads:  [As indicated on Drawings] [Uniform pressure (velocity pressure) of 20 lbf/sq. ft. (960 Pa), acting inward and outward] <Insert loads>.

a. Basic Wind Speed:  [85 mph (38 m/s)] [90 mph (40 m/s)] [100 mph (44 m/s)] [110 mph (49 m/s)] <Insert value>.

b. Importance Factor:  <Insert factor>.

c. Exposure Category:  [A] [B] [C] [D].

Revise subparagraph below to suit Project; verify deflection limits with manufacturer.  If using doors as storm shutters to protect glass, stricter deflection limits may be required.

2. Deflection Limits:  Design overhead coiling doors to withstand design wind load without evidencing permanent deformation or disengagement of door components.

First paragraph below is not a common requirement; verify availability with manufacturer.  See "Wind Loads" Article in Evaluations.

C. Operability under Wind Load:  Design overhead coiling doors to remain operable under [design] [uniform pressure (velocity pressure) of 20 lbf/sq. ft. (960 Pa)] <Insert load> wind load, acting inward and outward.

Retain first paragraph below if required for Project.  The International Building Code (IBC) establishes criteria for buildings in hurricane-prone locations, and authorities having jurisdiction may require testing for glazed door assemblies and impact-protective systems used to protect glazing.  Verify requirements of authorities having jurisdiction.

D. Windborne-Debris-Impact-Resistance Performance:  Provide [glazed] [and] [impact-protective] overhead coiling doors that pass missile-impact and cyclic-pressure tests when tested according to [ASTM E 1886 and ASTM E 1996] <Insert requirement>.

1. Large Missile Test:  For overhead coiling doors located within 30 feet (9.144 m) of grade.

2. Small Missile Test:  For overhead coiling doors located more than 30 feet (9.144 m) above grade.

Retain first paragraph below with "Seismic Qualification Certificates" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

E. Seismic Performance:  Overhead coiling doors shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain first subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.  The optional text is an example for a swinging emergency egress door within a door curtain; revise to suit Project.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the emergency-egress-door component will be fully operational after the seismic event]."

Retain subparagraph below for projects requiring seismic design.  The Component Importance Factor is 1.5 for life safety components required to function after an earthquake.  For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and the component is necessary for continued operation of the facility or if failure of the component could impair continued operation of the facility, in which case it is 1.5.

2. Seismic Component Importance Factor:  [1.5] [1.0].

F. Operation Cycles:  Provide overhead coiling door components and operators capable of operating for not less than number of cycles indicated for each door.  One operation cycle is complete when a door is opened from the closed position to the fully open position and returned to the closed position.

1.4 SUBMITTALS

First four paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type and size of overhead coiling door and accessory.  Include the following:

1. Construction details, material descriptions, dimensions of individual components, profiles for slats, and finishes.

2. Rated capacities, operating characteristics, electrical characteristics, and furnished accessories.

3. For fire-rated doors, description of fire-release system including testing and resetting instructions.

B. Shop Drawings:  For each installation and for special components not dimensioned or detailed in manufacturer's product data.  Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain first subparagraph below for fire-rated doors.

2. Show locations of replaceable fusible links.

Retain subparagraph below if equipment includes wiring.

3. Wiring Diagrams:  For power, signal, and control wiring.

C. Samples for Initial Selection:  Manufacturer's finish charts showing full range of colors and textures available for units with factory-applied finishes.

1. Include similar Samples of accessories involving color selection.

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain first paragraph below with or without above.

D. Samples for Verification:  For each type of exposed finish required, prepared on Samples of size indicated below.

Revise subparagraphs below to suit Project; delete items not required.

1. Curtain Slats:  12 inches (305 mm) long[, including vision window secured to slat].

Retain option in first subparagraph below for electric door operators.

2. Bottom Bar:  6 inches (150 mm) long[ with sensor edge].

3. Guides:  6 inches (150 mm) long.

4. Brackets:  6 inches (150 mm) square.

5. Hood:  6 inches (150 mm) square.

6. Laminate-Clad Counter Panel Product:  6 inches (150 mm) square; for each type, color, pattern, and surface finish; laminated to core.

First paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

E. Delegated-Design Submittal:  For overhead coiling doors indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail fabrication and assembly of seismic restraints.

Retain subparagraph below unless design calculations have already been made and do not need to be confirmed.  Walls and jambs must be designed to support loads imposed by door.

2. Summary of forces and loads on walls and jambs.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

F. Qualification Data:  For qualified Installer.

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Sections specifying seismic controls.  See SEI/ASCE 7 for certification requirements for equipment and components.

G. Seismic Qualification Certificates:  For overhead coiling doors, accessories, and components, from manufacturer.

Retain first paragraph below if oversize fire-rated doors are required and acceptable to authorities having jurisdiction.

H. Oversize Construction Certification:  For door assemblies required to be fire-rated and that exceed size limitations of labeled assemblies.

I. Maintenance Data:  For overhead coiling doors to include in maintenance manuals.

1.5 QUALITY ASSURANCE

A. Installer Qualifications:  Manufacturer's authorized representative who is trained and approved for both installation and maintenance of units required for this Project.

B. Source Limitations:  Obtain overhead coiling doors from single source from single manufacturer.

Retain subparagraph below or revise to suit Project.

1. Obtain operators and controls from overhead coiling door manufacturer.

Retain first paragraph below if applicable.  Overhead coiling doors are labeled by UL for sizes not exceeding 152 sq. ft. (14 sq. m), with no dimension exceeding 13 feet 6 inches (4.11 m).  See Evaluations.

C. Fire-Rated Door Assemblies:  Assemblies complying with NFPA 80 that are listed and labeled by a qualified testing agency, for fire-protection ratings indicated, based on testing at as close to neutral pressure as possible according to [NFPA 252] [UBC Standard 7-2] [or] [UL 10B].

Retain first subparagraph below if applicable and acceptable to authorities having jurisdiction.

1. Oversize Fire-Rated Door Assemblies:  For units exceeding sizes of tested assemblies, provide certification by a qualified testing agency that doors comply with standard construction requirements for tested and labeled fire-rated door assemblies except for size.

Retain first subparagraph below if required.  The IBC allows an exception for buildings equipped throughout with fire-suppression sprinklers.

2. Temperature-Rise Limit:  [Where indicated] [At vertical exit enclosures and exit passageways], provide doors that have a maximum transmitted temperature end point of not more than 450 deg F (250 deg C) above ambient after 30 minutes of standard fire-test exposure.

3. Smoke Control:  [Where indicated] [In corridors and smoke barriers], provide doors that are listed and labeled with the letter "S" on the fire-rating label by a qualified testing agency for smoke- and draft-control based on testing according to [UBC Standard 7-2] [UL 1784]; with maximum air-leakage rate of 3.0 cfm/sq. ft. (0.01524 cu. m/s x sq. m) of door opening at 0.10 inch wg (24.9 Pa) for both ambient and elevated temperature tests.

Retain first paragraph below if acoustically rated doors are required.

D. Sound-Control Doors:  Assemblies that have been fabricated and tested to control the passage of sound and have minimum certified STC rating according to ASTM E 413.

Retain first paragraph below for motorized operator.

E. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

F. Regulatory Requirements:  Comply with applicable provisions in [the U.S. Architectural & Transportation Barriers Compliance Board's ADA-ABA Accessibility Guidelines] [and] [ICC/ANSI A117.1].

PART 2 -  PRODUCTS

2.1 DOOR CURTAIN MATERIALS AND CONSTRUCTION

Retain requirements in this article to suit Project.  If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

A. Door Curtains:  Fabricate overhead coiling-door curtain of interlocking metal slats, designed to withstand wind loading indicated, in a continuous length for width of door without splices.  Unless otherwise indicated, provide slats of thickness and mechanical properties recommended by door manufacturer for performance, size, and type of door indicated, and as follows:

Retain one or more of first three subparagraphs below for required slat materials.  Consult manufacturers' data and revise subparagraphs to specify other materials if needed.  Verify sheet thicknesses with manufacturer.

1. Steel Door Curtain Slats:  Zinc-coated (galvanized), cold-rolled structural steel sheet; complying with ASTM A 653/A 653M, with G90 (Z275) zinc coating; nominal sheet thickness (coated) of 0.028 inch (0.71 mm) and as required to meet requirements.

2. Stainless-Steel Door Curtain Slats:  ASTM A 666, Type 304; sheet thickness of 0.025 inch (0.64 mm) and as required to meet requirements.

Aluminum is not applicable to fire-rated assemblies.

3. Aluminum Door Curtain Slats:  ASTM B 209 (ASTM B 209M) sheet or ASTM B 221 (ASTM B 221M) extrusions, alloy and temper standard with manufacturer for type of use and finish indicated; thickness of 0.050 inch (1.27 mm) and as required to meet requirements.

Retain first subparagraph below if vision panels are required for curtain slats.  Vision-panel availability may be limited to some manufacturers and according to type of slat.  Verify availability with manufacturer.

4. Vision-Panel Glazing:  Manufacturer's standard clear glazing, fabricated from transparent acrylic sheet or fire-protection rated glass as required for type of door; set in glazing channel secured to curtain slats.

Retain four subparagraphs below as required for thermally or acoustically insulated doors; revise to suit Project.

5. Insulation:  Fill slats for insulated doors with manufacturer's standard thermal insulation complying with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively, according to ASTM E 84.  Enclose insulation completely within slat faces.

First two subparagraphs below describe different interior facings for insulated slats; facing in first subparagraph is most common.

6. Metal Interior Curtain-Slat Facing:  Match metal of exterior curtain-slat face.

First subparagraph below is available from Alpine, AlumaTek, and Lawrence; it is not applicable to fire-rated assemblies.  Retain one flame-spread index; verify availability with manufacturer.

7. Plastic Interior Curtain-Slat Facing:  Extruded PVC plastic with maximum flame-spread index of [25] [75] [200] and smoke-developed index of 450, according to ASTM E 84.

Subparagraph below is available from some manufacturers and can improve overall performance but may be less durable than entirely metal-on-metal slats.  Verify availability with manufacturer.

8. Gasket Seal:  Provide insulated slats with manufacturer's standard interior-to-exterior thermal break or with continuous gaskets between slats.

Retain one or both of first two paragraphs below or revise to suit Project.  Retain option for exterior doors.

B. Endlocks[ and Windlocks] for Service Doors:  Malleable-iron casings galvanized after fabrication, secured to curtain slats with galvanized rivets or high-strength nylon.  Provide locks on not less than alternate curtain slats for curtain alignment and resistance against lateral movement.

C. Endlocks for Counter Doors:  Manufacturer's standard locks on not less than alternate curtain slats for curtain alignment and resistance against lateral movement.

Retain one or both of first two paragraphs below or revise to suit Project.  Verify availability with manufacturer.

D. Bottom Bar for Service Doors:  Consisting of two angles, each not less than 1-1/2 by 1-1/2 by 1/8 inch (38 by 38 by 3 mm) thick; fabricated from manufacturer's standard hot-dip galvanized steel, stainless steel, or aluminum extrusions to match curtain slats and finish.

E. Bottom Bar for Counter Doors:  Manufacturer's standard continuous channel or tubular shape, fabricated from manufacturer's standard hot-dip galvanized steel, stainless steel, or aluminum extrusions to match curtain slats and finish.

Retain first paragraph below for interior service or counter doors.  For exterior doors, retain weatherseals specified in "Curtain Accessories" Article.

F. Astragal for Interior Doors:  Equip each door bottom bar with a replaceable, adjustable, continuous, compressible gasket of flexible vinyl, rubber, or neoprene as a cushion bumper.

G. Curtain Jamb Guides:  Manufacturer's standard angles or channels and angles of same material and finish as curtain slats unless otherwise indicated, with sufficient depth and strength to retain curtain, to allow curtain to operate smoothly, and to withstand loading.  Slot bolt holes for guide adjustment.  Provide removable stops on guides to prevent overtravel of curtain[, and a continuous bar for holding windlocks].

Retain subparagraph below for removable post and guides separating multiple counter-door installations that require a clear opening.

1. Removable Posts and Jamb Guides for Counter Doors:  Manufacturer's standard.

Retain paragraph below if pass doors are required.

H. Pass Door(s):  Door and frame assembly constructed integrally with the coiling-door assembly[ and bearing the same fire rating].  Complying with egress and accessibility requirements of authorities having jurisdiction.

1. Door Frame and Integral Jamb Guide:  Fabricate of angles or channels and angles of same material and finish as curtain slats unless otherwise indicated, with sufficient depth and strength to retain curtain, to allow curtain to operate smoothly, and to withstand loading.

Frame in first subparagraph below is available from many manufacturers.  See Evaluations.

2. Hinged Frame:  Hinged pass door and frame that swings out of the way, as a unit, to allow use of the full coiling-door opening width.  One jamb of the pass-door frame is hinged and the other jamb includes a guide for the lower, narrower part of the coiling-door curtain.

Retain first subparagraph below only if there is sufficient headroom above door to accommodate rigid lower part of coiling door that contains the pass door.  This type is available from McKeon; verify availability with other manufacturers.

3. Rigid Frame:  Rigid pass door and frame that are built into the rigid, lower part of the door curtain and that raise with the curtain.

4. Locking Hardware:

Consult manufacturer on hardware that can be installed in pass doors.

a. [Lockset] [Exit Hardware]:  [As specified in Division 08 Section "Door Hardware."] [As selected by Architect from manufacturer's full range.] <Insert requirement.>

Retain one of first two options in first subparagraph below.

b. Lock Cylinders:  Provide cylinders [specified in Division 08 Section "Door Hardware."] [standard with manufacturer] [and keyed to building keying system].

Retain first subparagraph below if cylinders are provided by door manufacturer.

c. Keys:  [Two] [Three] <Insert number> for each cylinder.

Revise subparagraph below to suit Project.

5. Thresholds:  Equip pass doors with integral thresholds that comply with egress and accessibility requirements of authorities having jurisdiction.

2.2 HOOD

Retain requirements in this article to suit Project if coiled curtain and operating mechanism are exposed (not concealed in ceiling or soffit).  Integral frame, hood, and fascia assemblies for counter doors are included in "Counter Doors" Article.  If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

A. General:  Form sheet metal hood to entirely enclose coiled curtain and operating mechanism at opening head.  Contour to fit end brackets to which hood is attached.  Roll and reinforce top and bottom edges for stiffness.  Form closed ends for surface-mounted hoods and fascia for any portion of between-jamb mounting that projects beyond wall face.  Equip hood with intermediate support brackets as required to prevent sagging.

Retain required material(s) in first three subparagraphs below.  Thicker steel sheet is available from some manufacturers; verify availability.

1. Galvanized Steel:  Nominal 0.028-inch- (0.71-mm-) thick, hot-dip galvanized steel sheet with G90 (Z275) zinc coating, complying with ASTM A 653/A 653M.

2. Stainless Steel:  0.025-inch- (0.64-mm-) thick stainless-steel sheet, Type 304, complying with ASTM A 666.

First subparagraph below is for non-fire-rated doors only.  Clear- and color-anodized finishes are available.

3. Aluminum:  0.040-inch- (1.02-mm-) thick aluminum sheet complying with ASTM B 209 (ASTM B 209M), of alloy and temper recommended by manufacturer and finisher for type of use and finish indicated.

Retain first subparagraph below for fire-rated assemblies.

4. Include automatic drop baffle on fire-rated doors to guard against passage of smoke or flame.

Retain subparagraph below for exterior-mounted doors.

5. Exterior-Mounted Doors:  Fabricate hood to act as weather protection and with a perimeter sealant-joint-bead profile for applying joint sealant.

2.3 COUNTER DOORS

Retain requirements in this article to suit Project.  If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

Retain first paragraph below only for counter doors or fire-rated counter doors with integral frame and optional sill, which are available from some manufacturers; verify availability.

A. Integral Frame, Hood, and Fascia for Counter Door:  Welded sheet metal assembly of the following sheet metal:

Retain required material(s) in subparagraphs below.

1. Galvanized Steel:  Nominal [0.064-inch- (1.63-mm-)] <Insert thickness> thick, hot-dip galvanized steel sheet with G90 (Z275) zinc coating, complying with ASTM A 653/A 653M.

2. Stainless Steel:  [0.062-inch- (1.59-mm-)] <Insert thickness> thick stainless-steel sheet, Type 304, complying with ASTM A 666.

Retain first paragraph below if required.  Stainless steel with No. 4 finish is standard.  Verify availability of other finishes with manufacturer.

B. Integral Metal Sill for Counter Door:  Fabricate sills as integral part of frame assembly of Type 304 stainless steel in manufacturer's standard thickness with [No. 4] <Insert finish> finish.

Product in paragraph below is available from Cookson, Cornell, and Overhead Door, and may be specified for interior openings in lieu of integral sheet-metal sills.

C. Fire-Rated, Laminate Counter:  Fire-door manufacturer's high-pressure decorative laminate-covered countertop, UL or ITS tested and labeled for 1-1/2-hour fire rating for approved use with fire-door assembly.

2.4 LOCKING DEVICES

Retain requirements in this article to suit Project.  If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

Retain one or both of first two paragraphs below for required locking device(s); revise to suit Project.  First paragraph is standard for push-up doors; revise if no padlock is required or if manufacturer's standard is a bolt on one side.  Second paragraph describes a locking device with choice of locations and operation as retained in door assembly articles in Part 2.

A. Slide Bolt:  Fabricate with side-locking bolts to engage through slots in tracks for locking by padlock, located on both left and right jamb sides, operable from coil side.

B. Locking Device Assembly:  Fabricate with cylinder lock, spring-loaded dead bolt, operating handle, cam plate, and adjustable locking bars to engage through slots in tracks.

Retain one of first two options in first subparagraph below.

1. Lock Cylinders:  Provide cylinders [specified in Division 08 Section "Door Hardware."] [standard with manufacturer] [and keyed to building keying system].

Retain subparagraph below if cylinders are provided by door manufacturer.

2. Keys:  Provide [Two] [Three] <Insert number> for each cylinder.

Retain first paragraph below for chain-hoist-operated doors or emergency chain-hoist operation.

C. Chain Lock Keeper:  Suitable for padlock.

Retain paragraph below for power-operated doors.

D. Safety Interlock Switch:  Equip power-operated doors with safety interlock switch to disengage power supply when door is locked.

2.5 CURTAIN ACCESSORIES

Retain requirements in this article to suit Project.  If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

Retain first paragraph below for fire-rated service and counter doors.

A. Smoke Seals:  Equip each fire-rated door with smoke-seal perimeter gaskets for smoke and draft control as required for door listing and labeling by a qualified testing agency.

Retain first paragraph below for exterior doors.

B. Weatherseals:  Equip each exterior door with weather-stripping gaskets fitted to entire perimeter of door for a weathertight installation, unless otherwise indicated.

1. At door head, use 1/8-inch- (3-mm-) thick, replaceable, continuous sheet secured to inside of hood.

2. At door jambs, use replaceable, adjustable, continuous, flexible, 1/8-inch- (3-mm-) thick seals of flexible vinyl, rubber, or neoprene.

Retain first paragraph below for push-up-operated doors or emergency push-up operation.

C. Push/Pull Handles:  Equip each push-up-operated or emergency-operated door with lifting handles on each side of door, finished to match door.

Retain subparagraph below if required.

1. Provide pull-down straps or pole hooks for doors more than 84 inches (2130 mm) high.

Retain paragraph below for fire-rated service or counter doors.

D. Automatic-Closing Device for Fire-Rated Doors:  Equip each fire-rated door with an automatic-closing device that is inoperative during normal door operations and that has a governor unit complying with NFPA 80 and an easily tested and reset release mechanism designed to be activated by the following:

Retain one or more of four subparagraphs below and insert others if required to suit Project.  If more than one type of activation (or combination) is required, identify primary and secondary closing devices.  Verify requirements of authorities having jurisdiction.  See Evaluations.

Retain first subparagraph below to comply with NFPA 80 requirement for fusible links on both sides of door opening.  Revise if not required on both sides of door opening or to add fusible-link ceiling unit for use with suspended ceilings.

1. Replaceable fusible links with temperature rise and melting point of [165 deg F (74 deg C)] <Insert temperature> interconnected and mounted on both sides of door opening.

2. Manufacturer's standard UL-labeled smoke detector and door-holder-release devices.

3. Manufacturer's standard UL-labeled heat detector and door-holder-release devices.

4. Building fire-detection and -alarm systems and manufacturer's standard door-holder-release devices.

Insert other accessories to suit Project.

2.6 COUNTERBALANCING MECHANISM

Retain this article for all doors.

A. General:  Counterbalance doors by means of manufacturer's standard mechanism with an adjustable-tension, steel helical torsion spring mounted around a steel shaft and contained in a spring barrel connected to top of curtain with barrel rings.  Use grease-sealed bearings or self-lubricating graphite bearings for rotating members.

B. Counterbalance Barrel:  Fabricate spring barrel of manufacturer's standard hot-formed, structural-quality, welded or seamless carbon-steel pipe, of sufficient diameter and wall thickness to support rolled-up curtain without distortion of slats and to limit barrel deflection to not more than 0.03 in./ft. (2.5 mm/m) of span under full load.

C. Spring Balance:  One or more oil-tempered, heat-treated steel helical torsion springs.  Size springs to counterbalance weight of curtain, with uniform adjustment accessible from outside barrel.  Secure ends of springs to barrel and shaft with cast-steel barrel plugs.

D. Torsion Rod for Counterbalance Shaft:  Fabricate of manufacturer's standard cold-rolled steel, sized to hold fixed spring ends and carry torsional load.

E. Brackets:  Manufacturer's standard mounting brackets of either cast iron or cold-rolled steel plate.

2.7 MANUAL DOOR OPERATORS

Retain this article for manually operated doors, not including electric door operators with emergency manual operation.

Retain requirements in this article to suit Project.  If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

A. Equip door with manufacturer's recommended manual door operator unless another type of door operator is indicated.

Push-up door operation in first paragraph below is common for service doors with area of not more than 80 sq. ft. (7.4 sq. m).  Counter-door limitations are similar, but counter depth is also a factor.  Standard operation force as high as 35 lbf (156 N) is advertised by City-Gates.

B. Push-up Door Operation:  Design counterbalance mechanism so required lift or pull for door operation does not exceed [25 lbf (111 N)] <Insert force>.

Chain-hoist and crank operators in two paragraphs below are common for manually operated doors with area of more than 80 sq. ft. (7.4 sq. m).

C. Chain-Hoist Operator:  Consisting of endless steel hand chain, chain-pocket wheel and guard, and gear-reduction unit with a maximum [25 lbf (111 N)] [30 lbf (133 N)] <Insert force> force for door operation.  Provide alloy-steel hand chain with chain holder secured to operator guide.

"Awning" and "box" are the two types of crank operators.  Indicate required type in door assembly articles retained in Part 2.  See Evaluations.

D. Crank Operator:  Consisting of crank and crank gearbox, steel crank drive shaft, and gear-reduction unit, of type indicated.  Size gears to require not more than [25 lbf (111 N)] [30 lbf (133 N)] <Insert force> force to turn crank.  Fabricate gearbox to be oil tight and to completely enclose operating mechanism.  Provide manufacturer's standard crank-locking device.

2.8 ELECTRIC DOOR OPERATORS

Retain this article for electric door operators, including emergency manual operation, and for larger units and remote-control or frequently operated doors.  Coordinate with electrical engineer for interface of electric door operators and equipment with fire-protection system.

Retain requirements in this article to suit Project.  If retaining multiple requirements for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

Retain option in first paragraph below if retaining "Operation Cycles" Paragraph in Part 1 "Performance Requirements" Article.

A. General:  Electric door operator assembly of size and capacity recommended and provided by door manufacturer for door[ and operation-cycles requirement] specified, with electric motor and factory-prewired motor controls, starter, gear-reduction unit, solenoid-operated brake, clutch, remote-control stations, control devices, integral gearing for locking door, and accessories required for proper operation.

1. Comply with NFPA 70.

2. Provide control equipment complying with NEMA ICS 1, NEMA ICS 2, and NEMA ICS 6, with NFPA 70 Class 2 control circuit, maximum 24 V, ac or dc.

Durability requirement in first paragraph below is separate from operation cycles, which apply to the whole door system and are discussed in "Performance Requirements" Article.

B. Usage Classification:  Electric operator and components capable of operating for not less than number of cycles per hour indicated for each door.

C. Door Operator Location(s):  Operator location indicated for each door.

Retain one or more of five subparagraphs below as required for Project.  Delete all subparagraphs if operator location(s) is shown on Drawings.

1. Top-of-Hood Mounted:  Operator is mounted to the right or left door head plate with the operator on top of the door-hood assembly and connected to the door drive shaft with drive chain and sprockets.  Headroom is required for this type of mounting.

2. Front-of-Hood Mounted:  Operator is mounted to the right or left door head plate with the operator on coil side of the door-hood assembly and connected to the door drive shaft with drive chain and sprockets.  Front clearance is required for this type of mounting.

3. Wall Mounted:  Operator is mounted to the inside front wall on the left or right side of door and connected to door drive shaft with drive chain and sprockets.  Side room is required for this type of mounting.  Wall mounted operator can also be mounted above or below shaft; if above shaft, headroom is required.

4. Bench Mounted:  Operator is mounted to the right or left door head plate and connected to the door drive shaft with drive chain and sprockets.  Side room is required for this type of mounting.

5. Through-Wall Mounted:  Operator is mounted on other side of wall from coil side of door.

Default motor characteristics are specified in Division 11 Section "Common Motor Requirements for Equipment."

D. Electric Motors:  Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements specified in Division 11 Section "Common Motor Requirements for Equipment" unless otherwise indicated.

1. Electrical Characteristics:

Retain "Single phase" or "Polyphase" option in first subparagraph below based on required motor size.  Verify motor performance and availability with door manufacturer and coordinate electrical characteristics with electrical engineer.  See Evaluations.

a. Phase:  [Single phase] [Polyphase].

b. Volts:  [115] [208] [230] [460] <Insert value> V.

c. Hertz:  60.

2. Motor Type and Controller:  Reversible motor and controller (disconnect switch) for motor exposure indicated.

Speed in first subparagraph below is for standard-speed doors.  Consult manufacturer and revise for higher-speed operation.

3. Motor Size:  Minimum size as indicated.  If not indicated, large enough to start, accelerate, and operate door in either direction from any position, at a speed not less than 8 in./sec. (203 mm/s) and not more than 12 in./sec. (305 mm/s), without exceeding nameplate ratings or service factor.

Revise first subparagraph below if required; coordinate requirements with design electrical engineer.  Verify which electrical devices, connections, and wiring, if any, are furnished or installed by other than the coiling door manufacturer and that they comply with requirements for electrical devices and connections specified in Division 26 Sections.

4. Operating Controls, Controllers (Disconnect Switches), Wiring Devices, and Wiring:  Manufacturer's standard unless otherwise indicated.

5. Coordinate wiring requirements and electrical characteristics of motors and other electrical devices with building electrical system and each location where installed.

E. Limit Switches:  Equip each motorized door with adjustable switches interlocked with motor controls and set to automatically stop door at fully opened and fully closed positions.

Retain first paragraph below if required; revise if required for fire-rated door applications according to requirements of authorities having jurisdiction.

F. Obstruction Detection Device:  Equip motorized door with indicated external automatic safety sensor capable of protecting full width of door opening.[  For non-fire-rated doors, activation of device immediately stops and reverses downward door travel.] [ For fire-rated doors, activation delays closing.]

Retain one or both subparagraphs below to suit Project.

1. Photoelectric Sensor:  Manufacturer's standard system designed to detect an obstruction in door opening without contact between door and obstruction.

Retain first subparagraph below if a self-monitoring system to detect failure of sensor device is required.

a. Self-Monitoring Type:  Designed to interface with door operator control circuit to detect damage to or disconnection of sensing device.  When self-monitoring feature is activated, door closes only with sustained pressure on close button.

2. Sensor Edge:  Automatic safety sensor edge, located within astragal or weather stripping mounted to bottom bar.  Contact with sensor activates device.  Connect to control circuit using manufacturer's standard take-up reel or self-coiling cable.

Retain subparagraph below if a self-monitoring system to detect failure of sensor device is required.

a. Self-Monitoring Type:  Four-wire configured device designed to interface with door operator control circuit to detect damage to or disconnection of sensor edge.

Revise first paragraph below to suit Project.  A sustained-pressure (in lieu of a momentary-contact) switch may be required for closing or opening cycles, or both.  Verify acceptability with authorities having jurisdiction; revise requirements and door assembly articles retained in Part 2 as needed.

G. Remote-Control Station:  Momentary-contact, three-button control station with push-button controls labeled "Open," "Close," and "Stop."

Retain first subparagraph below for interior, clean, and dry installations.  Revise to suit Project.

1. Interior units, full-guarded, surface-mounted, heavy-duty type, with general-purpose NEMA ICS 6, Type 1 enclosure.

Retain subparagraph below for exterior, dusty, wet, or humid installations.  Revise to suit Project.

2. Exterior units, full-guarded, standard-duty, surface-mounted, weatherproof type, NEMA ICS 6, Type 4 enclosure, key operated.

H. Emergency Manual Operation:  Equip each electrically powered door with capability for emergency manual operation.  Design manual mechanism so required force for door operation does not exceed [25 lbf (111 N)] [30 lbf (133 N)] <Insert force>.

I. Emergency Operation Disconnect Device:  Equip operator with hand-operated disconnect mechanism for automatically engaging manual operator and releasing brake for emergency manual operation while disconnecting motor without affecting timing of limit switch.  Mount mechanism so it is accessible from floor level.  Include interlock device to automatically prevent motor from operating when emergency operator is engaged.

J. Motor Removal:  Design operator so motor may be removed without disturbing limit-switch adjustment and without affecting emergency manual operation.

Insert additional equipment for door operation if required; verify availability with manufacturer.  Remaining paragraphs are examples only; retain or revise to suit Project.

K. Audible and Visual Signals:  Audible alarm and visual indicator lights in compliance with regulatory requirements for accessibility.

Retain paragraph below if required as an auxiliary device; revise to suit Project.

L. Radio-Control System:  Consisting of the following:

1. Three-channel universal coaxial receiver to open, close, and stop door; [one] [two] <Insert number> per operator.

Revise first subparagraph below for multiple remote controls.

2. Multifunction remote control.

Retain subparagraph below if antenna is required.

3. Remote-antenna mounting kit.

2.9 DOOR ASSEMBLY <Insert drawing designation>

Copy this article and re-edit for each non-fire-rated coiling-door unit.  This article is intended as a guide if Project requires several units of varying sizes, characteristics, and capacities.  For each door assembly, retain required options in this article and their related requirements in other Part 2 articles.

Insert number to complete drawing designation for each unit required.  Use these designations on Drawings to identify each overhead coiling door.

A. [Service] [Insulated Service] [Counter] Door:  Overhead coiling door formed with curtain of interlocking metal slats.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ACME Rolling Doors.

b. Alpine Overhead Doors, Inc.

c. AlumaTek, Inc.

d. C.H.I. Overhead Doors.

e. City-Gates.

f. Cookson Company.

g. Cornell Iron Works, Inc.

h. Dynamic Closures Corp.

i. Lawrence Roll-Up Doors, Inc.

j. Mahon Door Corporation.

k. McKeon Rolling Steel Door Company, Inc.

l. Metro Door.

m. Overhead Door Corporation.

n. QMI Security Solutions.

o. Raynor.

p. Southwestern Steel Rolling Door Co.

q. Wayne-Dalton Corp.

r. Windsor Door.

s. <Insert manufacturer's name>.

Retain one option in first paragraph below or revise to suit Project.  First option is standard with some manufacturers; second option is more commonly used.  Third and fourth options are for high-cycle operation, corrosive environments, and severe or abusive use.

B. Operation Cycles:  Not less than [10,000] [20,000] [50,000] [100,000] <Insert number>.

Retain subparagraph below if high-cycle doors are specified.

1. Include tamperproof cycle counter.

Retain first paragraph below for acoustically insulated doors.  STC rating of 26 is available from Cornell.  Verify availability with other manufacturers.

C. STC Rating:  [26] <Insert STC rating>.

Retain first paragraph below for thermally insulated doors.

D. Curtain R-Value:  [4.5 deg F x h x sq. ft./Btu (0.792 K x sq. m/W)] [5.0 deg F x h x sq. ft./Btu (0.881 K x sq. m/W)] [6.0 deg F x h x sq. ft./Btu (1.057 K x sq. m/W)] <Insert value>.

E. Door Curtain Material:  [Galvanized steel] [Stainless steel] [Aluminum].

Slat profile and sizes in first paragraph below vary among manufacturers.  First two size options are advertised for counter-door slats; last three size options are advertised for service-door slats.  Revise size to a range if exact size is not important.

F. Door Curtain Slats:  [Curved] [Flat] profile slats of [1-1/4-inch (32-mm)] [1-1/2-inch (38-mm)] [1-7/8-inch (48-mm)] [2-5/8-inch (67-mm)] [3-1/4-inch (83-mm)] <Insert dimension> center-to-center height.

Features in first three subparagraphs below are available for service doors, from some manufacturers, for specific slat materials and profiles.  Verify availability and size with manufacturer; revise to suit Project.

1. Perforated Slats:  Approximately [1/16-inch (1.6-mm) pinholes] [3/32-inch (2.4-mm) pinholes] [7/8-inch- (22-mm-) wide by 3/8-inch- (10-mm-) high slots] <Insert dimensions>.

2. Fenestrated Slats:  Approximately [3- by 5/8-inch (76- by 16-mm)] [4- by 5/8-inch (102- by 16-mm)] [10- by 1-5/8-inch (254- by 41-mm)] <Insert dimensions> openings spaced approximately [1-1/2 inches (38 mm)] <Insert dimension> apart and beginning 12 inches (305 mm) from jamb guides.

Retain opening size and spacing in first subparagraph below or revise to suit Project.  Retain last option for use in thermally insulated doors.

3. Vision Panels:  Approximately 10- by 1-5/8-inch (254- by 41-mm) openings spaced approximately 2 inches (51 mm) apart and beginning 12 inches (305 mm) from end guides; in [two] [three] <Insert number> rows of slats at height indicated on Drawings; installed with[ insulated] vision-panel glazing.

4. Insulated-Slat Interior Facing:  [Metal] [Plastic].

"Galvanized steel" and "Stainless steel" options in first paragraph below are most commonly used for service doors.  Consult manufacturer for availability of last two options, which are sometimes used with counter doors.

G. Curtain Jamb Guides:  [Galvanized steel] [Stainless steel] [Aluminum] with exposed finish matching curtain slats.[  Provide continuous integral wear strips to prevent metal-to-metal contact and to minimize operational noise.] [  Provide removable post(s) and jamb guides where shown on Drawings.]

H. Pass Door(s):  [Hinged] [Rigid] frame with [lockset] [exit hardware].

Retain one of first two paragraphs below.

I. Hood:  [Match curtain material and finish] [Galvanized steel] [Stainless steel] [Aluminum].

First option in first subparagraph below is standard.  Verify availability of second option with manufacturer.

1. Shape:  [Round] [Square] [As shown on Drawings] <Insert shape>.

2. Mounting:  [Face of wall] [Between jambs] [As shown on Drawings].

J. Integral Frame, Hood, and Fascia for Counter Door:  [Galvanized steel] [Stainless steel].

1. Mounting:  [Face of wall] [Between jambs] [As shown on Drawings].

K. Sill Configuration for Counter Door:  [No sill] [Integral metal sill].

Retain one of first two options in first paragraph below.  Retain last option for chain-hoist-operated doors or emergency chain-hoist operation.

L. Locking Devices:  Equip door with [slide bolt for padlock] [locking device assembly] [and] [chain lock keeper].

Retain subparagraph below if retaining "locking device assembly" option in paragraph above.

1. Locking Device Assembly:  [Single-jamb side] [Cremone type, both jamb sides] locking bars, operable from [inside with thumb turn] [outside with cylinder] [outside only, with cylinder] [inside and outside with cylinders] <Insert requirement>.

Retain one of first two paragraphs below.

M. Manual Door Operator:  [Push-up operation] [Chain-hoist operator] [Manufacturer's standard crank operator] [Awning-crank operator] [Wall-crank operator].

Retain first subparagraph below for chain or crank operator if located on other side of wall from door curtain.

1. Provide operator with through-wall shaft operation.

Retain subparagraph below for crank operators if required.

2. Provide operator with manufacturer's standard removable operating arm.

N. Electric Door Operator:

Retain one option in first subparagraph below or revise to suit Project.  Usage classification varies among manufacturers; it is a durability requirement separate from whole-door operation cycles.  Consult manufacturer for specific recommendations.

1. Usage Classification:  [Heavy duty, 60 to 90 cycles per hour] [Standard duty, up to 60 cycles per hour] [Medium duty, up to 15 cycles per hour] [Light duty, up to 10 cycles per hour] <Insert classification>.

2. Operator Location:  [Top of hood] [Front of hood] [Wall] [Bench] [Through wall] [As shown on Drawings].

Retain one option in first subparagraph below or revise to suit Project.  The operating environment, including hazardous conditions, may require other motor types and enclosure modifications.

3. Motor Exposure:  [Interior] [Exterior, wet, and humid].

4. Emergency Manual Operation:  [Push-up] [Chain] [Crank] type.

"Pneumatic sensor" option in first subparagraph below may be limited to a width of 18 feet (5.5 m).  Verify availability with manufacturer.

5. Obstruction-Detection Device:  Automatic [photoelectric sensor] [electric sensor edge on bottom bar] [pneumatic sensor edge on bottom bar] [; self-monitoring type].

Retain first subparagraph below if retaining either second or third option in last subparagraph above.

a. Sensor Edge Bulb Color:  [Black] [As selected by Architect from manufacturer's full range] <Insert color>.

6. Remote-Control Station:  [Interior] [Exterior] [Where shown on Drawings] <Insert location>.

7. Other Equipment:  [Audible and visual signals] [Radio-control system] <Insert device>.

O. Door Finish:

Retain one of first four subparagraphs below.  These include advertised materials and finishes; available materials and finishes vary with each manufacturer.  If retaining more than one, indicate location of each on Drawings or by inserts.

Second option in first subparagraph below is standard; verify availability of other aluminum finishes with manufacturer.

1. Aluminum Finish:  [Mill] [Clear anodized] [Light bronze anodized] [Medium bronze anodized] [Dark bronze anodized] [Black anodized] [Anodized color matching Architect's sample] [Anodized color as selected by Architect from full range of industry colors and color densities] <Insert color>.

2. Baked-Enamel or Powder-Coated Finish:  [Color as indicated by manufacturer's designations] [Color matching Architect's sample] [Color as selected by Architect from manufacturer's full range] <Insert color and gloss>.

3. Factory Prime Finish:  Manufacturer's standard color.

Second option in first subparagraph below is standard; verify availability of other stainless-steel finishes with manufacturer.

4. Stainless-Steel Finish:  [No. 2B (bright, cold rolled)] [No. 4 (polished directional satin)] <Insert finish>.

Retain subparagraph below for insulated door curtains.

5. Interior Curtain-Slat Facing:  [Match finish of exterior curtain-slat face] [PVC plastic] <Insert finish>.

2.10 FIRE-RATED DOOR ASSEMBLY <Insert drawing designation>

Copy this article and re-edit for each fire-rated coiling-door unit.  This article is intended as a guide if Project requires several units of varying sizes, characteristics, and capacities.  For each door assembly, retain required options in this article and their related requirements in other Part 2 articles.

Insert number to complete drawing designation for each unit required.  Use these designations on Drawings to identify each overhead coiling door.

A. Fire-Rated [Service] [Insulated Service] [Counter] Door:  Overhead fire-rated coiling door formed with curtain of interlocking metal slats.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ACME Rolling Doors.

b. Alpine Overhead Doors, Inc.

c. AlumaTek, Inc.

d. C.H.I. Overhead Doors.

e. City-Gates.

f. Cookson Company.

g. Cornell Iron Works, Inc.

h. Lawrence Roll-Up Doors, Inc.

i. Mahon Door Corporation.

j. McKeon Rolling Steel Door Company, Inc.

k. Overhead Door Corporation.

l. Raynor.

m. Southwestern Steel Rolling Door Co.

n. Wayne-Dalton Corp.

o. Windsor Door.

p. <Insert manufacturer's name>.

Retain one option in first paragraph below or revise to suit Project.  First option is standard with some manufacturers; second option is more commonly used.  Third and fourth options are for high-cycle operation, corrosive environments, and severe or abusive use.

B. Operation Cycles:  Not less than [10,000] [20,000] [50,000] [100,000] <Insert number>.

Retain subparagraph below if high-cycle doors are specified.

1. Include tamperproof cycle counter.

Temperature-rise limit in first paragraph below is available from McKeon.  Verify availability with other manufacturers.

C. Fire Rating:  [3/4 hour] [1 hour] [1-1/2 hours] [3 hours] [4 hours] [with temperature-rise limit] [and] [with smoke control].

Retain first paragraph below for acoustically insulated, fire-rated doors.  STC rating of 27 is available from McKeon.  Verify availability with other manufacturers.

D. STC Rating:  [27] <Insert STC rating>.

Retain first paragraph below for thermally insulated doors.

E. Curtain R-Value:  [4.5 deg F x h x sq. ft./Btu (0.792 K x sq. m/W)] [5.0 deg F x h x sq. ft./Btu (0.881 K x sq. m/W)] [6.0 deg F x h x sq. ft./Btu (1.057 K x sq. m/W)] <Insert value>.

F. Door Curtain Material:  [Galvanized steel] [Stainless steel].

Slat profile and sizes in first paragraph below vary among manufacturers.  First two size options are advertised for counter-door slats; last three size options are advertised for service-door slats.  Revise size to a range if exact size is not important.

G. Door Curtain Slats:  [Curved] [Flat] profile slats of [1-1/4-inch (32-mm)] [1-1/2-inch (38-mm)] [1-7/8-inch (48-mm)] [2-5/8-inch (67-mm)] [3-1/4-inch (83-mm)] <Insert dimension> center-to-center height.

Features in two subparagraphs below are available for service doors, from some manufacturers, for specific slat materials and profiles.  Verify availability and size with manufacturer; revise to suit Project.

Retain opening size and spacing in first subparagraph below or revise to suit Project.

1. Vision Panels:  Approximately 10- by 1-5/8-inch (254- by 41-mm) openings spaced approximately 2 inches (51 mm) apart and beginning 12 inches (305 mm) from end guides; in [two] [three] <Insert number> rows of slats at height indicated on Drawings; installed with fire-rated vision-panel glazing.

2. Insulated-Slat Interior Facing:  Metal.

H. Curtain Jamb Guides:  [Galvanized steel] [Stainless steel] with exposed finish matching curtain slats.

I. Pass Door(s):  [Hinged] [Rigid] frame with [lockset] [exit hardware].

Retain one of first two paragraphs below.

J. Hood:  [Match curtain material and finish] [Galvanized steel] [Stainless steel].

First option in first subparagraph below is standard.  Verify availability of second option with manufacturer.

1. Shape:  [Round] [Square] [As shown on Drawings] <Insert shape>.

2. Mounting:  [Face of wall] [Between jambs] [As shown on Drawings].

K. Integral Frame, Hood, and Fascia for Counter Door:  [Galvanized steel] [Stainless steel].

1. Mounting:  [Face of wall] [Between jambs] [As shown on Drawings].

L. Sill Configuration for Fire-Rated Counter Door:  [No sill] [Integral metal sill] [Fire-rated, laminate counter].

Retain subparagraph below only if retaining last option in paragraph above.

1. High-Pressure Decorative Laminate:  Match color, pattern, and finish [as indicated by manufacturer's designations] [of Architect's sample] [as selected by Architect from manufacturer's full range] <Insert requirement>.

Retain one of first two options in first paragraph below.  Retain last option for chain-hoist-operated doors or emergency chain-hoist operation.

M. Locking Devices:  Equip door with [slide bolt for padlock] [locking device assembly] [and] [chain lock keeper].

Retain subparagraph below if retaining "locking device assembly" option in paragraph above.

1. Locking Device Assembly:  [Single-jamb side] [Cremone type, both jamb sides] locking bars, operable from [inside with thumbturn] [outside with cylinder] [outside only, with cylinder] [inside and outside with cylinders] <Insert requirement>.

Retain one of first two paragraphs below.

N. Manual Door Operator:  [Push-up operation] [Chain-hoist operator] [Manufacturer's standard crank operator] [Awning-crank operator] [Wall-crank operator].

Retain first subparagraph below for chain or crank operator if located on other side of wall from door curtain.

1. Provide operator with through-wall shaft operation.

Retain subparagraph below for crank operators if required.

2. Provide operator with manufacturer's standard removable operating arm.

O. Electric Door Operator:

Retain one option in first subparagraph below or revise to suit Project.  Usage classification varies among manufacturers; it is a durability requirement separate from whole-door operation cycles.  Consult manufacturer for specific recommendations.

1. Usage Classification:  [Heavy duty, 60 to 90 cycles per hour] [Standard duty, up to 60 cycles per hour] [Medium duty, up to 15 cycles per hour] [Light duty, up to 10 cycles per hour] <Insert classification>.

2. Operator Location:  [Top of hood] [Front of hood] [Wall] [Bench] [Through wall] [As shown on Drawings].

Retain one option in first subparagraph below or revise to suit Project.  The operating environment, including hazardous conditions, may require other motor types and enclosure modifications.

3. Motor Exposure:  [Interior] [Exterior, wet, and humid].

4. Emergency Manual Operation:  [Push-up] [Chain] [Crank] type.

"Pneumatic sensor" option in first subparagraph below may be limited to a width of 18 feet (5.5 m).  Verify availability with manufacturer.

5. Obstruction Detection Device:  Automatic [photoelectric sensor] [electric sensor edge on bottom bar] [pneumatic sensor edge on bottom bar] [; self-monitoring type].

Retain first subparagraph below if retaining either second or third option in last subparagraph above.

a. Sensor Edge Bulb Color:  [Black] [As selected by Architect from manufacturer's full range] <Insert color>.

6. Remote-Control Station:  [Interior] [Exterior] [Where shown on Drawings] <Insert location>.

7. Other Equipment:  [Audible and visual signals] [Radio-control system] <Insert device>.

P. Door Finish:

Retain one of first three subparagraphs below.  These include advertised materials and finishes; available materials and finishes vary with each manufacturer.  If retaining more than one, indicate location of each on Drawings or by inserts.

1. Baked-Enamel or Powder-Coated Finish:  [Color as indicated by manufacturer's designations] [Color matching Architect's sample] [Color as selected by Architect from manufacturer's full range] <Insert color and gloss>.

2. Factory Prime Finish:  Manufacturer's standard color.

Second option in first subparagraph below is standard; verify availability of other stainless-steel finishes with manufacturer.

3. Stainless-Steel Finish:  [No. 2B (bright, cold rolled)] [No. 4 (polished directional satin)] <Insert finish>.

Retain subparagraph below for insulated door curtains.

4. Interior Curtain-Slat Facing:  [Match finish of exterior curtain-slat face] <Insert finish>.

2.11 GENERAL FINISH REQUIREMENTS

A. Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

B. Appearance of Finished Work:  Noticeable variations in same piece are not acceptable.  Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

2.12 ALUMINUM FINISHES

Retain finishes in this article to suit Project.  If retaining more than one for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.  Revise finish designation if custom anodized finish is required and availability is verified.

A. Mill Finish:  Manufacturer's standard.

Retain one of two options in first paragraph below.  Class II finish is standard with many manufacturers; Class I finish is heavy anodized.  Verify availability with manufacturer.

B. Clear Anodic Finish:  AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

Retain one of two options in first paragraph below.  Verify availability with manufacturer.

C. Color Anodic Finish:  AAMA 611, [AA-M12C22A42/A44, Class I, 0.018 mm] [AA-M12C22A32/A34, Class II, 0.010 mm] or thicker.

Paragraph below references AAMA standard for pigmented organic coating on extrusions and panels.

D. Baked-Enamel or Powder-Coat Finish:  AAMA 2603.  Comply with coating manufacturer's written instructions for cleaning, conversion coating, application, and baking.

2.13 STEEL AND GALVANIZED-STEEL FINISHES

Retain one or both paragraphs below.  If retaining both paragraphs for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

A. Factory Prime Finish:  Manufacturer's standard primer, compatible with field-applied finish.  Comply with coating manufacturer's written instructions for cleaning, pretreatment, application, and minimum dry film thickness.

B. Baked-Enamel or Powder-Coat Finish:  Manufacturer's standard baked-on finish consisting of prime coat and thermosetting topcoat.  Comply with coating manufacturer's written instructions for cleaning, pretreatment, application, and minimum dry film thickness.

For exact finish, insert names of coating manufacturers and products.

2.14 STAINLESS-STEEL FINISHES

A. Surface Preparation:  Remove tool and die marks and stretch lines, or blend into finish.

Retain one or both paragraphs below.  Directional satin finish is the standard stainless-steel finish for all manufacturers.  Verify availability of other finishes with manufacturer.  If retaining more than one for different doors and to identify optional requirements for a single door, revise options and insert text as needed in door assembly articles retained in Part 2.

B. Polished Finishes:  Grind and polish surfaces to produce uniform finish, free of cross scratches.

Retain first subparagraph below for directional finishes.

1. Run grain of directional finishes with long dimension of each piece.

2. When polishing is completed, passivate and rinse surfaces.  Remove embedded foreign matter and leave surfaces chemically clean.

3. Directional Satin Finish:  No. 4.

Retain paragraph below for nondirectional finish.

C. Bright, Cold-Rolled, Unpolished Finish:  No. 2B.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates areas and conditions, with Installer present, for compliance with requirements for substrate construction and other conditions affecting performance of the Work.

B. Examine locations of electrical connections.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install overhead coiling doors and operating equipment complete with necessary hardware, anchors, inserts, hangers, and equipment supports; according to manufacturer's written instructions and as specified.

B. Install overhead coiling doors, hoods, and operators at the mounting locations indicated for each door.

C. Accessibility:  Install overhead coiling doors, switches, and controls along accessible routes in compliance with regulatory requirements for accessibility.

Retain paragraphs below if required.

D. Fire-Rated Doors:  Install according to NFPA 80.

E. Smoke-Control Doors:  Install according to NFPA 80 and NFPA 105.

3.3 STARTUP SERVICE

Retain this article if factory-authorized service representative is required.

A. Engage a factory-authorized service representative to perform startup service.

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Retain subparagraph below for fire-rated doors.  Verify whether testing is required by authorities having jurisdiction; revise accordingly.

3. Test door closing when activated by detector or alarm-connected fire-release system.  Reset door-closing mechanism after successful test.

3.4 ADJUSTING

A. Adjust hardware and moving parts to function smoothly so that doors operate easily, free of warp, twist, or distortion.

B. Lubricate bearings and sliding parts as recommended by manufacturer.

Retain paragraph below if weathertight installation or smoke-control doors are required.

C. Adjust seals to provide weathertight fit around entire perimeter.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain overhead coiling doors.

END OF SECTION 083323

	OVERHEAD COILING DOORS
	083323 - 1



