Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
05/04 (R 05/06)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 096900 - ACCESS FLOORING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Access flooring panels and understructure.

2. Floor panel coverings.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

If concrete sealer is specified in the Section listed in first subparagraph below and pedestal adhesive is specified in this Section, verify compatibility.

1. Division 03 Section "Cast-in-Place Concrete" for concrete floor sealer.

2. Division 09 Section "Tile Carpeting" for carpet tiles applied over access flooring panels.

3. Division 09 Section "Sheet Carpeting" for carpet applied over access flooring panels.

4. Division 23 Section "Testing, Adjusting, and Balancing for HVAC" for pressure testing of underfloor plenum.

5. Division 23 Section "Air Terminal Units" for variable-air-volume diffusers.

6. Division 26 Section "Grounding and Bonding for Electrical Systems" for connection to ground of access flooring understructure.

7. Division 26 Section "Cable Trays for Electrical Systems" for coordination with understructure.

8. Division 27 Section "Communications Horizontal Cabling for voice and data cabling for service outlets and for coordination with understructure pedestals.

Retain paragraph and subparagraphs below if quantity allowances are specified for cutouts and service outlets.  Provide details on Drawings, indicating differing cutout configurations, and coordinate with quantities listed in Division 01 Section "Allowances."

C. Quantity Allowances:  Provide the following as specified in Division 01 Section "Allowances."

1. Cutouts in floor panels.

2. Service outlets.

1.3 UNIT PRICES

Retain this Article if quantity of cutouts, service outlets, etc., is not known or is likely to change from either the actual number shown or the quantity specified under allowances.  Include provisions on the Bid Form and in Division 01 Section "Unit Prices" to cover these items and include information on Drawings, indicating size and location of cutouts.

A. Unit Prices:  The Contract Sum will be adjusted for changes in quantity from that indicated in allowances for [cutouts in floor panels] [and] [service outlets] based on amounts stipulated in the Form of Agreement and complying with Division 01 Section "Unit Prices." Changes to quantities and to the Contract Sum will be made by Change Order.

1.4 DEFINITION

Retain this Article if abbreviation in paragraph below remains after this Section has been edited.

A. ESD:  Electrostatic discharge.  The transfer of electric charge between bodies at different potentials.

1.5 SYSTEM DESCRIPTION

A. Access Flooring System:  Assemblies composed of modular floor panels on pedestals with or without stringers.

1.6 PERFORMANCE REQUIREMENTS

Loads are expressed in units of force, pounds-force (lbf) and newtons (N), unless otherwise indicated, and are examples only.  Retain or insert applicable loads to suit Project.  See Editing Instruction No. 2 in the Evaluations.  Verify that loading requirements coordinate with each other and match the products specified in Part 2.

A. Structural Performance:  Provide access flooring systems capable of withstanding the following loads and stresses within limits and under conditions indicated, as determined by testing manufacturer's current standard products according to referenced procedures in CISCA A/F, "Recommended Test Procedures for Access Floors":

Delete one of first two subparagraphs below.  Generally retain first subparagraph to measure top deflection of panels.  Bottom deflection is sometimes used as a criterion for unfilled, hollow steel panels where deformation of top surface may not be adequate to indicate actual structural performance.  Retain second subparagraph to measure bottom deflection.

1. Concentrated Loads:  Provide floor panels, including those with cutouts, capable of withstanding a concentrated design load of [1000 lbf (4448 N)] [1250 lbf (5560 N)] [1500 lbf (6672 N)] [2000 lbf (8896 N)] <Insert concentrated load>, with a top-surface deflection under load and a permanent set not to exceed, respectively, [0.10 and 0.010 inch (2.54 and 0.25 mm)] [0.080 inch and 0.010 inch (2.03 and 0.25 mm)] <Insert deflection and permanent set> according to CISCA A/F, Section I, "Concentrated Loads."

2. Concentrated Loads:  Provide floor panels, including those with cutouts, capable of withstanding a concentrated design load of [1000 lbf (4448 N)] [1250 lbf (5560 N)] [1500 lbf (6672 N)] [2000 lbf (8896 N)] <Insert concentrated load>, with a bottom-surface deflection under load and a permanent set not to exceed, respectively, [0.10 and 0.010 inch (2.54 and 0.25 mm)] [0.13 inch and 0.010 inch (3.30 and 0.25 mm)] <Insert deflection and permanent set>, measured below each applied-load location at horizontal surface of nearest composite beam according to CISCA A/F, Section I, "Concentrated Loads."

3. Ultimate Loads:  Provide access flooring systems capable of withstanding a minimum ultimate concentrated load of [2000 lbf (8896 N)] [2500 lbf (11 121 N)] [2600 lbf (11 565 N)] [3000 lbf (13 345 N)] [4000 lbf (17 793 N)] <Insert ultimate load>, without failing, according to CISCA A/F, Section II, "Ultimate Loading."

4. Rolling Loads:  Provide access flooring systems capable of withstanding rolling loads of the following magnitude, with a combination of local and overall deformation not to exceed 0.040 inch (1.02 mm) after exposure to rolling load over CISCA A/F Path A or B, whichever path produces the greatest top-surface deformation, according to CISCA A/F, Section III, "Rolling Loads."

Retain one or both subparagraphs below with subparagraph above.  CISCA A/F Wheel 1 load simulates heavy equipment move-in loads and is applied for 10 passes through a 3-inch (76-mm) diameter by 1-13/16-inch- (46-mm-) wide wheel similar to wheels found on moving dollies.  CISCA A/F Wheel 2 load simulates typical office loads and is applied for 10,000 passes through a 6-inch (152-mm) diameter by 1-13/16-inch- (46-mm-) wide wheel similar to wheels found on hand carts.

a. CISCA A/F Wheel 1 Rolling Load:  [600 lbf (2669 N)] [800 lbf (3559 N)] [1000 lbf (4448 N)] [1200 lbf (5338 N)] <Insert rolling load>.

b. CISCA A/F Wheel 2 Rolling Load:  [500 lbf (2224 N)] [600 lbf (2669 N)] [800 lbf (3559 N)] [1000 lbf (4448 N)] <Insert rolling load>.

Delete first subparagraph below if stringerless system is selected.

5. Stringer Load Testing:  Provide stringers, without panels in place, capable of withstanding a concentrated load of [75 lbf (334 N)] [225 lbf (1001 N)] [450 lbf (2002 N)] [850 lbf (3781 N)] <Insert stringer concentrated load> at center of span with a permanent set not to exceed 0.010 inch (0.25 mm), as determined per CISCA A/F, Section IV, "Stringer Load Testing."

6. Pedestal Axial Load Test:  Provide pedestal assemblies, without panels or other supports in place, capable of withstanding a [5000 lbf (22 240 N)] [6000 lbf (26 690 N)] <Insert axial load> axial load per pedestal, according to CISCA A/F, Section V, "Pedestal Axial Load Test."

Verify requirements for pedestal overturning moment in seismic zones with authorities having jurisdiction.  Coordinate with pedestals selected in Part 2 and method of attachment specified.

7. Pedestal Overturning Moment Test:  Provide pedestal assemblies, without panels or other supports in place, capable of withstanding an overturning moment per pedestal of [1000 lbf x inches (113 N x meters)] <Insert overturning moment>, according to CISCA A/F, Section VI, "Pedestal Overturning Moment Test."

Impact-load performance is reported by some manufacturers, but testing for impact-load performance is not included in CISCA A/F.

B. Floor Panel Impact-Load Performance:  Provide access flooring system capable of withstanding an impact load of [75 lb (34.0 kg)] [100 lb (45.5 kg)] [125 lb (56.7 kg)] [150 lb (68.0 kg)] [175 lbs (79.4 kg)] <Insert impact load> when dropped from 36 inches (914 mm) onto a 1-sq. in. (6.5-sq. cm) area located anywhere on panel, without failing.  Failure is defined as collapse of access flooring system.

Revise paragraph below to indicate specific loads determined by Project's structural engineer or refer to loads indicated on Drawings.  Model building codes and ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

C. Seismic Performance:  Provide access flooring system capable of withstanding the effects of seismic motions determined according to [ASCE 7, "Minimum Design Loads for Buildings and Other Structures":  Section 9, "Earthquake Loads."] <Insert applicable code requirement.>

Retain paragraph below for ESD-sensitive areas such as electronics manufacturing, computer, and explosive environments.  ESD floor coverings can add significant costs to access flooring systems and can limit styles and colors available.  See Evaluations for discussion of ESD-control systems and verify specific requirements with Owner.

D. ESD-Control Properties:  Provide floor coverings with ESD-control properties indicated as determined by testing identical products per test method indicated by an independent testing and inspecting agency.

Retain subparagraph and associated subparagraphs below for static-dissipative solid vinyl floor coverings.  Coordinate with products specified in Part 2 "Floor Panel Coverings" Article.

1. Static-Dissipative Floor Covering Properties:

Revise subparagraph and associated subparagraphs below to suit products selected.

a. Electrical Resistance:  Test per [ASTM F 150 with 100-V applied voltage] [ESD STM 7.1].

1) Average greater than 1 megohm and less than or equal to 1000 megohms when test specimens are tested surface to ground.

2) Average no less than 1 megohm and less than or equal to 1000 megohms when installed floor coverings are tested surface to ground.

Static-generation values reported by manufacturers may be limited by sensitivity of testing equipment used; consult manufacturers if static generation is critical.

b. Static Generation:  Less than [300] <Insert number> V when tested per AATCC-134 at 20 percent relative humidity with conductive footwear.

c. Static Decay:  5000 to 0 V in less than [0.25] <Insert number> seconds when tested per FED-STD-101C/4046.1.

Retain subparagraph and associated subparagraphs below for static-conductive solid vinyl or laminated floor coverings.  Coordinate with products specified in Part 2 "Floor Panel Coverings" Article.

2. Static-Conductive Floor Covering Properties:

Revise subparagraph and associated subparagraphs below to suit products selected.

a. Electrical Resistance:  Test per [ASTM F 150 with 500-V applied voltage] [ESD STM 7.1] [NFPA 99, Annex 2] [UL 779].

1) Average greater than 25,000 ohms and less than 1 megohm when test specimens and installed floor coverings are tested surface to surface (point to point).

2) Average no less than 25,000 ohms with no single measurement less than 10,000 ohms when installed floor coverings are tested surface to ground.

Static-generation values reported by manufacturers may be limited by sensitivity of testing equipment used; consult manufacturers if static generation is critical.

b. Static Generation:  Less than [100] <Insert number> V when tested per AATCC-134 at 20 percent relative humidity with conductive footwear.

c. Static Decay:  5000 to 0 V in less than [0.03] [0.01] <Insert number> seconds when tested per FED-STD-101C/4046.1.

Retain subparagraph and associated subparagraphs below for antistatic modular carpet tile floor coverings.  Coordinate with products specified in Part 2 "Floor Panel Coverings" Article.

3. Antistatic Floor Covering Properties:

Revise subparagraph and associated subparagraph below to suit products selected.

a. Electrical Resistance:  Test per ESD STM 7.1.

1) Average greater than 25,000 ohms and less than 1,000 megohm when test specimens and installed floor coverings are tested surface to surface (point to point).

Static-generation values reported by manufacturers may be limited by sensitivity of testing equipment used; consult manufacturers if static generation is critical.

b. Static Generation:  Less than [100] <Insert number> V when tested per AATCC-134 at 20 percent relative humidity with conductive footwear.

Resistance in subparagraph below represents maximum allowable to obtain electrical continuity for electrical-shock protection.  Revise if lower value is desired.

4. Panel-to-Understructure Resistance:  Not more than 10 ohms as measured without floor coverings.

1.7 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  Include layout of access flooring system and relationship to adjoining Work based on field-verified dimensions.

Edit or add to subparagraphs below to suit Project.

1. Details and sections with descriptive notes indicating materials, finishes, fasteners, typical and special edge conditions, accessories, and understructure.

Retain subparagraph below if products are required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify products' compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

2. For installed products indicated to comply with design loads, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

C. Samples for Initial Selection:  For each type of flooring material and exposed finish indicated.

Delete paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain first paragraph and subparagraphs below with or without above.

D. Samples for Verification:  For each type of flooring material and exposed finish indicated.

Edit subparagraphs below to suit types of floor coverings and items with an exposed finish.

1. Carpet:  Size equal to full-size floor panel.

2. Carpet Trim:  Size equal to length of one panel edge.

3. Solid Vinyl Tile:  Full-size units.

4. Plastic Laminate:  Size equal to full-size floor panel.

5. Resilient Accessories:  Manufacturer's standard accessories but not less than 12 inches (300 mm) in length.

6. Exposed Metal Accessories:  12 inches (300 mm) in length.

Delete subparagraph below if not required.

7. One complete full-size floor panel, pedestal, and understructure unit for each type of access flooring system required.

E. LEED Submittals:

Retain subparagraph below if pedestals are installed with adhesive and low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.1; coordinate with requirements selected in Part 2 for adhesive.

1. Product Data for Credit EQ 4.1:  For pedestal installation adhesive, including printed statement of VOC content.

Retain subparagraph below if access flooring panels are carpeted and low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.3; coordinate with requirements selected in Part 2 for carpet and adhesive.

2. Product Data for Credit EQ 4.3:  For carpet and installation adhesive, documentation indicating compliance with specified requirements.

Retain subparagraph below if steel-encapsulated, wood core panels are specified and low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.4.

3. Product Data for Credit EQ 4.4:  For particleboard used in steel-encapsulated, wood core panels, documentation indicating that particleboard contains no urea formaldehyde.

F. Product Certificates:  For each type of access flooring system, signed by product manufacturer.

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

G. Qualification Data:  For Installer.

H. Product Test Reports:  Based on evaluation of comprehensive tests performed by a qualified testing agency, or performed by access flooring manufacturer and witnessed by a qualified testing agency, for each type of flooring material and exposed finish.

1.8 QUALITY ASSURANCE

A. Installer Qualifications:  An employer of workers trained and approved by manufacturer.

B. Source Limitations:  Obtain access flooring system through one source from a single manufacturer.

Retain first paragraph below if compliance with NFPA 75, "Protection of Information Technology Equipment," is desired or if required by authorities having jurisdiction.

C. Regulatory Requirements:  Fabricate and install access flooring to comply with NFPA 75 requirements for raised flooring.

D. Provide floor panels that are clearly and permanently marked on their underside with panel type and concentrated-load rating.

Delete paragraph and subparagraphs below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.

E. Mockups:  Build mockups to verify selections made under sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution.

1. Build mockup of typical access flooring assembly as shown on Drawing.  Size to be an area no less than [five] <Insert number> floor panels in length by [five] <Insert number> floor panels in width.

Retain subparagraph below if mockups are erected as part of building rather than separately and the intention is to make an exception to the default requirement in Division 01 Section "Quality Requirements" for demolishing and removing mockups when directed, unless otherwise indicated.

2. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

Delete paragraph below if Work of this Section is not extensive or complex enough to justify a preinstallation conference.  If retaining, coordinate with Division 01.

F. Preinstallation Conference:  Conduct conference at Project site to comply with requirements in Division 01 Section "Project Management and Coordination."

Delete subparagraphs below if not required.  If retaining, revise to include Project-specific requirements.  Insert additional requirements to suit Project.

1. Review connection with mechanical and electrical systems.

2. Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

1.9 PROJECT CONDITIONS

Revise this Article to suit products selected.

A. Environmental Limitations:  Do not install access flooring until spaces are enclosed,[ subfloor has been sealed,] ambient temperature is between 40 and 90 deg F (4 and 32 deg C), and relative humidity is not more than 70 percent.

1.10 COORDINATION

A. Coordinate location of mechanical and electrical work in underfloor cavity to prevent interference with access flooring pedestals.

B. Mark pedestal locations on subfloor by use of a grid[, with a module equal to width of five floor panels in both directions,] to enable mechanical and electrical work to proceed without interfering with access flooring pedestals.

C. Proceed with installation only after completion of other construction within affected spaces.

1.11 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described in subparagraphs below that match products installed and that are packaged with protective coverings for storage and identified with labels describing contents.

1. Flooring Panels:  <Insert number.>

2. Pedestals:  <Insert number.>

3. Stringers:  <Insert number.>

PART 2 -  PRODUCTS

2.1 FLOOR PANELS AND UNDERSTRUCTURE

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and lists of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Steel-Encapsulated, Wood-Core Panel Systems:

a. ASM Modular Floors Inc.

b. Computer Environments Inc.

c. InterfaceAR.

d. Maxcess Technologies, Inc.

e. <Insert manufacturer's name.>

2. Formed-Steel Panel Systems:

a. AMICO-Genesis; Alabama Metal Industries Corporation.

b. ASM Modular Floors Inc.

c. Computer Environments Inc.

d. InterfaceAR.

e. Maxcess Technologies, Inc.

f. Tate Access Floors, Inc.

g. <Insert manufacturer's name.>

3. Cementitious-Filled, Formed-Steel Panel Systems:

a. ASM Modular Floors Inc.

b. Computer Environments Inc.

c. InterfaceAR.

d. Maxcess Technologies, Inc.

e. Tate Access Floors, Inc.

f. <Insert manufacturer's name.>

4. Die-Cast Aluminum Panel Systems:

a. Computer Environments Inc.

b. Maxcess Technologies, Inc.

c. Tate Access Floors, Inc.

d. <Insert manufacturer's name.>

5. Concrete-Filled, Steel-Pan Panel Systems:

a. InterfaceAR.

b. <Insert manufacturer's name.>

D. Floor Panels, General:  Provide modular panels complying with the following requirements that one person, using a portable lifting device, can interchange with other field panels without disturbing adjacent panels or understructure:

Retain one of first two subparagraphs below.  Retain first subparagraph for products manufactured to IP sizes; retain second for products manufactured to metric sizes.  Sizes indicated are standard for industry.  Other standard and special sizes are available from some manufacturers.

1. Nominal Panel Size:  24 by 24 inches (610 by 610 mm).

2. Nominal Panel Size:  600 by 600 mm.

3. Fabrication Tolerances:  Fabricate panels to the following tolerances with squareness tolerances expressed as the difference between diagonal measurements from corner to corner:

Revise tolerances in two subparagraphs below to suit products selected.

a. Size and Squareness:  Plus or minus 0.015 inch (0.38 mm) of required size, with a squareness tolerance of plus or minus 0.015 inch (0.38 mm), unless tolerances are otherwise indicated for a specific panel type.

b. Flatness:  Plus or minus 0.020 inch (0.50 mm), measured on a diagonal on top of panel.

Retain one of two subparagraphs below.  Retain second subparagraph only for pedestal heads designed for bolted attachment.

4. Panel Attachment to Understructure:  By gravity.

5. Panel Attachment to Understructure:  By bolting to pedestal head.  Provide panels with holes drilled in corners to align precisely with threaded holes in pedestal heads and to accept countersunk screws with heads flush with top of panel.

Delete subparagraph below if not required or available from manufacturers selected.

a. Provide fasteners held captive to panels.

Select type of panel construction required from first five paragraphs and associated subparagraphs below.  See Editing Instruction No. 3 in the Evaluations.  If more than one type is required, indicate location of each on Drawings or by inserts and coordinate with other components that apply to each panel type.

If retaining first paragraph below and low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.4, retain option after verifying availability of panels that comply with requirement.

E. Steel-Encapsulated, Wood-Core Panels:  Fabricated with 1-inch- (25-mm-) thick, particleboard core[, made without urea formaldehyde] laminated to top and bottom steel face sheets, with metal surfaces protected against corrosion by manufacturer's standard factory-applied finish, and with a flame-spread index of 25 or less per ASTM E 84.  Provide core edges enclosed with upturned, die-formed edge of bottom sheet or with perimeter steel channel welded to top sheet and welded or bonded to bottom sheet.

F. Formed-Steel Panels:  Fabricated with die-cut flat top sheet and die-formed and stiffened steel bottom pan formed from cold-rolled steel sheet and joined together by resistance welding, with metal surfaces protected against corrosion by manufacturer's standard factory-applied finish to produce units of the following type:

1. Solid Panels:  Flat, solid top surface.

Delete one or both subparagraphs and associated subparagraphs below if not required.  Perforated panels and grates are used for delivering large amounts of air to heavy equipment rooms such as telecommunication switch centers, but not for normal office ventilation.  Perforated panels and grates typically are not rated for same rolling-load performance as solid panels.

2. Perforated Panels:  Perforated top surface with [holes] [slots] of number, spacing, and size standard with manufacturer to produce a nominal open area of [25 percent] <Insert area>.[  Provide mechanical dampers with each panel unit.]

a. Quantity:  [As shown on Drawings] <Insert number>.

b. Finish:  [Manufacturer's standard] [To match solid panels] <Insert finish>.

3. Grates:  Grating ribs arranged in manufacturer's standard pattern to produce a nominal open area of [56 percent] <Insert area>.[  Provide mechanical dampers with each panel unit.]

a. Quantity:  [As shown on Drawings] <Insert number>.

b. Finish:  [Manufacturer's standard] [To match solid panels] <Insert finish>.

G. Cementitious-Filled, Formed-Steel Panels:  Fabricated with die-cut flat top sheet and die-formed and stiffened bottom pan formed from cold-rolled steel sheet joined together by resistance welding to form an enclosed assembly, with metal surfaces protected against corrosion by manufacturer's standard factory-applied finish.  Fully grout internal spaces of completed units with manufacturer's standard cementitious fill.

Retain paragraph and subparagraphs below for aluminum panels.  Aluminum panels and underfloor structures are used in MRI facilities, because of their nonmagnetic qualities, and in computer and clean rooms.  If an aluminum understructure is required, verify that pedestals and stringers are also aluminum.

H. Die-Cast Aluminum Panels:  Fabricated from manufacturer's standard aluminum alloy but not less than the strength and corrosion resistance of Alloy UNS No. A03830 or UNS No. A03840 per ASTM B 85, to produce units of the following type and with the following finish:

1. Solid Panels:  Flat, solid surface on top and symmetrical crossing ribs on bottom; edge machined after casting to specified tolerances.

Delete one or both subparagraphs and associated subparagraphs below if not required.  Perforated panels and grates are used for delivering large amounts of air to heavy equipment rooms such as telecommunication switch centers, but not for normal office ventilation.  Perforated panels and grates typically are not rated for same rolling-load performance as solid panels.

2. Perforated Panels:  Perforated top surface with [holes] [slots] of number, spacing, and size standard with manufacturer to produce a nominal open area of [25 percent] <Insert area>.[  Provide mechanical dampers with each panel unit.]

a. Quantity:  [As shown on Drawings] <Insert number>.

b. Finish:  [Manufacturer's standard] [To match solid panels] <Insert finish>.

3. Grates:  Grating ribs arranged in manufacturer's standard pattern to produce a nominal open area of [56 percent] <Insert area>.[  Provide mechanical dampers with each panel unit.]

a. Quantity:  [As shown on Drawings] <Insert number>.

b. Finish:  [Manufacturer's standard] [To match solid panels] <Insert finish>.

Retain one of two subparagraphs below or revise for other finishes.

4. Epoxy Finish:  [Conductive ]epoxy powder coating with a minimum average thickness of 2.5 mils (0.064 mm) and in color selected from manufacturer's full range.

5. Plated Finish:  Nickel-chrome electrodeposited plating, 0.000005-inch (0.000127-mm) chrome over 0.0008-inch (0.02-mm) nickel, without copper or brass strike, to produce complete coverage over significant surfaces with a matte metallic appearance.

Paragraph below describes panels with exposed concrete top surfaces and restricts selection to InterfaceAR's "TecCrete XL" panels.

I. Concrete-Filled, Steel Pan Panels:  Fabricated with bottom pan die-formed from electrolytic-zinc-coated steel sheet and filled with lightweight concrete that is reinforced and bonded to pan by shear ties.

Pedestals are typically made of steel; retain second option in paragraph below if using aluminum panels.

J. Pedestals:  Assembly consisting of base, column with provisions for height adjustment, and head (cap); made of [steel] [aluminum].

Delete subparagraph below if seismic pedestals are not required.

1. Provide pedestals designed for use in seismic applications.

Retain option in first subparagraph below for standard base.  Insert area for larger bases if needed to meet seismic requirements.  Verify requirements with structural engineer.

2. Base:  Square or circular base with not less than [16 sq. in. (103 sq. cm)] <Insert area> of bearing area.

3. Column:  Of height required to bring finished floor to elevations indicated.  Weld to base plate.

4. Provide vibration-proof leveling mechanism for making and holding fine adjustments in height over a range of not less than [2 inches (51 mm)] <Insert leveling range> and for locking at a selected height, so deliberate action is required to change height setting and vibratory displacement is prevented.

5. Head:  Designed to support understructure system indicated.

Pads or gaskets specified in subparagraph below are not used with bolted-panel systems and may be optional with nonbolted-panel systems.  Verify requirements with manufacturers selected.

a. Provide sound-deadening pads or gaskets at contact points between heads and panels.

Retain subparagraph below for bolted floor panels.

b. Provide head with four holes aligned with holes in floor panels for bolting of panels to pedestals.

Delete paragraph and subparagraphs below for stringerless installation.  See Evaluations.  Stringers are typically made of steel; retain second option below if using aluminum panels.

K. Stringer Systems:  Modular [steel] [aluminum] stringer systems made to interlock with pedestal heads and form a grid pattern placing stringers under each edge of each floor panel and a pedestal under each corner of each floor panel.  Protect steel components with manufacturer's standard galvanized or corrosion-resistant paint finish.

Retain one of two subparagraphs below.

1. Bolted Stringers:  System of main and cross stringers connected to pedestals with threaded fasteners accessible from above.

2. Snap-on Stringers:  System of stringers attached to pedestals with nonbolted interlocking connections to provide a stable understructure and to prevent accidental disengagement.

Both subparagraphs below apply to either type of stringer system but are not standard for all systems and manufacturers.  If retaining, coordinate with manufacturer's product data and list of manufacturers.

Subparagraph below may not be required where panel edge trim provides effective seal or where stringers are nested between panels.

3. Provide continuous gasket at contact surfaces between panel and stringers to deaden sound, to seal off underfloor cavity from above, and to maintain panel alignment and position.

Delete subparagraph below if not applicable.  Some understructure systems only provide lateral bracing with panels supported directly on pedestals.  Refer to manufacturer's literature.

4. Provide stringers that support each edge of each panel where required to meet design-load criteria.

2.2 FLOOR PANEL COVERINGS

Retain first paragraph below and delete remainder of Article if panels are to remain bare or if carpet tiles or other floor coverings are specified in a Division 09 Section and are to be field applied.  See Evaluations for discussion of floor coverings.

A. Provide bare panels without factory-applied floor coverings on traffic surfaces.

B. General:  Provide factory-applied floor coverings of type indicated that are laminated by access flooring manufacturer to tops of floor panels[ including perforated panels].

Retain one of three options in paragraph below.  If retaining first option, indicate colors, textures, and patterns in a separate schedule.  Choices of colors, textures, and patterns may be limited if ESD-control floor coverings are used; verify selections with manufacturer.

C. Colors, Textures, and Patterns:  [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range] <Insert colors, textures, and patterns>.

Select type(s) of floor panel coverings from first six paragraphs and associated subparagraphs below or revise to suit Project.  If retaining more than one, indicate location of each in finish schedule.

Select first option in paragraph below for 0.118-inch (3-mm) thickness.  Select second option for 0.059-inch (1.5-mm) thickness.

D. Standard Plastic Laminate:  NEMA LD 3, High-Wear type, Grade [HWH] [HDS]; fabricated in one piece to cover each panel face [within perimeter plastic] [with integral trim serving as] edging.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Formica Corporation.

b. Nevamar Company, LLC.

c. <Insert manufacturer's name.>

Select first option in paragraph below for 0.118-inch (3-mm) thickness.  Select second option for 0.059-inch (1.5-mm) thickness.

E. Static-Conductive Plastic Laminate:  NEMA LD 3, High-Wear type, Grade [CHWH] [CHDS], fabricated in one piece to cover each panel face within perimeter plastic edging or with integral trim serving as edging.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Nevamar Company, LLC.

b. <Insert manufacturer's name.>

Select first option in paragraph below for Flexco's "Conductive Tile" or VPI's "Conductile." Select second option for Flexco's "Dissipative Tile" or VPI's "Statmate."

F. Solid Vinyl Tile:  Static-[Conductive] [Dissipative], ASTM F 1700, Class I (Monolithic Vinyl Tile), Type A (Smooth Surface), fabricated in one piece to cover panel face within plastic edging.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Flexco, Inc.

b. VPI, LLC; Floor Products Division.

c. <Insert manufacturer's name.>

Low-emissivity tiles are used in clean-room and sensitive-electronic-fabrication facilities.  Select first or second option, along with either the third or fourth option, in first paragraph below.  Select third option for VPI's "Conductile LE" series; select fourth option for VPI's "Conductile XLE" series.  "XLE" series has lower emissivity than "LE" series.  Verify emissivity requirements with Owner.

G. Low-Emissivity, Solid Vinyl Tile:  Static-[Conductive] [Dissipative], ASTM F 1700, Class I (Monolithic Vinyl Tile), Type A (Smooth Surface), with [minimum 50 percent reduction in outgasing] [total mass loss of 1 percent and minimum 98 percent reduction in collected volatile condensable materials] compared to products with dioctyl phthalate as determined by testing per ASTM E 595.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. VPI, LLC; Floor Products Division.

b. <Insert manufacturer's name.>

H. Standard Commercial Carpet:  Die cut and adhesively bonded to top surface of panel.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation>or a comparable product by one of the following:

a. Beaulieu Group LLC.

b. <Insert manufacturer's name.>

4. Provide factory-applied carpet with the following characteristics:

Carpet characteristics in nine subparagraphs below are based on Beaulieu's "Corona" and are examples only.

a. Style:  [Passport] <Insert style>.

b. Fiber Type:  [100% BCF nylon] <Insert fiber>.

c. Pile Characteristics:  [Level loop] <Insert characteristics>.

d. Pile Thickness:  [0.130 inch (3.30 mm)] <Insert thickness>.

e. Stitches:  [10.0/inch (10.0/2.54 cm)] <Insert quantity>.

f. Surface Pile Weight:  [26 oz./sq. yd. (881 g/sq. m)] <Insert weight>.

g. Total Weight:  [56 oz./sq. yd. (1899 g/sq. m)] <Insert weight>.

h. Backing:  [Woven polypropylene] <Insert backing>.

i. Critical Radiant Flux Rating:  Minimum of 0.45 W/sq. cm per ASTM E 648.

Retain subparagraph below if low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.3.

5. Environmental Requirements:  Provide carpet that complies with testing and product requirements of Carpet and Rug Institute's "Green Label Plus" program.  Bond carpet to panels with adhesives with VOC content not more than 50g/L when calculated according to 40 CFR 59, Subpart D (EPA method 24).

I. Antistatic Carpet:  Antistatic modular carpet tile [bonded with conductive adhesive to] [with buttons that engage into positioning holes in] top surface of panel.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Julie Industries.

b. Shaw; a Berkshire Hathaway Company.

c. <Insert manufacturer's name.>

4. Provide carpet with the following characteristics:

Carpet characteristics in nine subparagraphs below are based on Julie Industries' "StaticSmart ESD Carpet Tile" and are examples only.

a. Style:  [Classic] [Contempo] <Insert style>.

First option in first two subparagraphs below applies to Classic style; second option applies to Contempo style.

b. Fiber Type:  [Solutia LXI nylon] [Performa SD Type 6 nylon] <Insert fiber>

c. Pile Characteristics:  [Textured loop] [Textured graphic loop] <Insert characteristics>.

d. Pile Thickness:  [0.125 and 0.188 inch (3.18 and 4.78 mm)] <Insert thickness>.

First option in first subparagraph below applies to Classic style; second option applies to Contempo style.

e. Stitches:  [11.0/inch (11.0/2.54 cm)] [10.0/inch (10.0/ 2.54 cm)] <Insert quantity>.

f. Surface Pile Weight:  [24 oz./sq. yd. (814 g/sq. m)] <Insert weight>.

g. Total Weight:  [148 oz./sq. yd. (5018 g/sq. m)] <Insert weight>.

h. Backing:  [Static-dissipative, unitary PVC backing with conductive additive] <Insert backing>.

i. Critical Radiant Flux Rating:  Minimum of 0.45 W/sq. cm per ASTM E 648.

Retain subparagraph below if low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.3.

5. Environmental Requirements:  Provide carpet that complies with testing and product requirements of Carpet and Rug Institute's "Green Label Plus" program.[  Bond carpet to panels with adhesives with VOC content not more than 50g/L when calculated according to 40 CFR 59, Subpart D (EPA method 24).]

Retain paragraph below for solid vinyl tile and plastic laminate.  Select first option for solid vinyl tile and second option for plastic laminate.  Edging is optional if specifying carpet.  Method of attaching edging differs with manufacturers and types of panel.  Revise if specific method is required; delete for noncomplying manufacturers.

J. Edging:  Manufacturer's standard [applied] [integral] edge trim.  Provide size and profile of applied edge trim that fits floor coverings selected.

Delete or revise paragraph below to suit Project.  Delete for projects where floor coverings and resilient wall base are specified in another Section or are not in the Contract.

K. Resilient Wall Base:  ASTM F 1861, Type [TS (rubber, vulcanized thermoset)] [TV (vinyl, thermoplastic)], Group 1 (solid), Style B (cove), [0.080 inch (2.03 mm)] [0.125 inch (3.18 mm)] thick and [2-1/2 inches (63.5 mm)] [4 inches (102 mm)] [6 inches (152 mm)] high[, with matching end stops and factory-made corner units].

2.3 ACCESSORIES

Retain one of first two paragraphs below.  Coordinate with Part 3 "Installation" Article.

A. Adhesives:  Manufacturer's standard adhesive for bonding pedestal bases to subfloor.

Retain subparagraph below if low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.1.  VOC limit is that for multipurpose construction adhesives.

1. Provide adhesive with a VOC content of 70 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain first paragraph below for seismic installations.  Verify expansion anchor requirements with structural engineer and, if necessary, insert more detailed requirements for type and depth of anchors.  Revise zinc-plating thickness to suit Project's service conditions but only after verifying availability.

B. Post-Installed Anchors:  For anchoring pedestal bases to subfloor, provide [2] [4] post-installed [expansion anchors] [threaded concrete screws] made from carbon-steel components, zinc plated to comply with ASTM B 633, Class Fe/Zn 5 (5 microns) for Class SC 1 service condition (mild), with the capability to sustain, without failure, a load equal to [1.5] <Insert number> times the loads imposed by pedestal overturning moment on fasteners, as determined by testing per ASTM E 488, conducted by a qualified independent testing agency.

C. Cutouts:  Provide cutouts in floor panels for cable penetrations and service outlets.  Provide reinforcement or additional support, if needed, to make panels with cutouts comply with standard performance requirements.

1. Number, Size, Shape, and Location:  [As indicated.] [As specified in Division 01 Sections "Allowances" and "Unit Prices."]

Delete one of two subparagraphs below.

2. Trim edge of cutouts with manufacturer's standard plastic molding.

3. Fit cutouts with manufacturer's standard grommets in sizes indicated or, if size of cutouts exceeds maximum grommet size available, trim edge of cutouts with manufacturer's standard plastic molding having tapered top flange.[  Furnish removable covers for grommets.]

Retain subparagraph below if underfloor cavity is used for air distribution.

4. Provide foam-rubber pads for sealing annular space formed in cutouts by cables.

Delete paragraph and subparagraphs below if no service outlets.  Service-outlet designs differ among manufacturers; revise to suit Project.

D. Service Outlets:  Standard UL-listed and -labeled assemblies, for recessed mounting flush with top of floor panels, for power, communication, and signal services, and complying with the following requirements:

1. Structural Performance:  Cover capable of supporting a 1000-lbf (4448-N) concentrated load.

Retain one of first two subparagraphs below, which broadly describe products available from most manufacturers.

2. Cover and Box Type:  Hinged polycarbonate cover with opening for passage of cables when cover is closed and including frame and steel box or formed-steel plate for mounting electrical receptacles.

3. Cover and Box Type:  Grommet with twist-close cover and including steel junction box for electrical receptacle with provision for telephone Amphenol connectors and signal cables.

4. Location:  In center of panel quadrant, unless otherwise indicated.

Delete one of two subparagraphs and associated subparagraphs below.  Coordinate with electrical distribution system requirements and revise to suit Project.

5. Receptacles and Wiring:  Electrical receptacles and wiring for service outlets are specified in Division 26 Sections.

6. Receptacles and Wiring:  Equip each service outlet with power receptacles to comply with the following requirements:

a. Type of Receptacle:  Heavy-duty duplex, 2-pole, 3-wire grounding, 20 A, 125 V, NEMA WD 6, Configuration 5-20R, unless otherwise indicated.

b. Number of Receptacles for Outlet:  [One] [Two] [Four].

Retain one of two subparagraphs below.

c. Wiring Method:  Factory wired for hard wiring in field with armored cable, containing 3 insulated No. 12 AWG solid-copper conductors, terminated with a [6-inch- (152-mm-)] <Insert length> long pigtail.

d. Wiring Method:  Power-in connectors, built into outlet housing, of type to fit power-in and power-out connectors of branch-circuit cables supplied with building electrical system.

Delete or revise first paragraph and subparagraphs below if automatically controlled, variable-air-volume diffusers such as York's "Modular Integrated Terminals" are included as part of an integrated, underfloor air delivery system.

E. Diffusers:  Manufacturer's standard round diffusers, [4 inches (102 mm)] [8 inches (203 mm)] in diameter, formed from [aluminum] [polycarbonate plastic] to produce a removable 1-piece unit complete with diffuser, manually adjustable flow regulator, dirt and dust receptacle, trim ring, and underfloor compression mounting ring; precisely fitted in factory-prepared openings of standard field panels, and complying with the following requirements:

Subparagraphs below are examples only.  Revise to suit products selected.

1. Air-Distribution Characteristics:  [100 cfm (47 L/s)] <Insert value> at [0.096-inch (24-Pa)] <Insert value> static pressure and a maximum noise criterion rating of [15] <Insert value>.

2. Structural Performance:  Capable of supporting a [600-lbf (2669-N)] <Insert value> concentrated load.

3. Fire-Test-Response Characteristics:  Classified 94V-0 per UL 94.

F. Floor Grilles:  Standard load-bearing grilles formed from [aluminum] [polycarbonate plastic] to produce removable one-piece unit precisely fitted in factory-prepared openings of standard field panels, [with adjustable/removable] [without] dampers and complying with the following requirements:

Subparagraphs below are examples only.  Revise to suit products selected.

1. Air-Distribution Characteristics:  468 cfm at 0.10-inch wg (221 L/s at 25-Pa) static pressure.

2. Structural Performance:  Capable of supporting a 1000-lbf (4448-N) concentrated load.

3. Fire-Test-Response Characteristics:  Classified 94V-0 per UL 94.

Delete paragraph below if not required.  Cavity dividers are used for air control, acoustic privacy, and security.

G. Cavity Dividers:  Provide manufacturer's standard metal dividers located where indicated to divide underfloor cavities.

Delete four paragraphs and associated subparagraph below if subfloor beneath access flooring is depressed so access flooring is at same level as adjacent flooring.

H. Vertical Closures (Fasciae):  Where underfloor cavity is not enclosed by abutting walls or other construction, provide metal-closure plates with [manufacturer's standard] <Insert finish> finish.

I. Ramps:  Manufacturer's standard ramp construction of width and slope indicated but not steeper than 1:12, with raised-disc or textured rubber or vinyl floor coverings, and of same materials, performance, and construction requirements as access flooring.

J. Steps:  Provide steps of size and arrangement indicated with floor coverings to match access flooring.  Apply nonslip aluminum nosings to treads, unless otherwise indicated.

K. Railings:  Standard extruded-aluminum railings, at ramps and open-sided perimeter of access flooring where indicated.  Include handrail, intermediate rails, posts, brackets, end caps, wall returns, wall and floor flanges, plates, and anchorages where required.

Retain subparagraph below if performance requirements are included in Project's Specifications, or delete subparagraph and insert performance requirements here.

1. Provide railings that comply with structural performance requirements specified in Division 05 Section "[Pipe and Tube Railings] [Decorative Metal Railings]."

For computer rooms to comply with NFPA 75, item in paragraph below must be located and well marked within computer room.

L. Panel Lifting Device:  Manufacturer's standard portable lifting device of type required for specified panels.  Provide one lifting devices per room of each type required.

Pedestals are generally used for perimeter support.  If special extrusion or other means are required, show details on Drawings and revise paragraph below accordingly.

M. Perimeter Support:  Where indicated, provide manufacturer's standard method for supporting panel edge and forming transition between access flooring and adjoining floor coverings at same level as access flooring.

PART 3 -  EXECUTION

3.1 EXAMINATION

Coordinate requirements specified in other Sections for subfloor construction and tolerances to ensure that they are appropriate for pedestal installation.

A. Examine substrates, with Installer and manufacturer's representative present, for compliance with requirements for installation tolerances and other conditions affecting performance of work.

1. Verify that substrates comply with tolerances and other requirements specified in other Sections and that substrates are free of cracks, ridges, depressions, scale, foreign deposits, and debris that might interfere with [adhesive] [post-installed anchor] attachment of pedestals.

2. Proceed with installation only after unsatisfactory conditions have been corrected.

Delete paragraph and subparagraphs below if pedestals are not adhesively attached to substrate or if field testing is not required.  Preinstallation adhesive field test can add time and expense to access flooring installation.  For projects where overturning moment is critical, consider post-installed anchor attachment, rather than adhesive attachment, of pedestals.

B. Preinstallation Adhesive Field Test:  Before installing pedestals, field test their adhesion to subfloor surfaces as follows:

1. In areas representative of each subfloor surface, set typical pedestal assemblies in same adhesive and methods required for completed work.

If construction schedule allows, extend period in first subparagraph below to 45 days.

2. Allow test installation to cure for 30 days, with a pressure of 25 lbf (111 N) applied vertically to pedestals during this period.

3. After curing, apply lateral load against a straight steel bar inserted 2 inches (51 mm) into pedestal stems.  Measure the force needed to cause adhesive failure of pedestal base.

4. Proceed with installation only after tests show compliance with performance requirement specified for pedestals' capability to resist overturning moment.

3.2 PREPARATION

A. Lay out floor panel installation to keep the number of cut panels at floor perimeter to a minimum.  Avoid using panels cut to less than 6 inches (152 mm).

B. Locate each pedestal, complete any necessary subfloor preparation, and vacuum clean subfloor to remove dust, dirt, and construction debris before beginning installation.

3.3 INSTALLATION

A. Install access flooring system and accessories under supervision of access flooring manufacturer's authorized representative to produce a rigid, firm installation that complies with performance requirements and is free of instability, rocking, rattles, and squeaks.

Delete one of first two paragraphs below.  Retain first paragraph for more common adhesive attachment of pedestals.  Retain second paragraph if bolted attachment of pedestal bases is required for seismic applications or where increased rigidity is desired.  Coordinate with Part 2 "Accessories" Article.

B. Set pedestals in adhesive as recommended in writing by access flooring manufacturer to provide full bearing of pedestal base on subfloor.

C. Attach pedestals to subfloor by post-installed mechanical anchors.

D. Adjust pedestals to permit top of installed panels to be set flat, level, and to proper height.

Delete first paragraph below for stringlerless systems.

E. Secure stringers to pedestal heads according to access flooring manufacturer's written instructions.

F. Install flooring panels securely in place, properly seated with panel edges flush.  Do not force panels into place.

Retain subparagraph below for panels with factory-applied carpet.

1. Carpeted Panels:  Install panels with carpet pile in same direction.

G. Scribe perimeter panels to provide a close fit with adjoining construction with no voids greater than 1/8 inch (3 mm) where panels abut vertical surfaces.

Delete subparagraph below if not required.

1. To prevent dusting, seal cut edges of steel-encapsulated, wood-core panels with sealer recommended in writing by panel manufacturer.

H. Cut and trim access flooring and perform other dirt-or-debris-producing activities at a remote location or as required to prevent contamination of subfloor under access flooring already installed.

Delete paragraph below if no electrical-resistance requirements for floor coverings.

I. Ground flooring system as recommended by manufacturer and as needed to comply with performance requirements for electrical resistance of floor coverings.

Delete first paragraph below if no underfloor-cavity dividers.

J. Scribe and install underfloor-cavity dividers to closely fit against subfloor surfaces, and seal with mastic.

K. Scribe vertical closures to closely fit against subfloor and adjacent finished-floor surfaces.  Set in mastic and seal to maintain plenum effect within underfloor cavity.

L. Clean dust, dirt, and construction debris caused by floor installation, and vacuum subfloor area, as installation of floor panels proceeds.

Retain first paragraph below for projects using underfloor air delivery systems.

M. Seal underfloor air cavities at construction seams, penetrations, and perimeter to control air leakage as recommended in writing by manufacturer.

N. Install access flooring without change in elevation between adjacent panels and within the following tolerances:

1. Plus or minus [1/16 inch (1.5 mm)] [1/8 inch (3 mm)] <Insert dimension> in any 10-foot (3-m) distance.

2. Plus or minus [1/8 inch (3 mm)] [1/4 inch (6.5 mm)] <Insert dimension> from a level plane over entire access flooring area.

3.4 ADJUSTING, CLEANING, AND PROTECTION

Delete first paragraph below if pedestals are mechanically attached to substrate.

A. Prohibit traffic on access flooring for 24 hours and removal of floor panels for [72] <Insert number> hours after installation to allow pedestal adhesive to set.

B. After completing installation, vacuum clean access flooring and cover with continuous sheets of reinforced paper or plastic.  Maintain protective covering until time of Substantial Completion.

C. Replace access flooring panels that are stained, scratched, or otherwise damaged or that do not comply with specified requirements.

END OF SECTION 096900

ACCESS FLOORING
096900 - 1

