Copyright 2005 AIA
MASTERSPEC Full Length
03/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220519 - METERS AND GAGES FOR PLUMBING PIPING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Thermometers.

2. Gages.

3. Test plugs.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 22 Section "Facility Water Distribution Piping" for domestic and fire-protection water service meters outside the building.

2. Division 22 Section "Domestic Water Piping" for domestic and fire-protection water service meters inside the building.

3. Division 23 Section "Facility Natural-Gas Piping" for gas meters.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. CR:  Chlorosulfonated polyethylene synthetic rubber.

B. EPDM:  Ethylene-propylene-diene terpolymer rubber.

1.4 SUBMITTALS

First two paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated; include performance curves.

B. Shop Drawings:  Schedule for [thermometers] [and] [gages] indicating manufacturer's number, scale range, and location for each.

Paragraph below is defined in Division 01 Section "Submittal Procedures" as "Informational Submittal."  Retain for material or product certificates from manufacturers.

C. Product Certificates:  For each type of [thermometer] [and] [gage], signed by product manufacturer.

PART 2 -  PRODUCTS

2.1 METAL-CASE, LIQUID-IN-GLASS THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Palmer - Wahl Instruments Inc.

2. Trerice, H. O. Co.

3. Weiss Instruments, Inc.

4. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

5. <Insert manufacturer's name.>

C. Case:  [Die-cast aluminum] [Die-cast aluminum or brass] [Brass] [Chrome-plated brass], [7 inches (178 mm)] [9 inches (229 mm)] <Insert other> long.

D. Tube:  Red or blue reading, [mercury] [mercury or organic-liquid] [organic-liquid] filled, with magnifying lens.

E. Tube Background:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

F. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

G. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, straight type] [Rigid, angle type].

H. Stem:  Copper-plated steel, aluminum, or brass for thermowell installation and of length to suit installation.

I. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.2 PLASTIC-CASE, LIQUID-IN-GLASS THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ernst Gage Co.

2. Eugene Ernst Products Co.

3. Marsh Bellofram.

4. Miljoco Corp.

5. Trerice, H. O. Co.

6. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

7. Winters Instruments.

8. <Insert manufacturer's name.>

C. Case:  Plastic, [7 inches (178 mm)] [9 inches (229 mm)] <Insert other> long.

D. Tube:  Red or blue reading, mercury or organic-liquid filled, with magnifying lens.

E. Tube Background:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

F. Window:  Glass or plastic.

G. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, straight type] [Rigid, angle type].

H. Stem:  Metal, for thermowell installation and of length to suit installation.

I. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.3 DIRECT-MOUNTING, VAPOR-ACTUATED DIAL THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

2. KOBOLD Instruments, Inc.

3. Marsh Bellofram.

4. Trerice, H. O. Co.

5. Weiss Instruments, Inc.

6. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

7. <Insert manufacturer's name.>

C. Case:  [Dry] [Liquid-filled] type, [drawn steel or cast aluminum] [metal or plastic] [plastic], [4-1/2-inch (114-mm)] [5-inch (127-mm)] [6-inch (152-mm)] <Insert other> diameter.

D. Element:  Bourdon tube or other type of pressure element.

E. Movement:  Mechanical, connecting element and pointer.

F. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

G. Pointer:  Red[ or other dark-color] metal.

H. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

I. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

J. Connector:  [Adjustable type, 180 degrees in vertical plane, 360 degrees in horizontal plane, with locking device] [Rigid, bottom type] [Rigid, back type].

K. Thermal System:  Liquid- or mercury-filled bulb in copper-plated steel, aluminum, or brass stem for thermowell installation and of length to suit installation.

L. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.4 REMOTE-MOUNTING, VAPOR-ACTUATED DIAL THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Marsh Bellofram.

4. Miljoco Corp.

5. Palmer - Wahl Instruments Inc.

6. REO TEMP Instrument Corporation.

7. Tel-Tru Manufacturing Company.

8. Trerice, H. O. Co.

9. Weiss Instruments, Inc.

10. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

11. Winters Instruments.

12. <Insert manufacturer's name.>

C. Case:  Dry type, [drawn steel or cast aluminum] <Insert other>, [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert other> diameter with [holes] <Insert other> for panel mounting.

D. Element:  Bourdon tube or other type of pressure element.

E. Movement:  Mechanical, connecting element and pointer.

F. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

G. Pointer:  Red[ or other dark-color] metal.

H. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

I. Ring:  [Metal] [Brass] [Stainless steel].

J. Connector:  [Bottom] [Back] union type.

K. Thermal System:  Liquid- or mercury-filled bulb in copper-plated steel, aluminum, or brass stem for thermowell installation and of length to suit installation.

L. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.5 BIMETALLIC-ACTUATED DIAL THERMOMETERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

2. Ernst Gage Co.

3. Eugene Ernst Products Co.

4. Marsh Bellofram.

5. Miljoco Corp.

6. NANMAC Corporation.

7. Noshok, Inc.

8. Palmer - Wahl Instruments Inc.

9. REO TEMP Instrument Corporation.

10. Tel-Tru Manufacturing Company.

11. Trerice, H. O. Co.

12. Weiss Instruments, Inc.

13. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

14. WIKA Instrument Corporation.

15. Winters Instruments.

16. <Insert manufacturer's name.>

C. Description:  Direct-mounting, bimetallic-actuated dial thermometers complying with ASME B40.3.

D. Case:  [Dry] [Liquid-filled] type, stainless steel with [3-inch (76-mm)] [5-inch (127-mm)] diameter.

E. Element:  Bimetal coil.

F. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

G. Pointer:  Red[ or other dark-color] metal.

H. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

I. Ring:  Stainless steel.

J. Connector:  [Adjustable angle] [Rigid, back] [Rigid, bottom] <Insert other> type.

K. Stem:  Metal, for thermowell installation and of length to suit installation.

L. Accuracy:  Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range.

2.6 THERMOWELLS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Ernst Gage Co.

4. Marsh Bellofram.

5. Miljoco Corp.

6. NANMAC Corporation.

7. Noshok, Inc.

8. Palmer - Wahl Instruments Inc.

9. REO TEMP Instrument Corporation.

10. Tel-Tru Manufacturing Company.

11. Trerice, H. O. Co.

12. Weiss Instruments, Inc.

13. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

14. WIKA Instrument Corporation.

15. Winters Instruments.

16. <Insert manufacturer's name.>

Retain one of two paragraphs and list above or first paragraph below.

C. Manufacturers:  Same as manufacturer of thermometer being used.

D. Description:  Pressure-tight, socket-type metal fitting made for insertion into piping and of type, diameter, and length required to hold thermometer.

2.7 PRESSURE GAGES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AMETEK, Inc.; U.S. Gauge Div.

2. Ashcroft Commercial Instrument Operations; Dresser Industries; Instrument Div.

3. Ernst Gage Co.

4. Eugene Ernst Products Co.

5. KOBOLD Instruments, Inc.

6. Marsh Bellofram.

7. Miljoco Corp.

8. Noshok, Inc.

9. Palmer - Wahl Instruments Inc.

10. REO TEMP Instrument Corporation.

11. Trerice, H. O. Co.

12. Weiss Instruments, Inc.

13. Weksler Instruments Operating Unit; Dresser Industries; Instrument Div.

14. WIKA Instrument Corporation.

15. Winters Instruments.

16. <Insert manufacturer's name.>

C. Direct-Mounting, Dial-Type Pressure Gages:  Indicating-dial type complying with ASME B40.100.

1. Case:  [Dry] [Liquid-filled] type, [drawn steel or cast aluminum] [metal or plastic] [plastic], [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert other> diameter.

2. Pressure-Element Assembly:  Bourdon tube, unless otherwise indicated.

3. Pressure Connection:  Brass, NPS 1/4 (DN 8), bottom-outlet type unless back-outlet type is indicated.

4. Movement:  Mechanical, with link to pressure element and connection to pointer.

5. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

6. Pointer:  Red[ or other dark-color] metal.

7. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

8. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

9. Accuracy:  Grade [A, plus or minus 1 percent of middle half] [B, plus or minus 2 percent of middle half] [C, plus or minus 3 percent of middle half] [D, plus or minus 5 percent of whole] scale.

10. Vacuum-Pressure Range:  30-in. Hg of vacuum to 15 psig of pressure (100 kPa of vacuum to 103 kPa of pressure).

11. Range for Fluids under Pressure:  Two times operating pressure.

D. Remote-Mounting, Dial-Type Pressure Gages:  ASME B40.100, indicating-dial type.

1. Case:  Dry type, [drawn steel or cast aluminum] <Insert other>, [4-1/2-inch (114-mm)] [6-inch (152-mm)] <Insert other> diameter with [holes] <Insert other> for panel mounting.

2. Pressure-Element Assembly:  Bourdon tube, unless otherwise indicated.

3. Pressure Connection:  Brass, NPS 1/4 (DN 8), bottom-outlet type unless back-outlet type is indicated.

4. Movement:  Mechanical, with link to pressure element and connection to pointer.

5. Dial:  Satin-faced, nonreflective aluminum with permanently etched scale markings.

6. Pointer:  Red[ or other dark-color] metal.

7. Window:  [Glass] [Glass or plastic] [Plastic] <Insert other>.

8. Ring:  [Metal] [Brass] [Stainless steel] [Metal or plastic] [Plastic].

9. Accuracy:  Grade [A, plus or minus 1 percent of middle half] [B, plus or minus 2 percent of middle half] [C, plus or minus 3 percent of middle half] [D, plus or minus 5 percent of whole] scale.

10. Vacuum-Pressure Range:  30-in. Hg of vacuum to 15 psig of pressure (100 kPa of vacuum to 103 kPa of pressure).

11. Range for Fluids under Pressure:  Two times operating pressure.

E. Pressure-Gage Fittings:

1. Valves:  NPS 1/4 (DN 8) brass or stainless-steel needle type.

2. Snubbers:  ASME B40.5, NPS 1/4 (DN 8) brass bushing with corrosion-resistant, porous-metal disc of material suitable for system fluid and working pressure.

2.8 TEST PLUGS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Flow Design, Inc.

2. MG Piping Products Co.

3. National Meter, Inc.

4. Peterson Equipment Co., Inc.

5. Sisco Manufacturing Co.

6. Trerice, H. O. Co.

7. Watts Industries, Inc.; Water Products Div.

8. <Insert manufacturer's name.>

C. Description:  Corrosion-resistant brass or stainless-steel body with core inserts and gasketed and threaded cap, with extended stem for units to be installed in insulated piping.

D. Minimum Pressure and Temperature Rating:  [500 psig at 200 deg F (3450 kPa at 93 deg C)] <Insert other>.

E. Core Inserts:  One or two self-sealing rubber valves.

1. Insert material for water service at 20 to 200 deg F (minus 7 to plus 93 deg C) shall be CR.

2. Insert material for water service at minus 30 to plus 275 deg F (minus 35 to plus 136 deg C) shall be EPDM.

Retain paragraph below if required.

F. Test Kit:  Furnish [one] <Insert other> test kit(s) containing one pressure gage and adaptor, [one] [two] thermometer(s), and carrying case.  Pressure gage, adapter probes, and thermometer sensing elements shall be of diameter to fit test plugs and of length to project into piping.

1. Pressure Gage:  Small bourdon-tube insertion type with [2- to 3-inch- (51- to 76-mm-)] <Insert other> diameter dial and probe.  Dial range shall be [0 to 200 psig (0 to 1380 kPa)] <Insert other>.

Retain one of first two subparagraphs below.  If both are required, indicate location of each on Drawings.

2. Low-Range Thermometer:  Small bimetallic insertion type with [1- to 2-inch- (25- to 51-mm-)] <Insert other> diameter dial and tapered-end sensing element.  Dial ranges shall be [25 to 125 deg F (minus 4 to plus 52 deg C)] <Insert other>.

3. High-Range Thermometer:  Small bimetallic insertion type with [1- to 2-inch- (25- to 51-mm-)] <Insert other> diameter dial and tapered-end sensing element.  Dial ranges shall be [0 to 220 deg F (minus 18 to plus 104 deg C)] <Insert other>.

4. Carrying case shall have formed instrument padding.

PART 3 -  EXECUTION

3.1 THERMOMETER APPLICATIONS

A. Install [liquid-in-glass] [direct-mounting, vapor-actuated dial] [remote-mounting, vapor-actuated dial] [bimetallic-actuated dial] thermometers in the outlet of each domestic, hot-water storage tank.

B. Install [dry] [liquid-filled]-case-type, [vapor] [bimetallic]-actuated dial thermometers at suction and discharge of each pump.

C. Provide the following temperature ranges for thermometers:

Other temperature ranges and units with both Fahrenheit and Celsius scales are available.

1. Domestic Hot Water:  [30 to 180 deg F, with 2-degree scale divisions (Minus 1 to plus 82 deg C, with 1-degree scale divisions)] [30 to 240 deg F, with 2-degree scale divisions (Minus 1 to plus 115 deg C, with 1-degree scale divisions)] <Insert other>.

2. Domestic Cold Water:  [0 to 100 deg F, with 2-degree scale divisions (Minus 18 to plus 38 deg C, with 1-degree scale divisions)] [30 to 130 deg F, with 2-degree scale divisions (Minus 1 to plus 55 deg C, with 1-degree scale divisions)] <Insert other>.

3.2 GAGE APPLICATIONS

A. Install dry-case-type pressure gages for discharge of each pressure-reducing valve.

B. Install [dry] [liquid-filled]-case-type pressure gages at suction and discharge of each pump.

3.3 INSTALLATIONS

A. Install direct-mounting thermometers and adjust vertical and tilted positions.

B. Install remote-mounting dial thermometers on panel, with tubing connecting panel and thermometer bulb supported to prevent kinks.  Use minimum tubing length.

C. Install thermowells with socket extending [a minimum of 2 inches (51 mm) into fluid] [one-third of diameter of pipe] [to center of pipe] and in vertical position in piping tees where thermometers are indicated.

D. Install direct-mounting pressure gages in piping tees with pressure gage located on pipe at most readable position.

E. Install remote-mounting pressure gages on panel.

F. Install needle-valve and snubber fitting in piping for each pressure gage.

G. Install test plugs in tees in piping.

H. Install permanent indicators on walls or brackets in accessible and readable positions.

I. Install connection fittings for attachment to portable indicators in accessible locations.

J. Install thermometers and gages adjacent to machines and equipment to allow service and maintenance for thermometers, gages, machines, and equipment.

K. Adjust faces of thermometers and gages to proper angle for best visibility.

END OF SECTION 220519

	METERS AND GAGES FOR PLUMBING PIPING
	220519 - 1



