Copyright 2001 and 2005 AIA
MASTERSPEC Full Length
09/01 (R 06/05)

Copyright 2001 and 2005 (R 09/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221123 - DOMESTIC WATER PUMPS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following all-bronze and bronze-fitted centrifugal pumps for domestic cold- and hot-water circulation:

Terminology used in this Section is from HI 1.1-1.2.

1. Close-coupled, in-line, sealless centrifugal pumps.

2. Separately coupled, in-line centrifugal pumps.

3. Separately coupled, horizontally mounted, in-line centrifugal pumps.

4. Close-coupled, horizontally mounted, in-line centrifugal pumps.

5. Close-coupled, vertically mounted, in-line centrifugal pumps.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 22 Section "Domestic-Water Packaged Booster Pumps" for booster systems.

2. Division 33 Section "Water Supply Wells" for well pumps.

1.3 SUBMITTALS

A. Product Data:  For each type and size of domestic water pump specified.  Include certified performance curves with operating points plotted on curves; and rated capacities of selected models, furnished specialties, and accessories.

B. Shop Drawings:  Diagram power, signal, and control wiring.

C. Operation and Maintenance Data:  For domestic water pumps to include in emergency, operation, and maintenance manuals.

1.4 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 01 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of domestic water pumps and are based on the specific system indicated.  Refer to Division 01 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. UL Compliance:  Comply with UL 778 for motor-operated water pumps.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Retain shipping flange protective covers and protective coatings during storage.

B. Protect bearings and couplings against damage.

C. Comply with pump manufacturer's written rigging instructions for handling.

1.6 COORDINATION

Retain this Article if pumps will be supported on a concrete base.

A. Coordinate size and location of concrete bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Refer to the Domestic Water Pump Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 CLOSE COUPLED, IN-LINE, SEALLESS CENTRIFUGAL PUMPS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Armstrong Pumps Inc.

2. Bell & Gossett Domestic Pump; ITT Industries.

3. Grundfos Pumps Corp.

4. Taco, Inc.

5. <Insert manufacturer's name.>

B. Description:  Factory-assembled and -tested, single-stage, close-coupled, in-line, sealless centrifugal pumps as defined in HI 5.1-5.6.

1. Pump and Motor Assembly:  Hermetically sealed, replaceable-cartridge-type unit with motor and impeller on common shaft and designed for installation with pump and motor shaft mounted horizontally.

2. Casing:  Bronze, with threaded companion-flange connections.

Edit first subparagraph below if bronze or stainless-steel impeller is required.

3. Impeller:  Corrosion-resistant material.

4. Motor:  Single speed, unless otherwise indicated.  Comply with requirements in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

C. Capacities and Characteristics:

1. Capacity:  <Insert gpm (L/s).>

2. Total Dynamic Head:  <Insert feet (kPa).>

3. Maximum Operating Pressure:  125 psig (860 kPa).

4. Maximum Continuous Operating Temperature:  220 deg F (104 deg C).

5. Impeller Size:  <Insert inches (mm).>

6. Inlet and Outlet Size:  <Insert inches (mm).>

7. Speed:  <Insert rpm.>

8. Motor Horsepower:  <Insert value.>

9. Electrical Characteristics:

a. Volts:  [120] [240] <Insert value>.

b. Phases:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

2.3 SEPARATELY COUPLED, IN-LINE CENTRIFUGAL PUMPS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Armstrong Pumps Inc.

2. Bell & Gossett Domestic Pump; ITT Industries.

3. Marshall Engineered Products Co.

4. Paco Pumps, Inc.

5. Taco, Inc.

6. Thrush Company, Inc.

7. Weinman Div.; Crane Pumps & Systems.

8. <Insert manufacturer's name.>

B. Description:  Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3; and designed for installation with pump and motor shafts mounted horizontally.

1. Pump Construction:  [All bronze] [All bronze or bronze fitted] [Bronze fitted].

a. Casing:  Radially split, [bronze] [cast iron], with threaded companion-flange connections.

b. Impeller:  [Corrosion-resistant material] [ASTM B 36/B 36M, rolled brass; or ASTM B 584, cast bronze]; keyed to shaft.

c. Shaft and Shaft Sleeve:  Steel shaft, with copper-alloy shaft sleeve.

d. Seal:  Mechanical, with carbon-steel rotating ring, stainless-steel spring, ceramic seat, and rubber bellows and gasket.  Include water slinger on shaft between motor and seal.

e. Bearings:  Oil-lubricated; bronze-journal or thrust type.

2. Shaft Coupling:  Flexible, capable of absorbing torsional vibration and shaft misalignment.

3. Motor:  Single speed, with oil-lubricated bearings, unless otherwise indicated; and resiliently mounted to pump casing.  Comply with requirements in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

C. Capacities and Characteristics:

1. Capacity:  <Insert gpm (L/s).>

2. Total Dynamic Head:  <Insert feet (kPa).>

3. Maximum Operating Pressure:  125 psig (860 kPa).

4. Maximum Continuous Operating Temperature:  225 deg F (107 deg C).

5. Impeller Size:  <Insert inches (mm).>

6. Inlet and Outlet Size:  <Insert inches (mm).>

7. Speed:  <Insert rpm.>

8. Motor Horsepower:  <Insert value.>

9. Electrical Characteristics:

a. Volts:  [120] [240] <Insert value>.

b. Phases:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

2.4 SEPARATELY COUPLED, HORIZONTALLY MOUNTED, IN-LINE CENTRIFUGAL PUMPS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Alyan Pump Company.

2. Aurora Pump; Pentair Pump Group (The).

3. Bell & Gossett Domestic Pump; ITT Industries.

4. Grundfos Pumps Corp.

5. Taco, Inc.

6. Thrush Company, Inc.

7. Weinman Div.; Crane Pumps & Systems.

8. <Insert manufacturer's name.>

B. Description:  Factory-assembled and -tested, overhung-impeller, single-stage, separately coupled, horizontally mounted, in-line centrifugal pumps as defined in HI 1.1-1.2 and HI 1.3; and designed for installation with pump and motor shafts mounted horizontally.

1. Pump Construction:  [All bronze] [All bronze or bronze fitted] [Bronze fitted].

a. Casing:  Radially split, cast iron, with threaded companion-flange connections for pumps with NPS 2 (DN 50) pipe connections and flanged connections for pumps with NPS 2-1/2 (DN 65) pipe connections.

b. Impeller:  ASTM B 584, cast bronze; statically and dynamically balanced, closed, and keyed to shaft.

c. Shaft and Shaft Sleeve:  Steel shaft, with copper-alloy shaft sleeve.

d. Seal:  Mechanical, with carbon-steel rotating ring, stainless-steel spring, ceramic seat, and rubber bellows and gasket.  Include water slinger on shaft between motor and seal.

e. Bearings:  Oil-lubricated; bronze-journal or ball type.

2. Shaft Coupling:  Flexible, capable of absorbing torsional vibration and shaft misalignment.

3. Motor:  Single speed, with grease-lubricated ball bearings; and resiliently mounted to pump casing.  Comply with requirements in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

C. Capacities and Characteristics:

1. Capacity:  <Insert gpm (L/s).>

2. Total Dynamic Head:  <Insert feet (kPa).>

3. Maximum Operating Pressure:  125 psig (860 kPa).

4. Maximum Continuous Operating Temperature:  225 deg F (107 deg C).

5. Impeller Size:  <Insert inches (mm).>

6. Inlet and Outlet Size:  <Insert inches (mm).>

7. Speed:  <Insert rpm.>

8. Motor Horsepower:  <Insert value.>

9. Electrical Characteristics:

a. Volts:  [120] [240] <Insert value>.

b. Phases:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

2.5 CLOSE-COUPLED, HORIZONTALLY MOUNTED, IN-LINE CENTRIFUGAL PUMPS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Armstrong Pumps Inc.

2. Bell & Gossett Domestic Pump; ITT Industries.

3. Marshall Engineered Products Co.

4. Paco Pumps, Inc.

5. Thrush Company, Inc.

6. Weinman Div.; Crane Pumps & Systems.

7. <Insert manufacturer's name.>

B. Description:  Factory-assembled and -tested, overhung impeller, single-stage, close-coupled, horizontally mounted, in-line centrifugal pumps as defined in HI 1.1-1.2 and HI 1.3; and designed for installation with pump and motor shafts mounted horizontally.

1. Pump Construction:  [All bronze] [All bronze or bronze fitted] [Bronze fitted].

a. Casing:  Radially split, cast iron, with threaded companion-flange connections for pumps with NPS 2 (DN 50) pipe connections and flanged connections for pumps with NPS 2-1/2 (DN 65) pipe connections.

b. Impeller:  ASTM B 584, cast bronze; statically and dynamically balanced, closed, and keyed to shaft.

c. Shaft and Shaft Sleeve:  Steel shaft, with copper-alloy shaft sleeve.

d. Seal:  Mechanical, with carbon-steel rotating ring, stainless-steel spring, ceramic seat, and rubber bellows and gasket.  Include water slinger on shaft between motor and seal.

e. Bearings:  Oil-lubricated; bronze-journal or ball type.

2. Shaft Coupling:  Rigid type if pump is provided with coupling.

3. Motor:  Single speed, with grease-lubricated ball bearings.  Comply with requirements in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

C. Capacities and Characteristics:

1. Capacity:  <Insert gpm (L/s).>

2. Total Dynamic Head:  <Insert feet (kPa).>

3. Maximum Operating Pressure:  175 psig (1200 kPa).

4. Maximum Continuous Operating Temperature:  225 deg F (107 deg C).

5. Impeller Size:  <Insert inches (mm).>

6. Inlet and Outlet Size:  <Insert inches (mm).>

7. Speed:  <Insert rpm.>

8. Motor Horsepower:  <Insert value.>

9. Electrical Characteristics:

a. Volts:  [120] [240] <Insert value>.

b. Phases:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

2.6 CLOSE-COUPLED, VERTICALLY MOUNTED, IN-LINE CENTRIFUGAL PUMPS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Alyan Pump Company.

2. Armstrong Pumps Inc.

3. Aurora Pump; Pentair Pump Group (The).

4. Bell & Gossett Domestic Pump; ITT Industries.

5. Federal Pump Corp.

6. Grundfos Pumps Corp.

7. Marshall Engineered Products Co.

8. Paco Pumps, Inc.

9. Sterling Peerless; Sterling Fluid Systems Group.

10. Taco, Inc.

11. Thrush Company, Inc.

12. Weinman Div.; Crane Pumps & Systems.

13. <Insert manufacturer's name.>

B. Description:  Factory-assembled and -tested, overhung impeller, single-stage, close-coupled, vertically mounted, in-line centrifugal pumps as defined in HI 1.1-1.2 and HI 1.3; and designed for installation with pump and motor shafts mounted vertically.

1. Pump Construction:  Bronze fitted.

a. Casing:  Radially split, cast iron, with wear rings and threaded companion-flange connections for pumps with NPS 2 (DN 50) pipe connections and flanged connections for pumps with NPS 2-1/2 (DN 65) pipe connections.[ Include pump manufacturer's base attachment for mounting pump on concrete base.]

b. Impeller:  ASTM B 584, cast bronze; statically and dynamically balanced, closed, and keyed to shaft.

c. Shaft and Shaft Sleeve:  [Stainless-steel or steel] [Stainless-steel] shaft, with copper-alloy shaft sleeve.

d. Seal:  Mechanical, with carbon-steel rotating ring, stainless-steel spring, ceramic seat, and rubber bellows and gasket.  Include water slinger on shaft between motor and seal.

e. Bearings:  Oil-lubricated; bronze-journal or ball type.

2. Shaft Coupling:  Rigid type if pump is provided with coupling.

3. Motor:  Single speed, with grease-lubricated ball bearings; and directly mounted to pump casing.  Comply with requirements in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

Delete subparagraph below if lifting and supporting lug feature is not available for pump models selected, if pumps will be supported by piping, or if pumps will be mounted on concrete bases.

a. Lifting and Supporting Lug:  Factory mounted in top of motor enclosure.

If Project has more than one pump, delete paragraph and subparagraphs below and schedule pumps on Drawings.

C. Capacities and Characteristics:

1. Capacity:  <Insert gpm (L/s).>

2. Total Dynamic Head:  <Insert feet (kPa).>

3. Maximum Operating Pressure:  175 psig (1200 kPa).

4. Inlet and Outlet Size:  <Insert inches (mm).>

5. Speed:  <Insert rpm.>

6. Motor Horsepower:  <Insert value.>

7. Electrical Characteristics:

a. Volts:  [120] [240] <Insert value>.

b. Phases:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

2.7 CONTROLS

Thermostats in first paragraph below are sometimes called "aquastats."  Aquastat is a registered trademark of Honeywell International.

A. Thermostats:  Electric; adjustable for control of hot-water circulation pump.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Honeywell International, Inc.

b. Square D.

c. White-Rodgers Div.; Emerson Electric Co.

d. <Insert manufacturer's name.>

2. Type:  Water-immersion sensor, for installation in hot-water circulation piping.

3. Range:  [50 to 125 deg F (10 to 52 deg C)] [65 to 200 deg F (18 to 93 deg C)] [100 to 240 deg F (38 to 116 deg C)] <Insert other>.

4. Operation of Pump:  On or off.

5. Transformer:  Provide if required.

6. Power Requirement:  [24 V, ac] [120 V, ac] <Insert other>.

7. Settings:  Start pump at [105 deg F (41 deg C)] [110 deg F (43 deg C)] [115 deg F (46 deg C)] <Insert other> and stop pump at [120 deg F (49 deg C)] [125 deg F (52 deg C)] <Insert other>.

Retain paragraph and associated subparagraphs below if applying controls to limit hot-water circulation pump operation to periods when hot water is required to qualify for LEED Prerequisite EA 2.

B. Timers:  Electric time clock for control of hot-water circulation pump.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Honeywell International, Inc.

b. Intermatic, Inc.

c. Johnson Controls, Inc.

d. Maple Chase Company.

e. TORK.

f. <Insert manufacturer's name.>

2. Type:  Programmable, [seven-day] <Insert other> clock with manual override on-off switch.

3. Enclosure:  Suitable for wall mounting.

4. Operation of Pump:  On or off.

5. Transformer:  Provide if required.

6. Power Requirement:  [24 V, ac] [120 V, ac] <Insert other>.

7. Programmable Sequence of Operation:  [Up to two on-off cycles each day for seven days] <Insert operational sequence>.

Retain paragraph and subparagraphs below if applying controls to limit hot-water storage tank circulation pump operation to qualify for LEED Prerequisite EA 2.

C. Time Delay Relay:  Control for hot-water storage tank circulation pump.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Honeywell International, Inc.

b. Intermatic, Inc.

c. Johnson Controls, Inc.

d. Maple Chase Company.

e. Square D.

f. White-Rodgers Div.; Emerson Electric Co.

g. <Insert manufacturer's name.>

2. Type:  Adjustable time delay relay.

3. Range:  Up to five minutes.

4. Setting:  Five minutes.

5. Operation of Pump:  On or off.

6. Transformer:  Provide if required.

7. Power Requirement:  [24 V, ac] [120 V, ac] <Insert other>.

8. Programmable Sequence of Operation:  Limit pump operation to periods of burner operation plus maximum five minutes after the burner stops.

2.8 FLEXIBLE CONNECTORS

Delete this Article if flexible connectors are specified in Division 22 Section "Domestic Water Piping" or if not required.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Anamet, Inc.

2. Flex-Hose Co., Inc.

3. Flexicraft Industries.

4. Flex-Pression, Ltd.

5. Flex-Weld, Inc.

6. Hyspan Precision Products, Inc.

7. Mercer Rubber.

8. Metraflex, Inc.

9. Proco Products, Inc.

10. Tozen America Corporation.

11. Unaflex Inc.

12. <Insert manufacturer's name.>

B. Description:  Corrugated, bronze inner tubing covered with bronze wire braid.  Include copper-tube ends or bronze flanged ends, braze-welded to tubing.  Include [125-psig (860-kPa)] <Insert other> minimum working-pressure rating and ends matching pump connections.

2.9 BUILDING-AUTOMATION-SYSTEM INTERFACE

A. Provide auxiliary contacts in pump controllers for interface to building automation system.  Include the following:

1. On-off status of each pump.

2. Alarm status.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in of domestic-water-piping system to verify actual locations of connections before pump installation.

3.2 CONCRETE BASES

Coordinate sizes and locations of concrete bases.  Verify structural requirements with structural engineer.

A. Install concrete bases of dimensions indicated for pumps and controllers.  Refer to Division 22 Section "Common Work Results for Plumbing."

Revise subparagraphs below based on installed equipment.  Indicate dowel-rod quantity, size, and spacing on Drawings.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

B. Cast-in-place concrete materials and placement requirements are specified in Division 03.

3.3 PUMP INSTALLATION

A. Comply with HI 1.4.

B. Install pumps with access for periodic maintenance including removal of motors, impellers, couplings, and accessories.

C. Independently support pumps and piping so weight of piping is not supported by pumps and weight of pumps is not supported by piping.

D. Install [in-line, sealless] [separately coupled, in-line] [separately coupled, horizontally mounted, in-line] [close-coupled, horizontally mounted, in-line] centrifugal pumps with motor and pump shafts horizontal.

E. Install continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of sufficient size to support pump weight.  Vibration isolation devices are specified in Division 22 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment." Fabricate brackets or supports as required.  Hanger and support materials are specified in Division 22 Section "Hangers and Supports for Plumbing Piping and Equipment."

F. Suspend vertically mounted, in-line centrifugal pumps independent of piping.  Install pumps with motor and pump shafts vertical.  Use continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of sufficient size to support pump weight.  Vibration isolation devices are specified in Division 21 Section "Vibration and Seismic Controls for Fire-Suppression Piping and Equipment." Hanger and support materials are specified in Division 22 Section "Hangers and Supports for Plumbing Piping and Equipment."

Retain paragraph above or below.

G. Install vertical in-line pumps on concrete bases.  Install pumps with motor and pump shafts vertical.

3.4 CONTROL INSTALLATION

A. Install immersion-type thermostats in hot-water return piping.

B. Install timers [on wall in engineer's office] <Insert other>.

3.5 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 22 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to pumps to allow service and maintenance.

C. Connect domestic water piping to pumps.  Install suction and discharge piping equal to or greater than size of pump nozzles.  Refer to Division 22 Section "Domestic Water Piping."

1. Install flexible connectors adjacent to pumps in suction and discharge piping of the following pumps:

a. Separately coupled, in-line centrifugal pumps.

b. Separately coupled, horizontally mounted, in-line centrifugal pumps.

c. Close-coupled, horizontally mounted, in-line centrifugal pumps.

d. Close-coupled, vertically mounted, in-line centrifugal pumps.

2. Install shutoff valve and strainer on suction side of pumps, and check valve and throttling valve on discharge side of pumps.  Install valves same size as connected piping.  Refer to Division 22 Section "General-Duty Valves for Plumbing Piping" for general-duty valves for domestic water piping and Division 22 Section "Domestic Water Piping Specialties" for strainers.

3. Install pressure gages at suction and discharge of pumps.  Install at integral pressure-gage tappings where provided or install pressure-gage connectors in suction and discharge piping around pumps.  Refer to Division 22 Section "Meters and Gages for Plumbing Piping" for pressure gages and gage connectors.

D. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

E. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

F. Connect [thermostats] [thermostats and timers] [timers] to pumps that they control.

Retain paragraph below if applying controls to limit hot-water storage tank circulation pump operation to qualify for LEED Prerequisite EA 2.

G. Interlock pump with water heater burner and time delay relay.

3.6 STARTUP SERVICE

Delete this Article if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Check piping connections for tightness.

3. Clean strainers on suction piping.

4. Set [thermostats] [thermostats and timers] [timers] for automatic starting and stopping operation of pumps.

5. Perform the following startup checks for each pump before starting:

a. Verify bearing lubrication.

b. Verify that pump is free to rotate by hand and that pump for handling hot liquid is free to rotate with pump hot and cold.  If pump is bound or drags, do not operate until cause of trouble is determined and corrected.

c. Verify that pump is rotating in the correct direction.

6. Prime pump by opening suction valves and closing drains, and prepare pump for operation.

7. Start motor.

8. Open discharge valve slowly.

9. Adjust temperature settings on thermostats.

10. Adjust timer settings.

3.7 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain[ controls and] pumps.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 221123

	DOMESTIC WATER PUMPS
	221123 - 1



