Copyright 2004 and 2005 AIA
MASTERSPEC Short Form
03/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221343 - FACILITY PACKAGED SEWAGE PUMPING STATIONS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes wet-well, packaged pumping stations with [submersible] [submersible grinder] sewage pumps.

1.2 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:  Show fabrication and installation details for each packaged sewage pumping station.  Detail equipment assemblies and indicate dimensions; shipping, installed, and operating weights; loads; required clearances; method of field assembly; components; electrical characteristics; and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and maintenance data.

E. Warranty:  Special warranty specified in this Section.

1.3 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. Comply with HI 1.1-1.2, "Centrifugal Pumps for Nomenclature and Definitions"; HI 1.3, "Centrifugal Pumps for Design and Application"; and HI 1.4, "Centrifugal Pumps for Installation, Operation and Maintenance," for sewage[ and sump] pumps.

C. Comply with UL 778, "Motor-Operated Water Pumps," for sewage[ and sump] pumps.

1.4 PROJECT CONDITIONS

Retain paragraph and subparagraphs below if interruption of existing sanitary sewer service is required.

A. Interruption of Existing Sanitary Sewer Service:  Do not interrupt sanitary sewer service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary sanitary sewer service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of sanitary sewer service.

2. Do not proceed with interruption of sanitary sewer service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of packaged sewage pumping stations that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Structural failures including shell.

b. Faulty operation of sewage pumps, controls, or accessories.

c. Deterioration of metals, metal finishes, and other materials beyond normal use.

Verify available warranties for units and components and insert number in subparagraphs below.

2. Warranty Period for Shells:  <Insert number> years from date of Substantial Completion.

3. Warranty Period for Sewage Pumps and Controls:  <Insert number> years from date of Substantial Completion.

4. Warranty Period for Accessories:  <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 WET-WELL, PACKAGED SEWAGE PUMPING STATIONS

A. Wet-Well, Packaged Sewage Pumping Stations with Submersible Sewage Pumps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Gorman-Rupp Company (The).

b. Metropolitan Industries, Inc.

c. PumpTech, Inc.

d. USEMCO.

e. Yeomans Chicago Corporation.

f. <Insert manufacturer's name.>

4. Description:  Factory fabricated, assembled, and tested with wet well for sewage pumps and collection of sanitary sewage and with sewage pumps and dry equipment chamber for controls and accessories.

a. Orientation:  Shell underground with dry equipment chamber [underground with top flush with grade] [partially recessed underground] [above grade] [underground with entrance tube to grade] <Insert orientation>.

b. Shell:  Factory fabricated from fiberglass.

Retain first subparagraph below if shell orientation requires an entrance tube.

c. Entrance Tube:  From dry compartment to entrance at grade, and of size required to replace largest piece of equipment, but not smaller than [36 inches (914 mm)] <Insert dimension> in diameter.

d. Sewage Pumps:  [Two] [Three] <Insert number> submersible-type sewage pumps, with guide rail, quick-disconnect system, controls, and piping.  Include ASTM A 48/A 48M, Class 25, nonclog, cast-iron impeller capable of passing solids of 3-inch (76-mm) minimum diameter; and hermetically sealed motor with moisture-sensing probe, mechanical seals, and waterproof power cable.

If Project has more than one wet-well, packaged sewage pumping station with submersible sewage pumps, delete subparagraph and associated subparagraphs below and schedule pumping stations on Drawings.

5. Capacities and Characteristics:

a. Diameter or Dimensions of Shell:  <Insert inches (mm) or other dimensions.>

b. Height of Shell Base Section:  <Insert inches (mm).>

c. Pumping Station, Inlet Pipe Size:  <Insert NPS (DN).>

d. Pumping Station, Discharge Pipe Size:  <Insert NPS (DN).>

e. Sewage Pumps:  [Two] [Three] <Insert number> required.

f. Each Sewage Pump:

1) Capacity:  <Insert gpm (L/s).>

2) Total Dynamic Head:  <Insert feet (kPa).>

3) Speed:  <Insert rpm.>

4) Impeller:

a) Type:  <Insert type.>

b) Diameter:  <Insert inches (mm).>

c) Solids Size Design:  <Insert inches (mm).>

5) Inlet Size:  <Insert NPS (DN).>

6) Discharge Size:  <Insert NPS (DN).>

7) Motor Size:  <Insert value> hp.

8) Electrical Characteristics:

a) Volts:  [240] [277] [480] <Insert value> V.

b) Phases:  [Single] [Three].

c) Hertz:  60.

g. Sump Pump:

1) Capacity:  <Insert gpm (L/s).>

2) Total Dynamic Head:  <Insert feet (kPa).>

3) Speed:  <Insert rpm.>

4) Discharge Size:  <Insert NPS (DN).>

5) Motor Size:  <Insert value> hp.

6) Electrical Characteristics:

a) Volts:  [120] [240] [277] [480] <Insert value> V.

b) Phases:  [Single] [Three].

c) Hertz:  60.

h. Pumping Station Electrical Characteristics:

1) Full-Load Amperes:  <Insert value.>

2) Minimum Circuit Ampacity:  <Insert value.>

3) Maximum Overcurrent Protection:  <Insert amperage.>

B. Wet-Well, Packaged Sewage Pumping Stations with Submersible Grinder Sewage Pumps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Environment One Corporation.

b. Gorman-Rupp Company (The).

c. Pentair Pump Group; F. E. Myers.

d. PumpTech, Inc.

e. USEMCO.

f. <Insert manufacturer's name.>

4. Description:  Factory fabricated, assembled, and tested with wet well for sewage pumps and collection of sanitary sewage and with dry equipment chamber for controls and accessories.

a. Orientation:  Shell underground with dry equipment chamber [underground with top flush with grade] [partially recessed underground] [above grade] [underground with entrance tube to grade] <Insert orientation>.

b. Shell:  Factory fabricated from fiberglass.

Retain first subparagraph below if shell orientation requires an entrance tube.

c. Entrance Tube:  From dry compartment to entrance at grade, and of size required to replace largest piece of equipment, but not smaller than [36 inches (914 mm)] <Insert dimension> in diameter.

d. Sewage Pumps:  [Two] [Three] <Insert number> submersible grinder-type sewage pumps, with guide rail, quick-disconnect system, controls, and piping.  Include stainless-steel grinder impeller and hermetically sealed motor with moisture-sensing probe, mechanical seals, and waterproof power cable.

If Project has more than one wet-well, packaged sewage pumping station with submersible grinder sewage pumps, delete subparagraph and associated subparagraphs below and schedule pumping stations on Drawings.

5. Capacities and Characteristics:

a. Diameter or Dimensions of Shell:  <Insert inches (mm) or other dimensions.>

b. Height of Shell Base Section:  <Insert inches (mm).>

c. Pumping Station, Inlet Pipe Size:  <Insert NPS (DN).>

d. Pumping Station, Discharge Pipe Size:  <Insert NPS (DN).>

e. Sewage Pumps:  [Two] [Three] <Insert number> required.

f. Each Sewage Pump:

1) Capacity:  <Insert gpm (L/s).>

2) Total Dynamic Head:  <Insert feet (kPa).>

3) Speed:  <Insert rpm.>

4) Impeller:  [Cutter] [Cutter or grinder] [Grinder] type.

5) Inlet Size:  <Insert NPS (DN).>

6) Discharge Size:  <Insert NPS (DN).>

7) Motor Size:  <Insert value> hp.

8) Electrical Characteristics:

a) Volts:  [240] [277] [480] <Insert value> V.

b) Phases:  [Single] [Three].

c) Hertz:  60.

g. Sump Pump:

1) Capacity:  <Insert gpm (L/s).>

2) Total Dynamic Head:  <Insert feet (kPa).>

3) Speed:  <Insert rpm.>

4) Discharge Size:  <Insert NPS (DN).>

5) Motor Size:  <Insert value> hp.

6) Electrical Characteristics:

a) Volts:  [120] [240] [277] [480] <Insert value> V.

b) Phases:  [Single] [Three].

c) Hertz:  60.

h. Pumping Station Electrical Characteristics:

1) Full-Load Amperes:  <Insert value.>

2) Minimum Circuit Ampacity:  <Insert value.>

3) Maximum Overcurrent Protection:  <Insert amperage.>

2.2 CONTROLS

Retain and revise this Article to suit Project.  Other controls are available.  See Evaluations for a more comprehensive discussion.  Paragraph below is for two sewage pumps; revise if three or more sewage pumps are required.

A. Control Sequence of Operation:  Cycle each sewage pump on and off automatically to maintain wet-well sewage level.  Automatic control operates both pumps in parallel if wet-well level rises above starting point of low-level pump, until shutoff level is reached.  Automatic alternator, with manual disconnect switch, changes sequence of lead-lag sewage pumps at completion of each pumping cycle.

In first paragraph below, select one option or allow for several sensors.

B. [Electrode] [Float-Switch] [Pressure-Switch] [Ultrasonic] System:  Senses variations of sewage level in wet well.  Include high and low adjustments capable of operating on 6-inch (150-mm) minimum differential of liquid level.

C. Motor Controllers:  Magnetic, full voltage, nonreversing.  Include undervoltage release, thermal-overload heaters in each phase, manual reset buttons, and hand-automatic selector switches.  Include circuit breakers to provide branch-circuit protection for each controller.

D. 120-V accessory controls with 15-A, single-phase circuit breakers or fuses for each item.

E. Control Panel:  Enclosure complying with UL 508A[ and with UL 508A, Supplement SB] with separate compartments and covers for controllers, circuit breakers, transformers, alternators, and single-phase controls.  Include 20-A duplex receptacle in NEMA WD 1, Configuration 5-20R mounted on exterior of control panel.

1. Mounting:  [Inside, on dry-chamber wall] [Outside, on pedestal, at grade] <Insert building description and room number>.

Revise enclosure type in subparagraph below if another type is required or more suitable.

2. Enclosure:  NEMA 250, Type [1] [4] [4X] <Insert type>.

F. Install labels on panel face to identify switches and controls.

G. Wiring:  Tin-copper wiring.

H. Connection for Portable Generator:  Nonautomatic (manual) transfer switch with receptacle matching generator electrical power requirements.  Nonautomatic transfer switches are specified in Division 26 Section "Transfer Switches" and receptacles are specified in Division 26 Section "Wiring Devices."

2.3 ACCESSORIES

Retain and revise this Article to suit Project.

A. Lighting:  Minimum of 2, UL 1571, heavy-duty, cast-metal, wet-location-type fixtures with 100-W bulbs and guards in service area.  Locate switches, with pilot lights, at chamber entrance.

B. Submersible Sump Pump:

1. Discharge Size:  NPS 1-1/4 (DN 32) minimum.

2. Pump End Bell and Motor Shell:  Cast iron.

Revise horsepower in first subparagraph below and add voltage and phase if required; or delete horsepower here and insert horsepower, voltage, and phase in schedule if required.

3. Motor:  1/3 hp, 1750-rpm, hermetically sealed, capacitor-start, with built-in overload protection.

4. Impeller:  ASTM B 584, cast bronze or ASTM B 36/B 36M, brass.

5. Shaft:  Stainless steel.

6. Bearings:  Grease-lubricated, factory-sealed ball bearings.

7. Seals:  Mechanical.

8. Accessories:  Inlet strainer.

9. Controls:  Float switch.

Dehumidifier in first paragraph below is needed to protect accessories, controls, and piping.

C. Dehumidifier:  Electric refrigeration system, adjustable humidistat, reverse-acting thermostat for low-temperature cutoff controls, and condensate pump with drain piping to sump.

Revise subparagraph below to suit Project.

1. Dehumidification system capacity adequate to remove at least 15 pints (7 L) of water per day from service area air that is 80 deg F (27 deg C) with a relative humidity of 60 percent.

D. Ventilation:  Electrically powered ventilation system.  Include centrifugal blower with 4-inch- (100-mm-) round exhaust vent designed to keep out rain, insects, and other foreign matter; limit switch to start blower if entrance door or lid is opened; 0- to 15-minute timer; and separate manual switch.

Revise subparagraph below to suit Project.

1. Ventilating system capacity to change air in dry equipment chamber every two minutes.

Delete first paragraph below if no heater.  If retaining, increase heater capacity to suit Project.

E. Heater:  Electric, 1.5 kW minimum, with fan and thermostat control.

F. High-Water Audio Alarm:  Horn for audio indication of station high-water level, energized by separate level-detecting device.  Include alarm silencer switch and relay in station.

G. Remote Alarm Circuit:  Include contacts for connection to remote alarm panel.

2.4 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 22 Section "Common Motor Requirements for Plumbing Equipment." If different characteristics are required, add paragraphs to this Article to suit Project.

A. General requirements for motors are specified in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

2.5 MISCELLANEOUS MATERIALS

A. Structural Steel:  ASTM A 6/A 6M, W or HP shapes, or ASTM A 36/A 36M, plates or beams.

B. Grout:  ASTM C 1107, Grade B, nonshrink cement grout.

1. Design Mix:  5000-psi (34.5-MPa), 28-day compressive strength.

C. Concrete:  Concrete is specified in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

2.6 PACKAGED SEWAGE PUMPING STATION FABRICATION

A. Fabricate shell from fiberglass with structural-steel reinforcement.

1. Attach structural-steel reinforcement to top and bottom heads.

2. Fabricate shell with continuous joints to make watertight and gastight construction.

3. Attach air vent to pump chamber[ and entrance tube].

4. Ladder:  [Steel] [Fiberglass].

B. Install sump, 18 inches (450 mm) in diameter by 10 inches (254 mm) deep in dry-chamber floor.  Slope floor toward sump and fasten rubber mat to floor walkway with cement.

Delete first paragraph below if entrance tube is not required.

C. Entrance tube may be furnished separately for field installation.

D. Entrance Cover:  Waterproof and corrosion resistant, with lock.  Include way to open cover from inside tube if cover is locked.

E. Air Vent:  Duct fabricated from corrosion-resistant material, extended to above grade, outlet turned down, and with insect screen in outlet.

F. Factory fabricate piping between unit components.

1. Use galvanized-steel pipe and cast-iron fittings or ductile-iron pipe and fittings.

2. Use fittings for changes in direction and branch connections.

3. Flanged and union joints may be used instead of joints specified.

4. Use dielectric fittings for connections between ferrous- and copper-alloy piping.

G. Piping Connections:  Unless otherwise indicated, make the following piping connections:

1. Install unions, in piping NPS 2 (DN 50) and smaller, adjacent to each valve and at final connection to each piece of equipment having NPS 2 (DN 50) or smaller threaded pipe connection.

2. Install flanges, in piping NPS 2-1/2 (DN 65) and larger, adjacent to flanged valves and at final connection to each piece of equipment having flanged pipe connection.

H. Valves:  Ferrous alloy.

1. Sewage Pump Piping:  Include gate valve on each pump inlet and gate and check valves on each discharge pipe.

Delete subparagraph below if not required.

2. Sump Pump Piping:  Include ball or gate and check valves on discharge pipe.

I. Wiring:  Tin-coated copper.

2.7 SOURCE QUALITY CONTROL

A. Test and inspect sewage[ and sump] pumps according to HI 1.6, "Centrifugal Pump Tests." Include test recordings that substantiate correct performance of pumps at design head, capacity, suction lift, speed, and horsepower.

B. Test accessories and controls through complete cycle.  Include test recordings that substantiate correct performance.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Excavation, trenching, and backfilling are specified in Division 31 Section "Earth Moving."

B. Install packaged sewage pumping station components where indicated, according to specific equipment and piping arrangement indicated.

Coordinate sizes and locations of concrete bases in first paragraph below with pumping stations.  Verify structural requirements with structural engineer.

C. Shell Base Supports:  Form from structural-steel beams, of number and lengths required to support bottom of shell and to anchor beams to concrete foundation.

Delete subparagraph below if dry-chamber floor is sloped down toward sump.

1. Use elevator blocks attached to bottom of shell to slope station floor 1 inch in 10 feet (25.4 mm in 3 m) down toward sump.

D. Grout under and around shell.  Ensure that there are no voids between foundation slab and underslab of pumping station.

E. Fill voids between shell sidewalls, sleeves, and piping and make watertight seal with grout.

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

F. Sanitary sewer piping installation requirements are specified in Division 22 Section "Facility Sanitary Sewers." Drawings indicate general arrangement of piping.

G. Install piping adjacent to machine to allow service and maintenance.

H. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

I. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

J. Install identifying labels permanently attached to equipment.

K. Install operating instruction signs permanently attached to equipment or on pumping station wall near equipment.

L. Arrange for installing green detectable warning tape over outside edges of underground packaged sewage pumping stations.  Tape materials and their installation are specified in Division 31 Section "Earth Moving."

M. Prepare and paint ferrous piping in wet wells, structural-steel supports, and anchor devices with coal-tar epoxy-polyamide paint according to SSPC-Paint 16.

N. Paint field-welded areas to match factory coating.

3.2 FIELD QUALITY CONTROL

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. After installing packaged sewage pumping stations and after electrical circuitry has been energized, test for compliance with requirements.  Furnish water required for pump tests.

2. Leak Test:  After installation, charge systems and test for leaks.  Repair leaks and retest until no leaks exist.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace packaged sewage pumping stations that do not pass tests and inspections and retest as specified above.

3.3 STARTUP SERVICE

Retain this Article if factory-authorized service representative is required.

A. Engage a factory-authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Adjust pump, accessory, and control settings, and safety and alarm devices.

3. <Insert, in separate subparagraphs, startup steps.>

END OF SECTION 221343

	FACILITY PACKAGED SEWAGE PUMPING STATIONS
	221343 - 5



