Copyright 2005 AIA
MASTERSPEC Full Length
06/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221423 - STORM DRAINAGE PIPING SPECIALTIES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following storm drainage piping specialties:

Adjust list below to suit Project.

1. Backwater valves.

2. Cleanouts.

3. Trench drains.

4. Channel drainage systems.

5. Catch basins.

6. Through-penetration firestop assemblies.

7. Roof drains.

8. Miscellaneous storm drainage piping specialties.

9. Flashing materials.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 22 Section "Sanitary Waste Piping Specialties" for backwater valves, floor drains, trench drains and channel drainage systems connected to sanitary sewer, air admittance valves, FOG disposal systems, grease interceptors and removal devices, oil interceptors, and solid interceptors.

1.3 DEFINITIONS

Retain acronyms and abbreviations that remain after this Section has been edited.

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. FOG:  Fats, oils, and greases.

C. FRP:  Fiberglass-reinforced plastic.

D. HDPE:  High-density polyethylene plastic.

E. PE:  Polyethylene plastic.

F. PP:  Polypropylene plastic.

G. PUR:  Polyurethane plastic.

H. PVC:  Polyvinyl chloride plastic.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

1.5 QUALITY ASSURANCE

A. Drainage piping specialties shall bear label, stamp, or other markings of specified testing agency.

1.6 COORDINATION

Retain paragraph below if retaining base-mounting equipment.

A. Coordinate size and location of roof penetrations.

PART 2 -  PRODUCTS

2.1 BACKWATER VALVES

Copy and edit paragraph and subparagraphs below for each type of horizontal, cast-iron backwater valve required.  If only one type is required, drawing designation may be omitted.

A. Horizontal, Cast-Iron Backwater Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfr. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name.>

4. Standard:  ASME A112.14.1.

5. Size:  Same as connected piping.

6. Body:  Cast iron.

7. Cover:  Cast iron with [bolted] [or] [threaded] access check valve.

8. End Connections:  [Hub and spigot] [Hub and spigot or hubless] [Hubless].

9. Type Check Valve:  Removable, bronze, swing check, factory assembled or field modified to hang [closed] [open for airflow unless subject to backflow condition].

10. Extension:  ASTM A 74, Service class; full-size, cast-iron, soil-pipe extension to field-installed cleanout at floor; replaces backwater valve cover.

Copy and edit paragraph and subparagraphs below for each type of drain-outlet backwater valve required.  If only one type is required, drawing designation may be omitted.

B. Drain-Outlet Backwater Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Josam Company; Josam Div.

b. Smith, Jay R. Mfr. Co.; Division of Smith Industries, Inc.

c. Watts Drainage Products Inc.

d. Zurn Plumbing Products Group; Specification Drainage Operation.

e. <Insert manufacturer's name.>

3. Size:  Same as floor drain outlet.

4. Body:  Cast iron or bronze made for vertical installation in bottom outlet of floor drain.

5. Check Valve:  Removable ball float.

6. Inlet:  Threaded.

7. Outlet:  Threaded or spigot.

Floor drains with integral backwater valves are specified as floor drains.

Copy and edit paragraph and subparagraphs below for each type of horizontal, plastic backwater valve required.  If only one type is required, drawing designation may be omitted.

Plastic backwater valves in paragraph below are available in NPS 2 to NPS 6 (DN 50 to DN 150).  Most are made of PVC.

C. Horizontal, Plastic Backwater Valves <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Canplas LLC.

b. IPS Corporation.

c. NDS Inc.

d. Oatey.

e. Plastic Oddities; a division of Diverse Corporate Technologies.

f. Sioux Chief Manufacturing Company, Inc.

g. Zurn Plumbing Products Group; Light Commercial Operation.

h. <Insert manufacturer's name.>

3. Size:  Same as connected piping.

4. Body:  [ABS] [PVC].

5. Cover:  Same material as body with threaded access to check valve.

6. Check Valve:  Removable swing check.

7. End Connections:  Socket type.

2.2 CLEANOUTS

Copy and edit paragraph and subparagraphs below for each type of exposed metal cleanout required.  If only one type is required, drawing designation may be omitted.

A. Exposed Metal Cleanouts <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists of manufacturers below.

Manufacturers in list below are for ASME A112.36.2M, cast-iron cleanouts.

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name.>

Manufacturers in list below are for ASME A112.3.1, stainless-steel cleanouts.

h. Josam Company; Blucher-Josam Div.

i. <Insert manufacturer's name.>

4. Standard:  [ASME A112.36.2M for cast iron] [ASME A112.3.1 for stainless steel] <Insert standard> for cleanout test tee.

5. Size:  Same as connected drainage piping

6. Body Material:  [Hub-and-spigot, cast-iron soil pipe T-branch] [Hubless, cast-iron soil pipe test tee] [Stainless-steel tee with side cleanout] as required to match connected piping.

7. Closure:  [Countersunk] [Countersunk or raised-head] [Raised-head], [brass] [cast-iron] [plastic] plug.

8. Closure Plug Size:  Same as or not more than one size smaller than cleanout size.

Retain last two subparagraphs above for ASME A112.36.2M cleanouts or subparagraph below for ASME A112.3.1, stainless-steel cleanouts.

9. Closure:  Stainless-steel plug with seal.

Copy and edit paragraph and subparagraphs below for each type of metal floor cleanout required.  If only one type is required, drawing designation may be omitted.

B. Metal Floor Cleanouts <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists of manufacturers below.

Manufacturers in list below are for ASME A112.36.2M, cast-iron cleanouts.

a. Josam Company; Josam Div.

b. Oatey.

c. Sioux Chief Manufacturing Company, Inc.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Tyler Pipe; Wade Div.

f. Watts Drainage Products Inc.

g. Zurn Plumbing Products Group; Light Commercial Operation.

h. Zurn Plumbing Products Group; Specification Drainage Operation.

i. <Insert manufacturer's name.>

Manufacturers in list below are for ASME A112.36.2M, stainless-steel cleanouts.

j. Josam Company; Josam Div.

k. Kusel Equipment Co.

l. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

m. <Insert manufacturer's name.>

Manufacturers in list below are for ASME A112.3.1, stainless-steel cleanouts.

n. Josam Company; Blucher-Josam Div.

o. <Insert manufacturer's name.>

Retain 12 subparagraphs below for cast-iron or stainless-steel cleanouts complying with ASME A112.36.2M.

4. Standard:  ASME A112.36.2M for [adjustable housing] [cast-iron soil pipe with cast-iron ferrule] [heavy-duty, adjustable housing] [threaded, adjustable housing] cleanout.

5. Size:  Same as connected branch.

6. Type:  [Adjustable housing] [Cast-iron soil pipe with cast-iron ferrule] [Heavy-duty, adjustable housing] [Threaded, adjustable housing].

7. Body or Ferrule:  [Cast iron] [Stainless steel] <Insert material>.

8. Clamping Device:  [Not required] [Required].

9. Outlet Connection:  [Inside calk] [Spigot] [Threaded].

10. Closure:  [Brass plug with straight threads and gasket] [Brass plug with tapered threads] [Cast-iron plug] [Plastic plug].

11. Adjustable Housing Material:  [Cast iron] [Plastic] <Insert material> with [threads] [set-screws or other device].

12. Frame and Cover Material and Finish:  [Nickel-bronze, copper alloy] [Painted cast iron] [Polished bronze] [Rough bronze] [Stainless steel] <Insert material and finish>.

13. Frame and Cover Shape:  [Round] [Square] <Insert shape>.

14. Top Loading Classification:  [Extra Heavy-] [Heavy] [Light] [Medium] Duty.

15. Riser:  ASTM A 74, [Extra-Heavy] [Service] class, cast-iron drainage pipe fitting and riser to cleanout.

Retain five subparagraphs below for stainless-steel cleanouts complying with ASME A112.3.1.

16. Standard:  ASME A112.3.1.

17. Size:  Same as connected branch.

18. Housing:  Stainless steel.

19. Closure:  Stainless steel with seal.

20. Riser:  Stainless-steel drainage pipe fitting to cleanout.

Copy and edit paragraph and subparagraphs below for each type of cast-iron wall cleanout required.  If only one type is required, drawing designation may be omitted.

C. Cast-Iron Wall Cleanouts <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name.>

4. Standard:  ASME A112.36.2M.  Include wall access.

5. Size:  Same as connected drainage piping.

6. Body:  [Hub-and-spigot, cast-iron soil pipe T-branch] [Hubless, cast-iron soil pipe test tee] as required to match connected piping.

Option for drilled-and-threaded plug in first subparagraph below is for a screw for a wall cover plate.

7. Closure:  [Countersunk] [Countersunk or raised-head] [Raised-head], [drilled-and-threaded] [brass] [cast-iron] plug.

8. Closure Plug Size:  Same as or not more than one size smaller than cleanout size.

9. Wall Access:  Round, [deep, chrome-plated bronze] [flat, chrome-plated brass or stainless-steel] cover plate with screw.

Retain subparagraph above for cover plate or subparagraph below for frame and cover to be installed in drywall.

10. Wall Access:  [Round] [Square], [nickel-bronze, copper-alloy, or stainless-steel] <Insert material> wall-installation frame and cover.

Copy and edit paragraph and subparagraphs below for each type of plastic floor cleanout required.  If only one type is required, drawing designation may be omitted.

D. Plastic Floor Cleanouts <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Canplas LLC.

b. IPS Corporation.

c. NDS Inc.

d. Plastic Oddities; a division of Diverse Corporate Technologies.

e. Sioux Chief Manufacturing Company, Inc.

f. Zurn Plumbing Products Group; Light Commercial Operation.

g. <Insert manufacturer's name.>

3. Size:  Same as connected branch.

4. Body:  PVC.

5. Closure Plug:  PVC.

6. Riser:  Drainage pipe fitting and riser to cleanout of same material as drainage piping.

2.3 TRENCH DRAINS

Copy and edit paragraph and subparagraphs below for each type of trench drain required.  If only one type is required, drawing designation may be omitted.

A. Trench Drains <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Josam Company; Josam Div.

b. MIFAB, Inc.

c. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

d. Tyler Pipe; Wade Div.

e. Watts Drainage Products Inc.

f. Zurn Plumbing Products Group; Specification Drainage Operation.

g. <Insert manufacturer's name.>

4. Standard:  ASME A112.6.3 for trench drains.

5. Material:  Ductile or gray iron.

6. Flange:  [Anchor] [Seepage] [Not required].

7. Clamping Device:  [Not required] [Required].

8. Outlet:  [Bottom] [End] [Side] <Insert location>.

9. Grate Material:  [Ductile iron] [Ductile iron or gray iron] [Gray iron] [Stainless steel] <Insert material>.

10. Grate Finish:  [Painted] [Not required] <Insert finish>.

11. Dimensions of Frame and Grate:  <Insert dimensions and describe body, sump, and grate if required.>

12. Top Loading Classification:  [Extra Heavy-Duty] [Heavy Duty] [Light Duty] [Medium Duty] <Delete if not applicable>.

13. Trap Material:  [Cast iron] [Stainless steel] [Not required] <Insert material>.

14. Trap Pattern:  [Standard P-trap] [Not required] <Insert pattern>.

2.4 CHANNEL DRAINAGE SYSTEMS

Copy and edit paragraph and subparagraphs below for each type of stainless-steel channel drainage system required.  If only one type is required, drawing designation may be omitted.

A. Stainless-Steel Channel Drainage Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists of manufacturers below.

Manufacturers in list below are for ASME A112.3.1, stainless-steel channel drainage systems.

a. Josam Company; Blucher-Josam Div.

b. <Insert manufacturer's name.>

Manufacturers in list below are for non-ASME A112.3.1, stainless-steel channel drainage systems.

c. MultiDrain Systems.

d. Zurn Plumbing Products Group; Flo-Thru Operation.

e. <Insert manufacturer's name.>

Retain subparagraph and associated subparagraphs below for ASME A112.3.1, stainless-steel channel drainage systems.

4. Type:  Modular system of stainless-steel channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

a. Standard:  ASME A112.3.1, for trench drains.

b. Channel Sections:  Interlocking-joint, stainless-steel with level invert.

1) Dimensions:  [5.8 inches (147 mm)] [11.7 inches (297mm)] wide.  Include number of units required to form total lengths indicated.

c. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channels.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

d. Covers:  Solid [ductile or gray iron] [stainless steel] <Insert material>, of width and thickness that fit recesses in channels, and of lengths indicated.

e. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

f. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Retain subparagraph and associated subparagraphs below for non-ASME A112.3.1, stainless-steel channel drainage systems.

5. Type:  Modular system of stainless-steel channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

a. Channel Sections:  Interlocking-joint, stainless steel with level invert.

1) Dimensions:  [6 inches (152 mm)] [12 inches (305 mm)] wide.  Include number of units required to form total lengths indicated.

b. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channels.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

c. Covers:  Solid [ductile or gray iron] [stainless steel] <Insert material>, of width and thickness that fit recesses in channels, and of lengths indicated.

d. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

e. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Copy and edit paragraph and subparagraphs below for each type of polymer-concrete channel drainage system required.  If only one type is required, drawing designation may be omitted.

B. Polymer-Concrete Channel Drainage Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists of manufacturers below.

Manufacturers in list below are for narrow, sloped-invert, polymer-concrete channel drainage systems.

a. ABT, Inc.

b. ACO Polymer Products, Inc.

c. Forte Composites, Inc.

d. Josam Company; Mea-Josam Div.

e. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

f. Strongwell Corporation; Lenoir City Division.

g. <Insert manufacturer's name.>

Manufacturers in list below are for narrow, level-invert, polymer-concrete channel drainage systems.

h. ABT, Inc.

i. ACO Polymer Products, Inc.

j. Forte Composites, Inc.

k. Josam Company; Mea-Josam Div.

l. <Insert manufacturer's name.>

Manufacturers in list below are for wide, level-invert, polymer-concrete channel drainage systems.

m. ABT, Inc.

n. ACO Polymer Products, Inc.

o. Josam Company; Mea-Josam Div.

p. Strongwell Corporation; Lenoir City Division.

q. <Insert manufacturer's name.>

4. Type:  Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

Retain one of three "Channel Sections" subparagraphs and associated subparagraphs below.

Retain subparagraph and associated subparagraphs below for narrow, sloped-invert, polymer-concrete channel drainage systems.

a. Channel Sections:  Narrow, interlocking-joint, sloped-invert, polymer-concrete modular units with end caps.  Include rounded bottom, with built-in invert slope of 0.6 percent and with outlets in number, sizes, and locations indicated.  Include extension sections necessary for required depth.

1) Dimensions:  4-inch (102-mm) inside width.  Include number of units required to form total lengths indicated.

2) Frame:  [Gray-iron or galvanized steel for grates] [Not required].

b. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

c. Covers:  Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

d. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

e. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Retain subparagraph and associated subparagraphs below for narrow, level-invert, polymer-concrete channel drainage systems.

f. Channel Sections:  Narrow, interlocking-joint, precast, polymer-concrete modular units with end caps.  Include rounded bottom, with level invert and with NPS 4 (DN 100) outlets in number and locations indicated.

1) Dimensions:  [5-inch (127-mm)] <Insert dimension> inside width and [9-3/4 inches (248 mm)] <Insert dimension> deep.  Include number of units required to form total lengths indicated.

2) Frame:  [Gray-iron or galvanized steel for grates] [Not required].

g. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

h. Covers:  Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

i. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

j. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Retain subparagraph and associated subparagraphs below for wide, level-invert, polymer-concrete channel drainage systems.

k. Channel Sections:  Wide, interlocking-joint, precast, polymer-concrete modular units with end caps.  Include flat or rounded bottom, with level invert and with outlets in number, sizes, and locations indicated.

1) Dimensions:  [8-inch (203-mm)] <Insert dimension> inside width and [13-3/4 inches (350 mm)] <Insert dimension> deep.  Include number of units required to form total lengths indicated.

2) Frame:  [Gray-iron or galvanized steel for grates] [Not required].

l. Grates:  Manufacturer's designation "[heavy] [medium] duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

1) Material:  [Ductile iron] [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

Show locations and lengths of covers on Drawings.

m. Covers:  Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

n. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

o. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Copy and edit paragraph and subparagraphs below for each type of FRP channel drainage system required.  If only one type is required, drawing designation may be omitted.

C. FRP Channel Drainage Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. ACO Polymer Products, Inc.

b. Aquaduct, Inc.; an ACO Polymer Products, Inc. Company.

c. Josam Company; Mea-Josam Div.

d. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

e. Zurn Plumbing Products Group; Flo-Thru Operation.

f. <Insert manufacturer's name.>

4. Description:  Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

a. Channel Sections:  Interlocking-joint, sloped-invert, FRP modular units, with end caps.  Include flat, rounded, or inclined inside bottom, with outlets in number, sizes, and locations indicated.

1) Dimensions:  [4 inches (102 mm)] [4 or 6 inches (102 or 152 mm)] [6 inches (152 mm)] [6 or 8 inches (152 or 203 mm)] [8 inches (203 mm)] wide.  Include number of units required to form total lengths indicated.

2) Frame:  [Galvanized steel] [Stainless steel] [Manufacturer's standard metal] <Insert material> for grates.

b. Grates:  With slots or perforations and widths and thickness that fit recesses in channel sections.

1) Material:  [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Locking Mechanism:  [Manufacturer's standard device for securing grates to channel sections] [Not required].

c. Covers:  Solid [ductile or gray iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

d. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

e. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

Copy and edit paragraph and subparagraphs below for each type of plastic channel drainage system required.  If only one type is required, drawing designation may be omitted.

D. Plastic Channel Drainage Systems <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of four lists of manufacturers below.

Manufacturers in list below are for HDPE or PE channel drainage systems.

a. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

b. Tuf-Tite Corporation.

c. Zurn Plumbing Products Group; Flo-Thru Operation.

d. <Insert manufacturer's name.>

Manufacturers in list below are for PP channel drainage systems.

e. Infinity Plastics, Inc.

f. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

g. <Insert manufacturer's name.>

Manufacturers in list below are for PVC channel drainage systems.

h. MultiDrain Systems.

i. NDS Inc.

j. <Insert manufacturer's name.>

Manufacturers in list below are for HDPE, PE, PP, or PVC channel drainage systems.

k. Infinity Plastics, Inc.

l. MultiDrain Systems.

m. NDS Inc.

n. Smith, Jay R. Mfg Co.; Division of Smith Industries, Inc.

o. Tuf-Tite Corporation.

p. Zurn Plumbing Products Group; Flo-Thru Operation.

q. <Insert manufacturer's name.>

4. Type:  Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

a. Channel Sections:  Interlocking-joint, [HDPE or PE] [PP] [or] [PVC] modular units,  with end caps.  Include flat, rounded, or inclined bottom, with level invert and with outlets in number, sizes, and locations indicated.

1) Dimensions:  4 inches (102 mm) wide.  Include number of units required to form total lengths indicated.

b. Grates:  With slots or perforations and widths and thickness that fit recesses in channel sections.

1) Material:  [Fiberglass] [Galvanized steel] [Gray iron] [Stainless steel] <Insert material>.

2) Color:  <Insert color or delete subparagraph.>

c. Supports, Anchors, and Setting Devices:  Manufacturer's standard, unless otherwise indicated.

d. Channel-Section Joining and Fastening Materials:  As recommended by system manufacturer.

2.5 CATCH BASINS

Copy and edit paragraph and subparagraphs below for each type of polymer-concrete catch basin required.  If only one type is required, drawing designation may be omitted.

A. Polymer-Concrete Catch Basins <Insert drawing designation if any>:

Revise two subparagraphs below to suit Project.

1. Description:  [24-by-12-inch (610-by-305-mm)] [19- to 24-inch by about 6-inch (483- to 610-mm by about 152-mm)] <Insert dimensions> precast, polymer-concrete body, with outlets in number and sizes indicated.  Include gray-iron slotted grate.

2. Frame:  [Gray-iron or galvanized steel for grate] [Not required].

Copy and edit paragraph and subparagraph below for each type of FRP catch basin required.  If only one type is required, drawing designation may be omitted.

B. FRP Catch Basins <Insert drawing designation if any>:

1. Description:  [12-by-24-inch (305-by-610-mm)] [24-inch- (610-mm-) square] body, with outlets in number and sizes indicated.  Include[ gray-iron frame and] slotted grate.

Copy and edit paragraph and subparagraph below for each type of HDPE or PE catch basin required.  If only one type is required, drawing designation may be omitted.

C. HDPE or PE Catch Basins <Insert drawing designation if any>:

1. Description:  12-inch- (305-mm-) square body, with outlets in number and sizes indicated.  Include PE slotted grate 11-3/4 inches (298 mm) square by 1-1/8 inches (28.6 mm) thick.

2.6 THROUGH-PENETRATION FIRESTOP ASSEMBLIES

Copy and edit paragraph and subparagraphs below for each type of through-penetration firestop assembly required.  If only one type is required, drawing designation may be omitted.

A. Through-Penetration Firestop Assemblies <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. ProSet Systems Inc.

b. <Insert manufacturer's name.>

3. Standard:  UL 1479 assembly of sleeve and stack fitting with firestopping plug.

4. Size:  Same as connected pipe.

5. Sleeve:  Molded PVC plastic, of length to match slab thickness and with integral nailing flange on one end for installation in cast-in-place concrete slabs.

Fitting in subparagraph below is for use with plastic stacks.

6. Stack Fitting:  ASTM A 48/A 48M, gray-iron, hubless-pattern, wye branch with neoprene O-ring at base and gray-iron plug in thermal-release harness.  Include PVC protective cap for plug.

Coating in subparagraph below is for use with corrosion-resistant plastic stacks.

7. Special Coating:  Corrosion resistant on interior of fittings.

2.7 ROOF DRAINS

Copy and edit paragraph and subparagraphs below for each type of metal roof drain required.  If only one type is required, drawing designation may be omitted.

A. Metal Roof Drains <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists of manufacturers below.

Manufacturers in list below are for aluminum roof drains.

a. Olympic Manufacturing Group.

b. Portals Plus, Inc.

c. Thaler Metal Industries Ltd.

d. <Insert manufacturer's name.>

Manufacturers in list below are for cast-iron roof drains.

e. Josam Company; Josam Div.

f. Marathon Roofing Products.

g. MIFAB, Inc.

h. Portals Plus, Inc.

i. Prier Products, Inc.

j. Smith, Jay R. Mfg. Co.; Division of Smith Industries, Inc.

k. Tyler Pipe; Wade Div.

l. Watts Drainage Products Inc.

m. Zurn Plumbing Products Group; Light Commercial Operation.

n. Zurn Plumbing Products Group; Specification Drainage Operation.

o. <Insert manufacturer's name.>

Manufacturers in list below are for copper roof drains.

p. LSP Products Group, Inc.

q. Marathon Roofing Products.

r. Olympic Manufacturing Group.

s. Thaler Metal Industries Ltd.

t. Thunderbird Products.

u. <Insert manufacturer's name.>

4. Standard:  ASME A112.21.2M.

5. Pattern:  [Balcony] [Canopy] [Cornice] [Promenade-deck] [Roof] [Scupper] <Insert pattern> drain.

6. Body Material:  [Aluminum] [Cast iron] [Copper] <Insert material>.

7. Dimensions of Body:  <Insert dimensions and describe body and sump if required.>

8. Combination Flashing Ring and Gravel Stop:  [Not required] [Required] <Insert other>.

9. Flow-Control Weirs:  [Not required] [Required].

10. Outlet:  [Bottom] [Side] [Angle] <Insert outlet>.

11. Dome Material:  [Aluminum] [Cast iron] [PE] [Stainless steel] <Insert material>.

12. Extension Collars:  [Not required] [Required].

13. Underdeck Clamp:  [Not required] [Required].

14. Sump Receiver:  [Not required] [Required].

Copy and edit paragraph and subparagraphs below for each type of plastic roof drain required.  If only one type is required, drawing designation may be omitted.

B. Plastic Roof Drains <Insert drawing designation if any>:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Canplas LLC.

b. LSP Products Group, Inc.

c. Marathon Roofing Products.

d. Olympic Manufacturing Group.

e. Plastic Oddities; a division of Diverse Corporate Technologies.

f. Portals Plus, Inc.

g. Sioux Chief Manufacturing Company, Inc.

h. Town & Country Plastics, Inc.

i. Zurn Plumbing Products Group; Light Commercial Operation.

j. <Insert manufacturer's name.>

4. Standard:  ASME A112.21.2M.

5. Pattern:  [Balcony] [Canopy] [Roof] [Scupper] <Insert pattern> drain.

6. Body Material:  [ABS] [ABS or PVC] [PVC] [PUR] <Insert material>.

7. Dimensions of Body:  <Insert dimensions and describe body and sump, or delete subparagraph.>

8. Combination Flashing Ring and Gravel Stop:  [Not required] [Required] <Insert other>.

9. Outlet:  [Bottom] [Side] [Angle] <Insert outlet>.

10. Dome Material:  [ABS] [ABS or PVC] [PVC] [PUR] <Insert material>.

11. Underdeck Clamp:  [Not required] [Required].

2.8 MISCELLANEOUS STORM DRAINAGE PIPING SPECIALTIES

Copy and edit paragraph and subparagraphs below for each type of expansion joint required.  If only one type is required, drawing designation may be omitted.

A. Expansion Joints <Insert drawing designation if any>:

1. Standard:  ASME A112.21.2M.

2. Body:  Cast iron with bronze sleeve, packing, and gland.

3. End Connections:  Matching connected piping.

4. Size:  Same as connected piping.

Copy and edit paragraph and subparagraphs below for each type of downspout boot required.  If only one type is required, drawing designation may be omitted.

B. Downspout Boots <Insert drawing designation if any>:

Boots in first subparagraph below are available with inlet dimensions of 4 by 3 inches (102 by 76 mm), 5 by 4 inches (127 by 102 mm), and 4 inches (102 mm) in diameter.  Outlet is NPS 4 (DN 100).

1. Description:  Manufactured, ASTM A 48/A 48M, gray-iron casting, with strap or ears for attaching to building; NPS 4 (DN 100) outlet; and shop-applied bituminous coating.

2. Size:  Inlet size to match downspout.

Retain two subparagraphs above or below.

Boots in first subparagraph below are available in NPS 2 to NPS 10 (DN 50 to DN 250).

3. Description:  ASTM A 74, Service class, hub-and-spigot, cast-iron soil pipe.

4. Size:  Same as or larger than connected downspout.

Copy and edit paragraph and subparagraphs below for each type of conductor nozzle required.  If only one type is required, drawing designation may be omitted.

Conductor nozzles in paragraph below are available in NPS 2 to NPS 10 (DN 50 to DN 250).

C. Conductor Nozzles <Insert drawing designation if any>:

1. Description:  Bronze body with threaded inlet and bronze wall flange with mounting holes.

2. Size:  Same as connected conductor.

2.9 FLASHING MATERIALS

Coordinate this Article with Division 07 Sections "Sheet Metal Flashing and Trim" and "Roof Accessories."  Delete Article if all required materials are specified in Division 07 Sections.

Coordinate first two paragraphs below with Division 07 Section "Sheet Metal Flashing and Trim" if used for drainage receptors.

A. Copper Sheet:  ASTM B 152/B 152M, 12 oz./sq. ft. (3.7 kg/sq. m or 0.41-mm) thickness.

B. Zinc-Coated Steel Sheet:  ASTM A 653/A 653M, with 0.20 percent copper content and 0.04-inch (1.01-mm) minimum thickness, unless otherwise indicated.  Include G90 (Z275) hot-dip galvanized, mill-phosphatized finish for painting if indicated.

C. Elastic Membrane Sheet:  ASTM D 4068, flexible, chlorinated polyethylene, 40-mil (1.01-mm) minimum thickness.

D. Fasteners:  Metal compatible with material and substrate being fastened.

E. Metal Accessories:  Sheet metal strips, clamps, anchoring devices, and similar accessory units required for installation; matching or compatible with material being installed.

F. Solder:  ASTM B 32, lead-free alloy.

G. Bituminous Coating:  SSPC-Paint 12, solvent-type, bituminous mastic.

PART 3 -  EXECUTION

3.1 INSTALLATION

In this Article, retain only those storm drainage piping specialties that are specified in Part 2.  Additional instructions may be required for special applications.  Show locations of specialties in plans, details, and schematics on Drawings.

A. Refer to Division 22 Section "Common Work Results for Plumbing" for piping joining materials, joint construction, and basic installation requirements.

B. Install cleanouts in aboveground piping and building drain piping according to the following, unless otherwise indicated:

1. Size same as drainage piping up to NPS 4 (DN 100).  Use NPS 4 (DN 100) for larger drainage piping unless larger cleanout is indicated.

2. Locate at each change in direction of piping greater than 45 degrees.

3. Locate at minimum intervals of 50 feet (15 m) for piping NPS 4 (DN 100) and smaller and 100 feet (30 m) for larger piping.

4. Locate at base of each vertical soil and waste stack.

C. For floor cleanouts for piping below floors, install cleanout deck plates with top flush with finished floor.

D. For cleanouts located in concealed piping, install cleanout wall access covers, of types indicated, with frame and cover flush with finished wall.

E. Install trench drains at low points of surface areas to be drained.  Set grates of drains flush with finished surface, unless otherwise indicated.

Retain one of first two paragraphs below.

F. Assemble and install ASME A112.3.1, stainless-steel channel drainage systems according to ASME A112.3.1.  Install on support devices so that top will be flush with surface.

G. Assemble non-ASME A112.3.1, stainless-steel channel drainage system components according to manufacturer's written instructions.  Install on support devices so that top will be flush with adjacent surface.

H. Assemble FRP channel drainage system components according to manufacturer's written instructions.  Install on support devices so that top will be flush with adjacent surface.

I. Assemble plastic channel drainage system components according to manufacturer's written instructions.  Install on support devices so that top will be flush with adjacent surface.

Retain one of first two paragraphs below.

J. Install through-penetration firestop assemblies in plastic [conductors] [and] [stacks] at floor penetrations.

K. Install roof drains at low points of roof areas according to roof membrane manufacturer's written installation instructions.  Roofing materials are specified in Division 07.

1. Install roof-drain flashing collar or flange so that there will be no leakage between drain and adjoining roofing.  Maintain integrity of waterproof membranes where penetrated.

2. Position roof drains for easy access and maintenance.

L. Install sleeve flashing device with each riser and stack passing through floors with waterproof membrane.

M. Install expansion joints on vertical stacks and conductors.  Position expansion joints for easy access and maintenance.

N. Install manufactured, gray-iron downspout boots at grade with top [6 inches (152 mm)] [12 inches (305 mm)] [18 inches (457 mm)] <Insert dimension> above grade.  Secure to building wall.

O. Install cast-iron soil pipe downspout boots at grade with top of hub [6 inches (152 mm)] [12 inches (305 mm)] [18 inches (457 mm)] <Insert dimension> above grade.

P. Install conductor nozzles at exposed bottom of conductors where they spill onto grade.

Q. Install escutcheons at wall, floor, and ceiling penetrations in exposed finished locations and within cabinets and millwork.  Use deep-pattern escutcheons if required to conceal protruding pipe fittings.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 22 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

3.3 FLASHING INSTALLATION

Coordinate this Article with Division 07 Section "Sheet Metal Flashing and Trim."

A. Fabricate flashing from single piece unless large pans, sumps, or other drainage shapes are required.  Join flashing according to the following if required:

1. Lead Sheets:  Burn joints of lead sheets 6.0-lb/sq. ft. (30-kg/sq. m), 0.0938-inch (2.4-mm) thickness or thicker.  Solder joints of lead sheets 4.0-lb/sq. ft. (20-kg/sq. m), 0.0625-inch (1.6-mm) thickness or thinner.

2. Copper Sheets:  Solder joints of copper sheets.

B. Install sheet flashing on pipes, sleeves, and specialties passing through or embedded in floors and roofs with waterproof membrane.

1. Pipe Flashing:  Sleeve type, matching pipe size, with minimum length of 10 inches (250 mm), and skirt or flange extending at least 8 inches (200 mm) around pipe.

2. Sleeve Flashing:  Flat sheet, with skirt or flange extending at least 8 inches (200 mm) around sleeve.

3. Embedded Specialty Flashing:  Flat sheet, with skirt or flange extending at least 8 inches (200 mm) around specialty.

C. Set flashing on floors and roofs in solid coating of bituminous cement.

D. Secure flashing into sleeve and specialty clamping ring or device.

Coordinate paragraph below with Division 07 Section "Sheet Metal Flashing and Trim."

E. Fabricate and install flashing and pans, sumps, and other drainage shapes.

3.4 PROTECTION

A. Protect drains during remainder of construction period to avoid clogging with dirt or debris and to prevent damage from traffic or construction work.

B. Place plugs in ends of uncompleted piping at end of each day or when work stops.

END OF SECTION 221423

	STORM DRAINAGE PIPING SPECIALTIES
	221423 - 1



