Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
03/03 (R 06/05)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 223200 - DOMESTIC WATER FILTRATION EQUIPMENT
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following types of water filtration equipment for water systems in buildings:

Adjust list below to suit Project.

1. Bag-type filters.

2. Freestanding cartridge filters.

3. Off-floor cartridge filters.

4. Carbon filters.

5. Circulating sand filters.

6. Multimedia sand filters.

7. Greensand filters.

8. Separators.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 22 Section "Domestic Water Piping Specialties" for small cartridge-type water filters for plumbing fixtures and for plumbing piping strainers.

2. Division 23 Section "Hydronic Piping" for hydronic piping strainers.

3. Division 23 Section "Steam and Condensate Heating Piping" for steam piping system strainers.

4. Division 23 Section "HVAC Water Treatment" for HVAC condenser water filtration units and hot-water/chilled-water filtration units.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. ABS:  Acrylonitrile-butadiene-styrene plastic.

B. FRP:  Fiberglass-reinforced plastic.

C. NBR:  Acrylonitrile-butadiene rubber.

D. PE:  Polyethylene plastic.

E. PP:  Polypropylene plastic.

F. ppm:  Parts per million.

G. PVC:  Polyvinyl chloride plastic.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

Retain paragraph below only for multiple-filter systems using carbon or sand filters or separators.

B. Shop Drawings:  Detail water filtration equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain subparagraph below if equipment includes wiring.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph below only if required.

C. Certificates of Shop Inspections and Data Reports:  For products required to have ASME label, signed by product manufacturer.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

D. Welding certificates.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 22 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment."

E. Manufacturer Seismic Qualification Certification:  Submit certification that water filtration equipment, accessories, and components will withstand seismic forces defined in Division 22 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

F. Source quality-control test reports.

Retain paragraph below if Contractor is responsible for field quality-control testing.

G. Field quality-control test reports.

Retain first paragraph below if Contractor is responsible for startup service test reports.

H. Startup service test reports.

I. Operation and Maintenance Data:  For water filtration equipment to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Source Limitations:  Obtain each type of water filtration equipment through one source from a single manufacturer.

Retain paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 01 requirements.

B. Product Options:  Drawings indicate size, profiles, and dimensional requirements of water filtration equipment and are based on the specific system indicated.  Refer to Division 01 Section "Product Requirements."

Delete first paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

C. Welding:  Qualify processes and operators according to ASME Boiler and Pressure Vessel Code:  Section IX.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with NSF 61, "Drinking Water System Components - Health Effects; Sections 1 through 9," for all components that will be in contact with potable water.

1.6 PROJECT CONDITIONS

Delete first paragraph and subparagraphs below if no interruption of existing water service is required.

A. Interruption of Existing Water Service:  Do not interrupt water service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary water service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of water service.

2. Do not proceed with interruption of water service without [Architect's] [Construction Manager's] [Owner's] written permission.

B. Feedwater Analysis:

1. Alkalinity:  <Insert ppm (mg/L).>

2. Arsenic:  <Insert ppm (mg/L).>

3. Calcium:  <Insert ppm (mg/L).>

4. Chlorine:  <Insert ppm (mg/L).>

5. Color:  <Insert nephelometric turbidity units.>

6. Hydrogen-Ion Concentration:  <Insert pH.>

7. Hardness:  <Insert ppm (mg/L).>

8. Hydrogen Sulfide:  <Insert ppm (mg/L).>

9. Iron:  <Insert ppm (mg/L).>

10. Lead:  <Insert ppm (mg/L).>

11. Magnesium:  <Insert ppm (mg/L).>

12. Manganese:  <Insert ppm (mg/L).>

13. Potassium:  <Insert ppm (mg/L).>

14. Sand:  <Insert ppm (mg/L).>

15. Silt:  <Insert ppm (mg/L).>

16. Sodium:  <Insert ppm (mg/L).>

17. Total Dissolved Solids:  <Insert ppm (mg/L).>

18. Turbidity:  <Insert ppm (mg/L).>

19. <Insert characteristic>:  <Insert value.>

C. Feedwater Properties:

1. Inlet Water Pressure:  <Insert psig (kPa).>

2. Water Temperature:  <Insert deg F (deg C).>

1.7 COORDINATION

A. Coordinate size and location of concrete bases with Architectural and Structural Drawings.

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Bag-Type Filter Bags:  Bags for bag-type filters equal to [200] [400] <Insert number> percent of amount installed for each size and media indicated.

2. Cartridge-Filter Elements:  Elements for cartridge filters equal to [200] [400] <Insert number> percent of amount installed for each size and media indicated.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 BAG-TYPE FILTERS

Refer to the tables for water filtration equipment at the end of the Evaluations for lists of manufacturers' products.  Use these tables in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Single-Bag-Type Filters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Cycron Corporation.

b. Eden Equipment Co.

c. Filter Specialists, Inc.

d. Filtration Systems; div. of Mechanical Mfg. Corporation.

e. Hayward Industrial Products, Inc.

f. Krystal Klear Technologies, Inc.; a div. of Geyer's Mfr. & Design, Inc.

g. Parker Hannifin Corporation; Process Filtration Div.

h. PEP Filters, Inc.

i. Rosedale Products, Inc.

j. RPA Process Technologies.

k. Shelco Filters; division of Tinny Corp.

l. USFilter.

m. <Insert manufacturer's name.>

2. Description:  Simplex, floor-mounting housing with filter bag for removing suspended particles from water.

a. Housing:  Corrosion resistant; designed to separate feedwater from filtrate and to direct feedwater through one bag-type water filter; with bag support and base, feet, or skirt.

1) Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

2) Steel Housing Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Steel, Class 150 flanges according to ASME B16.5 or grooved according to AWWA C606.  Provide stainless-steel flanges if housing is stainless steel.

3) Plastic Housing Pipe Connections NPS 2-1/2 (DN 65) and Larger:  150-psig (1035-kPa) plastic flanges.

b. Bag:  Replaceable; of shape to fit housing.

If more than one single-bag-type filter is required on Project, delete subparagraph and associated subparagraphs below and schedule bag-type filters on Drawings.

3. Capacity and Characteristics:

a. Filtrate Design Concentrations:

Retain only required data in list below; add other data as needed.

1) Alkalinity:  <Insert ppm (mg/L).>

2) Chlorine:  <Insert ppm (mg/L).>

3) Color:  <Insert nephelometric turbidity units.>

4) Hydrogen Sulfide:  <Insert ppm (mg/L).>

5) Iron:  <Insert ppm (mg/L).>

6) Manganese:  <Insert ppm (mg/L).>

7) Sand:  <Insert ppm (mg/L).>

8) Silt:  <Insert ppm (mg/L).>

9) Turbidity:  <Insert ppm (mg/L).>

10) <Insert characteristic>:  <Insert value.>

b. Filter Design:

1) Continuous Flow:  <Insert gpm (L/s).>

2) Peak Flow:  <Insert gpm (L/s).>

3) Filtration Efficiency:  [98] <Insert number> percent retention of suspended particles [10] [20] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

4) Pressure Drop:  Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean[, and <Insert value> when dirty].

c. Housing:

1) Material:  [Carbon steel with NSF 61 lining material] [Plastic] [Stainless steel].

2) Pressure Rating:  <Insert psig (kPa).>

3) Seals:  [NBR] <Insert material>.

4) Diameter:  <Insert inches (mm).>

5) Height or Length:  <Insert inches (mm).>

6) Inlet and Outlet Size:  <Insert NPS (DN).>

7) Drain Size:  [Not applicable] <Insert NPS (DN)>.

8) Bag Support:  Top lock ring and perforated [stainless-steel] <Insert material> basket.

d. Bag:

1) Nominal Diameter:  <Insert inches (mm).>

2) Nominal Length:  <Insert inches (mm).>

3) Media:  [Cotton] [Polyester] [PP] <Insert material>; [felt, filament, or mesh] [felt] [filament] [mesh] construction.

B. Multiple-Bag-Type Filters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Filter Specialists, Inc.

b. Hayward Industrial Products, Inc.

c. Krystal Klear Technologies, Inc.; a div. of Geyer's Mfr. & Design, Inc.

d. Parker Hannifin Corporation; Process Filtration Div.

e. PEP Filters, Inc.

f. Rosedale Products, Inc.

g. RPA Process Technologies.

h. Shelco Filters; division of Tinny Corp.

i. <Insert manufacturer's name.>

2. Description:  Simplex, floor-mounting housing with multiple filter bags for removing suspended particles from water.

a. Housing:  Corrosion resistant; designed to separate feedwater from filtrate and to direct feedwater through bag-type water filters; with bag supports and base, feet, or skirt.

1) Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

2) Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Steel, Class 150 flanges according to ASME B16.5 or grooved according to AWWA C606.  Provide stainless-steel flanges if housing is stainless steel.

3) Plastic Housing Pipe Connections NPS 2-1/2 (DN 65) and Larger:  150-psig (1035-kPa) plastic flanges.

b. Bags:  Replaceable; of shape to fit housing.

If more than one multiple-bag-type filter is required on Project, delete subparagraph and associated subparagraphs below and schedule bag-type filters on Drawings.

3. Capacity and Characteristics:

a. Filtrate Design Concentrations:

Retain only required data in list below; add other data as needed.

1) Alkalinity:  <Insert ppm (mg/L).>

2) Chlorine:  <Insert ppm (mg/L).>

3) Color:  <Insert nephelometric turbidity units.>

4) Hydrogen Sulfide:  <Insert ppm (mg/L).>

5) Iron:  <Insert ppm (mg/L).>

6) Manganese:  <Insert ppm (mg/L).>

7) Sand:  <Insert ppm (mg/L).>

8) Silt:  <Insert ppm (mg/L).>

9) Turbidity:  <Insert ppm (mg/L).>

10) <Insert characteristic>:  <Insert value.>

b. Filter Design:

1) Continuous Flow:  <Insert gpm (L/s).>

2) Peak Flow:  <Insert gpm (L/s).>

3) Filtration Efficiency:  [98] <Insert number> percent retention of suspended particles [10] [20] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

4) Pressure Drop:  Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean[, and <Insert value> when dirty].

c. Housing:

1) Material:  [Carbon steel with NSF 61 lining material] [Plastic] [Stainless steel].

2) Pressure Rating:  <Insert psig (kPa).>

3) Seals:  [NBR] <Insert material>.

4) Diameter:  <Insert inches (mm).>

5) Height or Length:  <Insert inches (mm).>

6) Inlet and Outlet Size:  <Insert NPS (DN).>

7) Drain Size:  [Not applicable] <Insert NPS (DN)>.

8) Bag Support(s):  Top lock rings and perforated [stainless-steel] <Insert material> basket(s).

d. Bags:

1) Number Required:  <Insert number.>

2) Nominal Diameter:  <Insert inches (mm).>

3) Nominal Length:  <Insert inches (mm).>

4) Media:  [Cotton] [Polyester] [PP] <Insert material>; [felt, filament, or mesh] [felt] [filament] [mesh] construction.

2.3 CARTRIDGE FILTERS

Refer to the tables for water filtration equipment at the end of the Evaluations for lists of manufacturers' products.  Use these tables in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Freestanding Cartridge Filters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Campbell Manufacturing, Inc.

b. Cycron Corporation.

c. Diamond Water Conditioning.

d. Eden Equipment Co.

e. Filter Specialists, Inc.

f. Filterspun; a div. of Service Filtration Corp.

g. Filtrine Manufacturing Company; Drinking Water Division.

h. Flowmatic Systems, Inc.

i. Graver Technologies; Liquid Filter Products.

j. Harmsco Filtration Products.

k. Hydro Systems International.

l. Keystone Filter Div.; Met-Pro Corporation.

m. Krystal Klear Technologies, Inc.; a div. of Geyer's Mfr. & Design, Inc.

n. Osmonics, Inc.; Hytrex Filters Div.

o. Parker Hannifin Corporation; Process Filtration Div.

p. PEP Filters, Inc.

q. Rosedale Products, Inc.

r. Serfilco, Ltd.

s. Shelco Filters; division of Tinny Corp.

t. USFilter.

u. WET Products and Systems.

v. <Insert manufacturer's name.>

2. Description:  Simplex, floor-mounting housing with replaceable element(s) for removing suspended particles from water.

a. Housing:  Corrosion resistant; designed to separate feedwater from filtrate and to direct feedwater through water filter element(s); with element support(s) and base, feet, or skirt.

Retain first subparagraph below for projects in seismic areas.

1) Fabricate supports and base, feet, or skirt and attachment to housing with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

2) Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

3) Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Steel, Class 150 flanges according to ASME B16.5 or grooved according to AWWA C606.  Provide stainless-steel flanges if housing is stainless steel.

4) Plastic Housing Pipe Connections NPS 2-1/2 (DN 65) and Larger:  150-psig (1035-kPa) plastic flanges.

b. Element(s):  Replaceable; of shape to fit housing.

If more than one freestanding cartridge filter is required on Project, delete subparagraph and associated subparagraphs below and schedule cartridge filters on Drawings.

3. Capacity and Characteristics:

a. Filtrate Design Concentrations:

Retain only required data in list below; add other data as needed.

1) Alkalinity:  <Insert ppm (mg/L).>

2) Chlorine:  <Insert ppm (mg/L).>

3) Color:  <Insert nephelometric turbidity units.>

4) Hydrogen Sulfide:  <Insert ppm (mg/L).>

5) Iron:  <Insert ppm (mg/L).>

6) Manganese:  <Insert ppm (mg/L).>

7) Sand:  <Insert ppm (mg/L).>

8) Silt:  <Insert ppm (mg/L).>

9) Turbidity:  <Insert ppm (mg/L).>

10) <Insert characteristic>:  <Insert value.>

b. Filter Design:

1) Continuous Flow:  <Insert gpm (L/s).>

2) Peak Flow:  <Insert gpm (L/s).>

3) Filtration Efficiency:  [98] <Insert number> percent retention of suspended particles [1] [10] [20] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

4) Pressure Drop:  Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean[, and <Insert value> when dirty].

c. Housing:

1) Material:  [Plastic] [Stainless steel] <Insert material>.

2) Pressure Rating:  <Insert psig (kPa).>

3) Seals:  [NBR] <Insert material>.

4) Diameter:  <Insert inches (mm).>

5) Height or Length:  <Insert inches (mm).>

6) Inlet and Outlet Size:  <Insert NPS (DN).>

7) Drain Size:  [Not applicable] <Insert NPS (DN)>.

d. Elements:

1) Number Required:  [One] [Two] <Insert number>.

2) Nominal Diameter:  <Insert inches (mm).>

3) Nominal Length:  <Insert inches (mm).>

4) Media:  [Activated charcoal] [Activated or ground charcoal] [Ground charcoal] [Pleated polyester] [Pleated polyester or PP] [Pleated PP] [Wound polyester] [Wound polyester or PP] [Wound PP] <Insert material>.

B. Off-Floor Cartridge Filters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alamo Water Treatment.

b. Campbell Manufacturing, Inc.

c. Culligan International Company.

d. Eagle Spring Filtration, Inc.

e. Eden Equipment Co.

f. Everpure, Inc.

g. Fairey Industrial Ceramics Ltd.

h. Filpro Corporation.

i. Filterspun; a div. of Service Filtration Corp.

j. Filtrine Manufacturing Company; Drinking Water Division.

k. Flint & Walling, Inc.; Subsidiary of Zoeller Co.

l. Flowmatic Systems, Inc.

m. Graver Technologies; Liquid Filter Products.

n. Harmsco Filtration Products.

o. Hydro Systems International.

p. Hydrotech, Inc.

q. Keystone Filter Div.; Met-Pro Corporation.

r. Matterhorn Filter Corporation.

s. Omnipure Filter Company.

t. Osmonics, Inc.; Hytrex Filters Div.

u. Parker Hannifin Corporation; Process Filtration Div.

v. Plymouth Products, Inc.

w. Shelco Filters; division of Tinny Corp.

x. Topway Global, Inc.

y. USFilter.

z. WET Products and Systems.

aa. WaterSoft; a div. of AMTROL Inc.

ab. Watts Premier.

ac. <Insert manufacturer's name.>

2. Description:  Simplex, [in-line] [wall-mounting] housing with replaceable element for removing suspended particles from water.

a. Housing:  Corrosion resistant; designed to separate feedwater from filtrate and to direct feedwater through water filter element; with element support.

1) Pipe Connections:  Threaded according to ASME B1.20.1.

Retain first subparagraph below only if filters are wall-mounting type.

2) Support:  Wall bracket.

b. Element:  Replaceable; of shape to fit housing.

If more than one off-floor cartridge filter is required on Project, delete subparagraph and associated subparagraphs below and schedule cartridge filters on Drawings.

3. Capacity and Characteristics:

a. Filtrate Design Concentrations:

Retain only required data in list below; add other data as needed.

1) Alkalinity:  <Insert ppm (mg/L).>

2) Chlorine:  <Insert ppm (mg/L).>

3) Color:  <Insert nephelometric turbidity units.>

4) Hydrogen Sulfide:  <Insert ppm (mg/L).>

5) Iron:  <Insert ppm (mg/L).>

6) Manganese:  <Insert ppm (mg/L).>

7) Sand:  <Insert ppm (mg/L).>

8) Silt:  <Insert ppm (mg/L).>

9) Turbidity:  <Insert ppm (mg/L).>

10) <Insert characteristic>:  <Insert value.>

b. Filter Design:

1) Continuous Flow:  <Insert gpm (L/s).>

2) Peak Flow:  <Insert gpm (L/s).>

3) Filtration Efficiency:  [98] <Insert number> percent retention of suspended particles [1] [10] [20] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

4) Pressure Drop:  Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean[, and <Insert value> when dirty].

c. Housing:

1) Material:  [PE or PP] [Plastic] [Stainless steel] <Insert material>.

2) Pressure Rating:  <Insert psig (kPa).>

3) Seals:  [NBR] <Insert material>.

4) Diameter:  <Insert inches (mm).>

5) Height or Length:  <Insert inches (mm).>

6) Inlet and Outlet Size:  <Insert NPS (DN).>

7) Drain Size:  [Not applicable] <Insert NPS (DN)>.

d. Element:

1) Nominal Diameter:  <Insert inches (mm).>

2) Nominal Length:  <Insert inches (mm).>

3) Media:  [Activated charcoal] [Activated or ground charcoal] [Ground charcoal] [Pleated polyester] [Pleated polyester or PP] [Pleated PP] [Wound polyester] [Wound polyester or PP] [Wound PP] <Insert material>.

2.4 CARBON FILTERS

Refer to the tables for water filtration equipment at the end of the Evaluations for lists of manufacturers' products.  Use these tables in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Description:  Simplex carbon filter, with media tank, media, and automatic backwash for [removing chlorine from] [and] [improving color, odor, and taste of] <Insert application> water.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alamo Water Treatment.

b. CSI; a division of Chandler Systems, Inc.

c. Culligan International Company.

d. CUNO Incorporated.

e. Diamond Water Conditioning.

f. EcoWater Systems, Inc.

g. Environmental Dynamics Corporation.

h. Marlo Incorporated.

i. PEP Filters, Inc.

j. RainSoft Div.; Aquion Partners L. P.

k. Separmatic Fluid Systems.

l. Springsoft International, Inc.

m. USFilter.

n. Water & Power Technologies, Inc.

o. Water Right.

p. WaterSoft; a div. of AMTROL Inc.

q. <Insert manufacturer's name.>

2. Media Tank:  Corrosion resistant with distribution system and media.

a. Construction:

Retain subparagraph below to require steel or stainless-steel tanks to be ASME labeled; delete for non-code construction.

1) Fabricate and label steel filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain subparagraph below to require FRP tanks to be ASME labeled; delete for non-code construction.

2) Fabricate and label FRP filter tanks to comply with ASME Boiler and Pressure Vessel Code:  Section X, if indicated.

Retain first subparagraph below for projects in seismic areas.

3) Fabricate supports and base and attachment to tank with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

4) Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

5) Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Steel, Class 150 flanges according to ASME B16.5 or grooved according to AWWA C606.  Provide stainless-steel flanges if tank is stainless steel.

6) FRP Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Type A, integral; Designation [E, 125-psig (0.862-MPa)] [or] [F, 150-psig (1.034-MPa)]pressure category flanges of grade same as tank material according to ASTM D 5421.

7) Support:  Base, feet, or skirt.

3. Controls:  Automatic for control of backwash; factory wired for single, external electrical connection.

a. Panel:  NEMA 250, Type [4] <Insert type> enclosure.

b. Backwash Initiation Device:  [Differential pressure gages] [Electric time clock] [Water meter].

If more than one carbon filter is required on Project, delete subparagraph and associated subparagraphs below and schedule carbon filters on Drawings.

4. Capacity and Characteristics:

a. Filtrate Design Concentrations:

Retain only required data in list below.  For public utility water, only chlorine concentration may be required.  For water from a well, all or most data listed below may be required.

1) Alkalinity:  <Insert ppm (mg/L).>

2) Chlorine:  <Insert ppm (mg/L).>

3) Color:  <Insert nephelometric turbidity units.>

4) Hydrogen-Ion Concentration:  <Insert pH.>

5) Hydrogen Sulfide:  <Insert ppm (mg/L).>

6) Iron:  <Insert ppm (mg/L).>

7) Manganese:  <Insert ppm (mg/L).>

8) Total Dissolved Solids:  <Insert ppm (mg/L).>

9) Turbidity:  <Insert ppm (mg/L).>

10) <Insert characteristic>:  <Insert value.>

b. Filter Design:

1) Continuous Flow:  <Insert gpm (L/s).>

2) Flow Rate:  <Insert gpm/sq. ft. (L/s per sq. m)> of media cross-sectional area.

3) Peak Flow:  <Insert gpm (L/s).>

4) Filtration Efficiency:  [98] <Insert number> percent retention of suspended particles [20] [40] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

5) Pressure Drop:  Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean[, and <Insert value> when dirty].

6) Backwash Flow:  <Insert gpm (L/s).>

Retain one of first three subparagraphs below to match backwash initiation device selected above.

c. Filter Backwash Interval:  <Insert psig (kPa)> pressure drop measured by differential pressure gages.

d. Filter Backwash Interval:  <Insert number> days measured by time clock.

e. Filter Backwash Interval:  <Insert gal. (cu. m)> measured by water meter.

f. Media Tank:

1) Material:  [Carbon steel with NSF 61 lining material] [FRP] [Stainless steel].

2) Pressure Rating:  <Insert psig (kPa).>

3) Media:  [Activated charcoal] [Ground charcoal] <Insert material>.

4) Media Quantity:  <Insert cu. ft. (cu. m).>

5) Diameter:  <Insert inches (mm).>

6) Height:  <Insert inches (mm).>

7) Inlet and Outlet Size:  <Insert NPS (DN).>

g. Unit Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value> V.

2) Phase:  [Single] [Three].

3) Hertz:  [60] <Insert value> Hz.

4) Full-Load Amperes:  <Insert value> A.

5) Minimum Circuit Ampacity:  <Insert value> A.

6) Maximum Overcurrent Protection:  <Insert value> A.

2.5 SAND FILTERS

Refer to the tables for water filtration equipment at the end of the Evaluations for lists of manufacturers' products.  Use these tables in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Circulating Sand Filters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Diamond Water Systems, Inc.

b. Everfilt.

c. Griswold Controls.

d. LAKOS; a div. of Claude Laval Corporation.

e. Miami Filter LLC.

f. PEP Filters, Inc.

g. Puroflux Corporation.

h. United Industries, Inc.

i. <Insert manufacturer's name.>

2. Description:  Factory-fabricated and -tested, simplex, sand-filter system of filter tank, media, strainer, circulating pump, piping, and controls for removing sediment particles from water.

a. Filter Tank:  Corrosion resistant with distribution system and media.

1) Construction:

Retain subparagraph below to require steel or stainless-steel tanks to be ASME labeled; delete for non-code construction.

a) Fabricate and label steel filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain subparagraph below to require FRP tanks to be ASME labeled; delete for non-code construction.

b) Fabricate and label FRP filter tanks to comply with ASME Boiler and Pressure Vessel Code:  Section X, if indicated.

Retain first subparagraph below for projects in seismic areas.

c) Fabricate supports and base and attachment to tank with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

2) Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

3) Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Steel, Class 150 flanges according to ASME B16.5 or grooved according to AWWA C606.

4) FRP Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Type A, integral; Designation [E, 125-psig (0.862-MPa)] [or] [F, 150-psig (1.034-MPa)] pressure category flanges of grade same as tank material according to ASTM D 5421.

b. Strainer:  Basket type.

1) Pipe Connections:

a) Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

b) Connections NPS 2-1/2 (DN 65) and Larger:  Cast-iron, Class 125 flanges according to ASME B16.1.

c. Piping:  [Galvanized steel pipe, galvanized cast-iron fittings] [Stainless-steel pipe, stainless-steel fittings], and flanged, grooved, or threaded joints.

Retain subparagraph above or first subparagraph below.

d. Piping:  ASTM B 88, Type L (ASTM B 88M, Type B) copper water tube, copper-alloy solder-joint fittings, and brazed, flanged, or grooved joints.

e. Safety Valves:  Automatic and manual pressure relief.

f. Circulating Pump:  Overhung impeller, close coupled, single stage, end suction, centrifugal.  Comply with UL 778 and with HI 1.1-1.2 and HI 1.3.

1) Pump Construction:  Bronze fitted.

a) Casing:  Radially split, cast iron.

b) Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] minimum.

c) Impeller:  ASTM B 584, cast bronze; statically and dynamically balanced, closed, and keyed to shaft.

d) Shaft and Shaft Sleeve:  Steel shaft, with copper-alloy shaft sleeve.

e) Seal:  Mechanical.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 22 Section "Common Motor Requirements for Plumbing Equipment."  If different characteristics are required, add subparagraphs below to suit Project.

2) Motor:  General requirements for motors are specified in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

g. Controls:  Automatic for control of circulating pump and tank backwash; factory wired for single, external electrical connection.

1) Panel:  NEMA 250, Type [4] <Insert type> enclosure with time clock and pressure gages.

2) Pump:  Automatic and manual.

3) Backwash:  Automatic; with [time-clock] [differential-pressure-switch] initiation device.

4) Backwash Valve:  Tank mounted.

h. Support:  Skid mounting.

If more than one circulating sand filter is required on Project, delete subparagraph and associated subparagraphs below and schedule sand filters on Drawings.

3. Capacity and Characteristics:

a. Filtrate Design Concentrations:

1) Sand:  <Insert ppm (mg/L).>

2) Silt:  <Insert ppm (mg/L).>

3) <Insert characteristic>:  <Insert value.>

b. Filter Design:

1) Continuous Flow:  <Insert gpm (L/s)> at [5 psig (34.5 kPa)] <Insert value> pressure drop.

2) Flow Rate:  <Insert gpm/sq. ft. (L/s per sq. m)> of media cross-sectional area.

3) Peak Flow:  <Insert gpm (L/s).>

4) Filtration Efficiency:  [98] <Insert number> percent removal of [1.8] <Insert number> minimum, specific-gravity suspended particles [5] [10] [20] [45] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

c. Filter Tank:  With internal distribution piping.

1) Material:  [Carbon steel with NSF 61 lining material] [FRP] <Insert material>.

2) Pressure Rating:  <Insert psig (kPa).>

3) Diameter:  <Insert inches (mm).>

4) Height:  <Insert inches (mm).>

5) Inlet and Outlet Size:  <Insert NPS (DN).>

6) Purge Size:  <Insert NPS (DN).>

d. Filter Media:  [Graded silica sand] <Insert media>.

Retain one of first two subparagraphs below to match backwash initiation device selected above.

e. Filter Backwash Interval:  <Insert psig (kPa)> pressure drop measured by differential pressure gages.

f. Filter Backwash Interval:  <Insert number> days measured by time clock.

g. Circulating Pump:

1) Capacity:  <Insert gpm (L/s).>

2) Total Dynamic Head:  <Insert feet (kPa).>

3) Speed:  <Insert rpm.>

4) Inlet Size:  <Insert NPS (DN).>

5) Outlet Size:  <Insert NPS (DN).>

h. Pump Motor Size and Characteristics:

1) Horsepower:  <Insert value.>

2) Volts:  [120] [208] [240] [277] [480] <Insert value> V.

3) Phase:  [Single] [Three].

4) Hertz:  [60] <Insert value> Hz.

i. Unit Electrical Characteristics:

1) Full-Load Amperes:  <Insert value> A.

2) Minimum Circuit Ampacity:  <Insert value> A.

3) Maximum Overcurrent Protection:  <Insert value> A.

B. Multimedia Sand Filters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alamo Water Treatment.

b. Columbia Water Conditioning Systems, Inc.

c. CSI; a division of Chandler Systems, Inc.

d. Culligan International Company.

e. CUNO Incorporated.

f. Diamond Water Conditioning.

g. Diamond Water Systems, Inc.

h. Environmental Dynamics Corporation.

i. Everfilt.

j. Filtronics, Inc.

k. Hungerford & Terry, Inc.

l. Industrial Filter & Pump Mfg. Co.

m. Ion Exchange Products, Inc.

n. LAKOS; a div. of Claude Laval Corporation.

o. Marlo Incorporated.

p. Mer-Made Filter, Inc.

q. Miami Filter LLC.

r. PEP Filters, Inc.

s. Puroflux Corporation.

t. RainSoft Div.; Aquion Partners L. P.

u. Separmatic Fluid Systems.

v. Smith & Loveless, Inc.

w. Springsoft International, Inc.

x. USFilter/Whittier, Inc.

y. Water & Power Technologies, Inc.

z. Water King.

aa. WaterSoft; a div. of AMTROL Inc.

ab. <Insert manufacturer's name.>

2. Description:  Factory-fabricated and -tested, [simplex] [duplex] [triplex], multimedia, sand-filter system of filter tank(s), media, piping, and controls for removing sediment particles from water.

a. Tank Construction:

Retain subparagraph below to require steel or stainless-steel tanks to be ASME labeled; delete for non-code construction.

1) Fabricate and label steel filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain subparagraph below to require FRP tanks to be ASME labeled; delete for non-code construction.

2) Fabricate and label FRP filter tanks to comply with ASME Boiler and Pressure Vessel Code:  Section X, if indicated.

Retain first subparagraph below for projects in seismic areas.

3) Fabricate supports and base and attachment to tank with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

b. Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

c. Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Steel, Class 150 flanges according to ASME B16.5 or grooved according to AWWA C606.

d. FRP Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Type A, integral; Designation [E, 125-psig (0.862-MPa)] [or] [F, 150-psig (1.034-MPa)] pressure category flanges of grade same as tank material according to ASTM D 5421.

e. Service Valve(s):  Diaphragm-type [hydraulically] [pneumatically] operated.

Retain one of first three subparagraphs below.

f. Piping:  [Galvanized steel pipe, galvanized cast-iron fittings] [Stainless-steel pipe, stainless-steel fittings], and flanged, grooved, or threaded joints.

g. Piping:  ASTM B 88, Type L (ASTM B 88M, Type B) copper water tube, copper-alloy solder-joint fittings, and brazed, flanged, or grooved joints.

h. Piping:  Schedule 80 ABS or PVC pipe and fittings with solvent-cemented joints.

i. Safety Valves:  Automatic air vent.

j. Controls for Simplex Tank System:  Automatic, electric time clock for control of filter system flow and backwash cycles; factory wired for single, external electrical connection.

Retain subparagraph above or first subparagraph below, or both if required.

k. Controls for [Duplex] [Triplex] Tank System:  Automatic, electric time clock for control of filter system flow and backwash cycles; factory wired for single, external electrical connection.  System operation shall be continuous with bypass piping and not more than one tank in backwash cycle at same time.

l. Support:  Skid mounting.

If more than one multimedia sand filter is required on Project, delete subparagraph and associated subparagraphs below and schedule sand filters on Drawings.

3. Capacity and Characteristics:

a. Filtrate Design Concentrations:

Retain only required data in list below; add other data as needed.

1) Chlorine:  <Insert ppm (mg/L).>

2) Color:  <Insert nephelometric turbidity units.>

3) Iron:  <Insert ppm (mg/L).>

4) Manganese:  <Insert ppm (mg/L).>

5) Total Dissolved Solids:  <Insert ppm (mg/L).>

6) Turbidity:  <Insert ppm (mg/L).>

7) <Insert characteristic>:  <Insert value.>

b. Filter Design:

1) Continuous Flow:  <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

2) Peak Flow:  <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

3) Filtration Efficiency:  [98] <Insert number> percent removal of suspended particles [10] [20] [40] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

4) Backwash Flow:  <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

c. Media Tank:  Single with controls.

Retain subparagraph above or first subparagraph below.

d. Media Tanks:  [Two] [Three] with manifolded inlet, outlet, and drain piping and controls.

e. Each Media Tank:

1) Material:  [Carbon steel with NSF 61 lining material] [FRP] <Insert material>.

2) Pressure Rating:  <Insert psig (kPa)> minimum.

3) Distribution System:  Factory-installed plastic.

4) Temperature Rating:  <Insert deg F (deg C)> minimum.

5) Diameter:  <Insert inches (mm).>

6) Height:  <Insert inches (mm).>

7) Service Valve Size:  <Insert NPS (DN).>

8) Inlet and Outlet Size:  <Insert NPS (DN).>

9) Drain Size:  <Insert NPS (DN).>

f. Filter Media:  [Graded silica sand] <Insert media>.

C. Greensand Filters:

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alamo Water Treatment.

b. CSI; a division of Chandler Systems, Inc.

c. Culligan International Company.

d. CUNO Incorporated.

e. Diamond Water Conditioning.

f. Environmental Dynamics Corporation.

g. Filtronics, Inc.

h. Hungerford & Terry, Inc.

i. Ion Exchange Products, Inc.

j. Marlo Incorporated.

k. PEP Filters, Inc.

l. RainSoft Div.; Aquion Partners L. P.

m. Separmatic Fluid Systems.

n. USFilter/Whittier, Inc.

o. WaterSoft; a div. of AMTROL Inc.

p. <Insert manufacturer's name.>

2. Description:  Greensand-filter system of piping, and controls for removing [iron] [iron and manganese] [manganese] from water.

a. Tank Construction:

Retain subparagraph below to require steel or stainless-steel tanks to be ASME labeled; delete for non-code construction.

1) Fabricate and label steel filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain subparagraph below to require FRP tanks to be ASME labeled; delete for non-code construction.

2) Fabricate and label FRP filter tanks to comply with ASME Boiler and Pressure Vessel Code:  Section X, if indicated.

Retain first subparagraph below for projects in seismic areas.

3) Fabricate supports and base and attachment to tank with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

b. Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

c. Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Steel, Class 150 flanges according to ASME B16.5 or grooved according to AWWA C606.

d. FRP Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Type A, integral; Designation [E, 125-psig (0.862-MPa)] [or] [F, 150-psig (1.034-MPa)] pressure category flanges of grade same as tank material according to ASTM D 5421.

e. Service Valve(s):  Diaphragm-type [hydraulically] [pneumatically] operated.

Retain one of first three subparagraphs below.

f. Piping:  [Galvanized steel pipe, galvanized cast-iron fittings] [Stainless-steel pipe, stainless-steel fittings], and flanged, grooved, or threaded joints.

g. Piping:  ASTM B 88, Type L (ASTM B 88M, Type B) copper water tube, copper-alloy solder-joint fittings, and brazed, flanged, or grooved joints.

h. Piping:  Schedule 80 ABS or PVC pipe and fittings with solvent-cemented joints.

i. Safety Valves:  Automatic air vent.

j. Controls for Simplex Tank System:  Automatic, electric time clock for control of filter system flow and backwash cycles; factory wired for single, external electrical connection.

Retain subparagraph above or first subparagraph below, or both if required.

k. Controls for [Duplex] [Triplex] Tank System:  Automatic, electric time clock for control of filter system flow and backwash cycles; factory wired for single, external electrical connection.  System operation shall be continuous with bypass piping and not more than one tank in backwash cycle at same time.

l. Support:  Skid mounting.

If more than one greensand filter is required on Project, delete subparagraph and associated subparagraphs below and schedule sand filters on Drawings.

3. Capacity and Characteristics:

a. Filtrate Design Concentrations:

1) Iron:  <Insert ppm (mg/L).>

2) Manganese:  <Insert ppm (mg/L).>

3) <Insert characteristic>:  <Insert value.>

b. Filter Design:

1) Continuous Flow:  <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

2) Peak Flow:  <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

3) Filtration Efficiency:  [98] <Insert number> percent removal of suspended particles [10] [20] [40] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

4) Backwash Flow:  <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

c. Media Tank:  Single with controls.

Retain subparagraph above or first subparagraph below.

d. Media Tanks:  [Two] [Three] with manifolded inlet, outlet, and drain piping and controls.

e. Each Media Tank:

1) Material:  [Carbon steel with NSF 61 lining material] [FRP] <Insert material>.

2) Pressure Rating:  <Insert psig (kPa)> minimum.

3) Distribution System:  Factory-installed plastic.

4) Temperature Rating:  <Insert deg F (deg C)> minimum.

5) Diameter:  <Insert inches (mm).>

6) Height:  <Insert inches (mm).>

7) Service Valve Size:  <Insert NPS (DN).>

8) Inlet and Outlet Size:  <Insert NPS (DN).>

9) Drain Size:  <Insert NPS (DN).>

f. Filter Media:  [Graded silica sand] <Insert media>.

2.6 SEPARATORS

Refer to the tables for water filtration equipment at the end of the Evaluations for lists of manufacturers' products.  Use these tables in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Description:  Simplex separator housing with baffles and chambers for removing sediment particles from water by centrifugal action and gravity.

Retain paragraph above or below.

B. Description:  Factory-fabricated and -tested, simplex separator system of housing with baffles and chambers, strainer, circulating pump, piping, and controls for removing sediment particles from water by centrifugal action and gravity.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Alamo Water Treatment.

b. Culligan International Company.

c. Griswold Controls.

d. LAKOS; a div. of Claude Laval Corporation.

e. PEP Filters, Inc.

f. Puroflux Corporation.

g. Rosedale Products, Inc.

h. USFilter/Whittier, Inc.

i. <Insert manufacturer's name.>

Retain subparagraph and associated subparagraphs below with either "Description" Paragraph above.

2. Housing:  With manufacturer's proprietary system of baffles and chambers.

a. Construction:

Retain subparagraph below to require steel or stainless-steel tanks to be ASME labeled; delete for non-code construction.

1) Fabricate and label steel separator housing to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain first subparagraph below for projects in seismic areas.

2) Fabricate supports and base and attachment to separator housing with reinforcement strong enough to resist separator movement during a seismic event when separator base is anchored to building structure.

b. Inlet:  Designed with tangential entry to produce centrifugal flow of feedwater.

c. Vortex Chamber:  Designed for downward vortex flow and gravity separation of particles.

d. Collection Chamber:  Designed to hold separated particles.

e. Outlet:  Near top of unit.

f. Purge:  At bottom of collection chamber.

g. Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

h. Pipe Connections NPS 2-1/2 (DN 65) and Larger:  ASME B16.1; steel, Class 150 flanges according to ASME B16.5 or grooved according to AWWA C606.  Provide stainless-steel flanges if tank is stainless steel.

Retain first subparagraph and associated subparagraphs below only if separator is circulating type.

3. Strainer:  Basket type.

a. Pipe Connections NPS 2 (DN 50) and Smaller:  Threaded according to ASME B1.20.1.

b. Pipe Connections NPS 2-1/2 (DN 65) and Larger:  Cast-iron, Class 125 flanges according to ASME B16.1.

4. Piping:  [Galvanized steel pipe, galvanized cast-iron fittings] [Stainless-steel pipe, stainless-steel fittings], and flanged, grooved, or threaded joints.

Retain subparagraph above or first subparagraph below.

5. Piping:  ASTM B 88, Type L (ASTM B 88M, Type B) copper water tube, copper-alloy solder-joint fittings, and brazed, flanged, or grooved joints.

6. Safety Valves:  Automatic and manual pressure relief.

7. Circulating Pump:  Overhung impeller, close coupled, single stage, end suction, centrifugal.  Comply with UL 778 and with HI 1.1-1.2 and HI 1.3.

a. Pump Construction:  Bronze fitted.

1) Casing:  Radially split, cast iron.

2) Pressure Rating:  [125 psig (860 kPa)] [150 psig (1035 kPa)] minimum.

3) Impeller:  ASTM B 584, cast bronze; statically and dynamically balanced, closed, and keyed to shaft.

4) Shaft and Shaft Sleeve:  Steel shaft, with copper-alloy shaft sleeve.

5) Seal:  Mechanical.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 22 Section "Common Motor Requirements for Plumbing Equipment."  If different characteristics are required, add subparagraphs below to suit Project.

b. Motor:  General requirements for motors are specified in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

8. Controls:  Automatic for control of circulating pump and separator purge; factory wired for single, external electrical connection.

a. Panel:  NEMA 250, Type [4] <Insert type> enclosure.

b. Pump:  Automatic and manual.

c. Separator Purge:  Automatic and manual.

9. Support:  Skid mounting.

If more than one separator is required on Project, delete subparagraph and associated subparagraphs below and schedule separators on Drawings.

10. Capacity and Characteristics:

a. Filtrate Design Concentrations:

1) Sand:  <Insert ppm (mg/L).>

2) Silt:  <Insert ppm (mg/L).>

3) <Insert characteristic>:  <Insert value.>

b. Separator Design:

1) Continuous Flow:  <Insert gpm (L/s)> at [5-psig (34.5-kPa)] <Insert value> pressure drop.

2) Peak Flow:  <Insert gpm (L/s).>

3) Separator Efficiency:  [98] <Insert number> percent removal of listed [1.8] <Insert number> minimum, specific-gravity suspended particles [5] [10] [20] [45] <Insert size> micrometers and larger from feedwater of listed filtrate design concentrations.

c. Housing:

1) Material:  [Carbon] [Stainless] steel.

2) Pressure Rating:  <Insert psig (kPa).>

3) Diameter:  <Insert inches (mm).>

4) Height:  <Insert inches (mm).>

5) Inlet and Outlet Size:  <Insert NPS (DN).>

6) Purge Size:  <Insert NPS (DN).>

Retain first subparagraph and associated subparagraphs below only if separator is circulating type.

d. Circulating Pump:

1) Capacity:  <Insert gpm (L/s).>

2) Total Dynamic Head:  <Insert feet (kPa).>

3) Speed:  <Insert rpm.>

4) Inlet Size:  <Insert NPS (DN).>

5) Outlet Size:  <Insert NPS (DN).>

e. Pump Motor Size and Characteristics:

1) Horsepower:  <Insert value.>

2) Volts:  [120] [208] [240] [277] [480] <Insert value> V.

3) Phase:  [Single] [Three].

4) Hertz:  [60] <Insert value> Hz.

f. Unit Electrical Characteristics:

1) Full-Load Amperes:  <Insert value> A.

2) Minimum Circuit Ampacity:  <Insert value> A.

3) Maximum Overcurrent Protection:  <Insert value> A.

2.7 SOURCE QUALITY CONTROL

Retain this Article for carbon or sand filters and for separators.

A. Hydrostatically test before shipment to minimum of one and one-half times pressure rating.

B. Prepare test reports.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of [filters] [and] [separators].

B. Examine roughing-in for piping systems to verify actual locations of piping connections before equipment installation.

C. Examine walls and floors for suitable conditions where [filters] [and] [separators] will be installed.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 CONCRETE BASES

Revise this Article based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.

A. Anchor [filters] [and] [separators] to concrete bases.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

Coordinate sizes and locations of concrete bases.  Verify structural requirements with structural engineer.

5. Concrete base construction requirements are specified in Division 22 Section "Common Work Results for Plumbing."

6. Cast-in-place concrete materials and placement requirements are specified in Division 03.

3.3 BAG-TYPE FILTER INSTALLATION

A. Install bag-type filters on concrete bases.

1. Exception:  Omit concrete bases if installation directly on floor is indicated.

B. Install bag-type filters level and plumb, according to layout drawings, original design, and referenced standards.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices needing service are accessible.

1. Install filter media bags secured in filter housings.

Retain paragraph below for Project in a seismic area.  Add special requirements for seismic restraints here or detail on Drawings.

C. Install seismic restraints for bag-type filter housings and anchor to building structure.

3.4 CARTRIDGE-FILTER INSTALLATION

A. Install cartridge filters level and plumb, according to layout drawings, original design, and referenced standards.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices needing service are accessible.

B. Install freestanding cartridge filters on concrete bases.

1. Exception:  Omit concrete bases if installation directly on floor is indicated.

C. Attach wall brackets for off-floor, wall-mounting, cartridge filter to vertical surface.  Attach housing(s), and base if any, to wall bracket.

D. Install housings for off-floor, in-line, cartridge filters in piping.

E. Install filter elements in cartridges.

Retain paragraph below for Project in a seismic area.  Add special requirements for seismic restraints here or detail on Drawings.

F. Install seismic restraints for freestanding cartridge-filter housings and anchor to building structure.

3.5 CARBON-FILTER INSTALLATION

A. Install carbon filters on concrete bases, level and plumb.

1. Prepare carbon-filter tank distribution system and underbed, if any, for filter media and place specified media into tanks.

Retain paragraph below for Project in a seismic area.  Add special requirements for seismic restraints here or detail on Drawings.

B. Install seismic restraints for carbon-filter housings and anchor to building structure.

3.6 SAND-FILTER INSTALLATION

A. Install sand-filter tanks on concrete bases, level and plumb.

1. Prepare sand-filter tank distribution system and underbed for filter media and place specified sand and other media into tanks.

Retain paragraph below for Project in a seismic area.  Add special requirements for seismic restraints here or detail on Drawings.

B. Install seismic restraints for sand-filter tanks and accessories and anchor to building structure.

3.7 SEPARATOR INSTALLATION

A. Install separators on concrete bases, level and plumb.

Retain paragraph below for Project in a seismic area.  Add special requirements for seismic restraints here or detail on Drawings.

B. Install seismic restraints for separators and accessories and anchor to building structure.

3.8 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 22 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to equipment to allow service and maintenance.

C. Make piping connections between water filtration equipment and dissimilar-metal water piping with dielectric fittings.  Dielectric fittings are specified in Division 22 Section "Common Work Results for Plumbing."

D. Install shutoff valves on feedwater-inlet and filtrate-outlet piping of each water filtration equipment [filter] [and] [separator] [, and on inlet and outlet headers].

1. Metal general-duty valves are specified in Division 22 Section "General-Duty Valves for Plumbing Piping."

2. Plastic valves are specified in Division 22 Section "Domestic Water Piping."

Retain subparagraph below if factory-installed valves are acceptable.

3. Exception:  Water filtration equipment with factory-installed shutoff valves at locations indicated.

E. Install pressure gages on feedwater-inlet and filtrate-outlet piping of each water filtration equipment [filter] [and] [separator].  Pressure gages are specified in Division 22 Section "Meters and Gages for Plumbing Piping."

Retain subparagraph below if factory-installed valves are acceptable.

1. Exception:  Water filtration equipment with factory-installed pressure gages at locations indicated.

Retain subparagraph below if pressure gages are not required.

2. Exception:  Cartridge water filters.

F. Install valved bypass water piping around each water filtration equipment [filter] [and] [separator].

1. Metal general-duty valves are specified in Division 22 Section "General-Duty Valves for Plumbing Piping."

2. Plastic valves are specified in Division 22 Section "Domestic Water Piping."

3. Water piping is specified in Division 22 Section "Domestic Water Piping."

Retain one or both subparagraphs below if bypass is not required.

4. Exception:  Bag-type water filtration equipment.

5. Exception:  Cartridge water filtration equipment.

G. Install drains as indirect wastes to spill into open drains or over floor drains.

H. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

I. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.9 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

Retain subparagraph below only for units with pump, controls, or electrical devices.

2. Operational Test:  After electrical circuitry has been energized, start units to confirm proper unit operation.

Retain subparagraph below only for units with controls or other devices.

3. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace water filtration equipment that does not pass tests and inspections and retest as specified above.

3.10 STARTUP SERVICE

Retain this Article if factory-authorized service representative is required.

A. Engage a factory-authorized service representative to perform startup service for [carbon-] [and] [sand-] filter water filtration equipment.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. <Insert startup steps if any.>

B. Sample [filter] [and] [separator] filtrate after startup and at three consecutive seven-day intervals (total of four samples), and prepare certified test reports for required water performance characteristics.

3.11 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain [carbon-] [and] [sand-] filter water filtration equipment.  Refer to Division 01 Section " Demonstration and Training."

END OF SECTION 223200

	DOMESTIC WATER FILTRATION EQUIPMENT
	223200 - 1



