Copyright 2002 and 2005 AIA
MASTERSPEC Full Length
12/02 (R 06/06)

Copyright 2002 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 223400 - FUEL-FIRED DOMESTIC WATER HEATERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following fuel-fired water heaters:

Adjust list below to suit Project.

1. Household, atmospheric, storage, gas water heaters.

2. Household, direct-vent, storage, gas water heaters.

3. Household, power-vent, storage, gas water heaters.

4. Instantaneous, tankless, gas water heaters.

5. Commercial, atmospheric, storage, gas water heaters.

6. Commercial, power-burner, storage, gas water heaters.

7. Commercial, power-vent, storage, gas water heaters.

8. Commercial, high-efficiency, gas water heaters.

9. Commercial, coil-type, finned-tube, gas water heaters.

10. Commercial, grid-type, finned-tube, gas water heaters.

11. Household, oil-fired water heaters.

12. Commercial, oil-fired water heaters.

13. Large-capacity, oil-fired water heaters.

14. Dual-fuel, gas and oil-fired water heaters.

15. Compression tanks.

16. Water heater accessories.

1.3 DEFINITIONS

Retain term that remains after this Section has been edited.

A. LP Gas:  Liquefied-petroleum fuel gas.

1.4 SUBMITTALS

A. Product Data:  For each type and size of water heater indicated.  Include rated capacities, operating characteristics, furnished specialties, and accessories.

B. LEED Submittal:

1. Product Data for Prerequisite EA 2:  Documentation indicating that units comply with ASHRAE/IESNA 90.1-2004, Section 7 - "Service Water Heating."

Retain paragraph below only for water heaters that require electrical power.

C. Shop Drawings:  Diagram power, signal, and control wiring.

Retain paragraph below only for commercial and instantaneous water heaters and if certificates are required.

D. Product Certificates:  For each type of [commercial] [and] [instantaneous] water heater, signed by product manufacturer.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 22 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment."

E. Manufacturer Seismic Qualification Certification:  Submit certification that commercial water heaters, accessories, and components will withstand seismic forces defined in Division 22 Section "Vibration and Seismic Controls for Plumbing Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

F. Source quality-control test reports.

G. Field quality-control test reports.

H. Operation and Maintenance Data:  For water heaters to include in emergency, operation, and maintenance manuals.

I. Warranty:  Special warranty specified in this Section.

1.5 QUALITY ASSURANCE

A. Source Limitations:  Obtain same type of water heaters through one source from a single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 01 requirements.

B. Product Options:  Drawings indicate size, profiles, and dimensional requirements of water heaters and are based on the specific system indicated.  Refer to Division 01 Section "Product Requirements."

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EA 2 requires that water heaters comply with ASHRAE/IESNA 90.1-2004, including equipment efficiency indicated in table titled "Performance Requirements for Water Heating Equipment."

D. ASHRAE/IESNA 90.1-2004Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004.

E. ASME Compliance:

1. Where ASME-code construction is indicated, fabricate and label commercial water heater storage tanks to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

2. Where ASME-code construction is indicated, fabricate and label commercial, finned-tube water heaters to comply with ASME Boiler and Pressure Vessel Code:  Section IV.

F. Comply with NSF 61, "Drinking Water System Components - Health Effects; Sections 1 through 9" for all components that will be in contact with potable water.

1.6 COORDINATION

A. Coordinate size and location of concrete bases with Architectural and Structural Drawings.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of fuel-fired water heaters that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, the following:

a. Structural failures including storage tank and supports.

b. Faulty operation of controls.

c. Deterioration of metals, metal finishes, and other materials beyond normal use.

Verify available warranties for units and components and insert numbers below.

2. Warranty Period(s):  From date of Substantial Completion:

a. Household, Gas Water Heaters:

1) Storage Tank:  [Five] [Six] [10] <Insert number> years.

2) Controls and Other Components:  [Two] [Three] <Insert number> years.

b. Instantaneous, Gas Water Heaters:

1) Heat Exchanger:  [Five] <Insert number> years.

2) Controls and Other Components:  [Three] <Insert number> years.

c. Commercial, Gas Water Heaters:

1) Storage Tank:  [Three] [Five] <Insert number> years.

2) Controls and Other Components:  [Three] [Five] <Insert number> years.

d. Oil-Fired Water Heaters:

1) Storage Tank:  [Three] [Five] <Insert number> years.

2) Burner and Controls:  [One] [Two] [Three] <Insert number> year(s).

3) Other Components:  [Three] [Five] <Insert number> years.

e. Dual-Fuel Water Heaters:

1) Storage Tank:  [Three] [Five] <Insert number> years.

2) Burner and Controls:  [One] [Two] [Three] <Insert number> year(s).

3) Other Components:  [Three] [Five] <Insert number> years.

f. Compression Tanks:  [One] <Insert number> year(s).

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 HOUSEHOLD, GAS WATER HEATERS

Refer to the Household and Tankless, Gas Water Heater Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Household, Atmospheric, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.1/CSA 4.1.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Apollo Heating & Cooling; a division of State Industries, Inc.

c. Bradford White Corporation.

d. GSW Water Heating Company.

e. Lochinvar Corporation.

f. Maytag Corp.; Water Heating Appliances Div.

g. Rheem Water Heater Div.; Rheem Manufacturing Company.

h. Ruud Water Heater Div.; Rheem Manufacturing Company.

i. Smith, A. O. Water Products Company.

j. State Industries, Inc.

k. <Insert manufacturer's name.>

2. Storage-Tank Construction:  Steel.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Burner:  For use with atmospheric water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

Retain first subparagraph below if required.  Verify availability for model selected.

g. Automatic Ignition:  ANSI Z21.20, electric, automatic, gas-ignition system.

h. Temperature Control:  Adjustable thermostat.

i. Heat Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

j. Combination Temperature and Pressure Relief Valve:  ANSI Z21.22/CSA 4.4.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

4. Draft Hood:  Low-profile-type, draft diverter; complying with ANSI Z21.12.

Retain subparagraph below if required.  Verify availability for model selected.

5. Automatic Damper:  ANSI Z21.66, [electrically operated] [mechanically activated] [thermally activated], automatic-vent-damper device with size matching draft hood.

If more than one household, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

6. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

Retain first subparagraph and associated subparagraphs below only if model selected requires electrical power.

g. Electrical Characteristics:

1) Volts:  [120] [240] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

B. Household, Direct-Vent, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.1/CSA 4.1.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Apollo Heating & Cooling; a division of State Industries, Inc.

c. Bradford White Corporation.

d. Rheem Water Heater Div.; Rheem Manufacturing Company.

e. Ruud Water Heater Div.; Rheem Manufacturing Company.

f. Smith, A. O. Water Products Company.

g. State Industries, Inc.

h. <Insert manufacturer's name.>

2. Storage-Tank Construction:  Steel.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Burner:  For use with direct-vent water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

Retain first subparagraph below if required.  Verify availability for model selected.

g. Automatic Ignition:  ANSI Z21.20, electric, automatic, gas-ignition system.

h. Temperature Control:  Adjustable thermostat.

i. Heat Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

j. Combination Temperature and Pressure Relief Valve:  ANSI Z21.22/CSA 4.4.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

4. Direct-Vent System:  Through-[wall] [roof], coaxial- or double-channel, vent assembly with water heater manufacturers' outside intake/exhaust screen.

If more than one household, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

5. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

Retain first subparagraph and associated subparagraphs below only if model selected requires electrical power.

g. Electrical Characteristics:

1) Volts:  [120] [240] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

C. Household, Power-Vent, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.1/CSA 4.1.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Apollo Heating & Cooling; a division of State Industries, Inc.

c. Bradford White Corporation.

d. GSW Water Heating Company.

e. Lochinvar Corporation.

f. Rheem Water Heater Div.; Rheem Manufacturing Company.

g. Ruud Water Heater Div.; Rheem Manufacturing Company.

h. Smith, A. O. Water Products Company.

i. State Industries, Inc.

j. <Insert manufacturer's name.>

2. Storage-Tank Construction:  Steel.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Burner:  For use with power-vent water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

Retain first subparagraph below if required.  Verify availability for model selected.

g. Automatic Ignition:  ANSI Z21.20, electric, automatic, gas-ignition system.

h. Temperature Control:  Adjustable thermostat.

i. Heat Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

j. Combination Temperature and Pressure Relief Valve:  ANSI Z21.22/CSA 4.4.  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

4. Power-Vent System:  Exhaust fan, interlocked with burner.

If more than one household, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

5. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

g. Electrical Characteristics:

1) Volts:  [120] [240] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

2.3 INSTANTANEOUS, GAS WATER HEATERS

Refer to the Household and Tankless, Gas Water Heater Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Description:  Comply with ANSI Z21.10.3/CSA 4.3, except storage is not required.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Controlled Energy Corporation.

b. NORITZ America Corporation.

c. Paloma Industries, Inc.

d. Takagi Industrial Co. USA, Inc.

e. <Insert manufacturer's name.>

2. Construction:  Copper piping or tubing complying with NSF 61 barrier materials for potable water, without storage capacity.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Heat Exchanger:  Copper tubing.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Burner:  For use with tankless water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

Ignition device in first subparagraph below may be batteries, gas pilot, or electrical power.

f. Automatic Ignition:  Manufacturer's proprietary system for automatic, gas ignition.

g. Temperature Control:  Adjustable thermostat.

h. Jacket:  Metal with enameled finish or plastic.

3. Support:  Bracket for wall mounting.

If more than one instantaneous, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

4. Capacity and Characteristics:

a. Flow Rate:  <Insert gpm (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

b. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

c. Fuel Gas Demand:  <Insert cfh (L/s).>

d. Fuel Gas Input:  <Insert Btu/h (W).>

e. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

Retain first subparagraph and associated subparagraphs below only if model selected requires electrical power.

f. Electrical Characteristics:

1) Volts:  [120] <Insert value>.

2) Phase:  Single.

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

g. Minimum Vent Diameter:  <Insert inches (mm).>

2.4 COMMERCIAL, GAS WATER HEATERS

Refer to the Commercial, Gas Water Heater Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Commercial, Atmospheric, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.3/CSA 4.3.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. American Water Heater Company.

b. Bock Water Heaters, Inc.

c. Bradford White Corporation.

d. GSW Water Heating Company.

e. HESco Industries, Inc.

f. Lochinvar Corporation.

g. PVI Industries, LLC.

h. Rheem Water Heater Div.; Rheem Manufacturing Company.

i. Ruud Water Heater Div.; Rheem Manufacturing Company.

j. Smith, A. O. Water Products Company.

k. State Industries, Inc.

l. <Insert manufacturer's name.>

2. Storage-Tank Construction:  [ASME] [Non-ASME]-code steel with [150-psig (1035-kPa)] <Insert psig (kPa)> working-pressure rating.

a. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

Retain subparagraph above or first subparagraph below.  If specific lining is required, verify availability for model selected.

c. Lining:  [Cement] [Glass] [Nickel plate] [Phenolic coating] [Sheet copper] <Insert material> complying with NSF 61 barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

d. Insulation:  Comply with ASHRAE/IESNA 90.1.  Surround entire storage tank except connections and controls.

e. Jacket:  Steel with enameled finish.

f. Burner:  For use with atmospheric water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

Retain first subparagraph below if required.  Verify availability for model selected.

g. Automatic Ignition:  ANSI Z21.20, electric, automatic, gas-ignition system.

h. Temperature Control:  Adjustable thermostat.

i. Safety Controls:  Automatic, high-temperature-limit and low-water cutoff devices or systems.

j. Combination Temperature and Pressure Relief Valves:  ANSI Z21.22/CSA 4.4.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

4. Special Requirements:  NSF 5 construction.

5. Draft Hood:  Draft diverter; complying with ANSI Z21.12.

Retain subparagraph below if required.  Verify availability for model selected.

6. Automatic Damper:  ANSI Z21.66, [electrically operated] [mechanically activated] [thermally activated], automatic-vent-damper device with size matching draft hood.

Retain subparagraph below only if water heater has electrical power.

7. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

If more than one commercial, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

8. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

Retain first subparagraph and associated subparagraphs below only if model selected requires electrical power.

g. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

B. Commercial, Power-Burner, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.3/CSA 4.3.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Aldrich Company.

b. Bock Water Heaters, Inc.

c. Bradford White Corporation.

d. HESco Industries, Inc.

e. Precision Boilers.

f. PVI Industries, LLC.

g. RECO USA.

h. Sellers Engineering Co.

i. Smith, A. O. Water Products Company.

j. <Insert manufacturer's name.>

2. Storage-Tank Construction:  [ASME] [Non-ASME]-code steel with [150-psig (1035-kPa)] <Insert psig (kPa)> working-pressure rating.

a. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

Retain subparagraph above or first subparagraph below.  If specific lining is required, verify availability for model selected.

c. Lining:  [Cement] [Glass] [Nickel plate] [Phenolic coating] [Sheet copper] <Insert material> complying with NSF 61 barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

d. Insulation:  Comply with ASHRAE/IESNA 90.1.  Surround entire storage tank except connections and controls.

e. Jacket:  Steel with enameled finish.

f. Combination Temperature and Pressure Relief Valves:  ANSI Z21.22/CSA 4.4.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

4. Burner:  Comply with UL 795 for power-burner water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.  Delete if list is not required.

a. [Available ]Manufacturers:

1) Adams Manufacturing Co.

2) Aero Environmental Ltd.

3) Carlin Combustion Technology, Inc.

4) Gordon-Piatt Group; John Zink Company, LLC.

5) Midco International Inc.

6) Power Flame, Inc.

7) Webster Engineering Co., L.L.C.

8) <Insert manufacturer's name.>

b. Automatic Ignition:  ANSI Z21.20, electric, automatic, gas-ignition system.

5. Temperature Control:  Adjustable thermostat.

6. Safety Controls:  Automatic, high-temperature-limit and low-water cutoff devices or systems.

7. Special Requirements:  NSF 5 construction.

8. Draft Hood:  [Draft diverter; complying with ANSI Z21.12] <Insert different hood or other arrangement>.

9. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

If more than one commercial, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

10. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

g. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

C. Commercial, Power-Vent, Storage, Gas Water Heaters:  Comply with ANSI Z21.10.3/CSA 4.3.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Bradford White Corporation.

b. Lochinvar Corporation.

c. Rheem Water Heater Div.; Rheem Manufacturing Company.

d. Ruud Water Heater Div.; Rheem Manufacturing Company.

e. Smith, A. O. Water Products Company.

f. <Insert manufacturer's name.>

2. Storage-Tank Construction:  [ASME] [Non-ASME]-code steel with [150-psig (1035-kPa)] <Insert psig (kPa)> working-pressure rating.

a. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

Retain subparagraph above or first subparagraph below.  If specific lining is required, verify availability for model selected.

c. Lining:  [Cement] [Glass] [Nickel plate] [Phenolic coating] [Sheet copper] <Insert material> complying with NSF 61 barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

d. Insulation:  Comply with ASHRAE/IESNA 90.1.  Surround entire storage tank except connections and controls.

e. Jacket:  Steel with enameled finish.

f. Burner:  For use with power-vent water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

g. Automatic Ignition:  ANSI Z21.20, electric, automatic, gas-ignition system.

h. Temperature Control:  Adjustable thermostat.

i. Safety Controls:  Automatic, high-temperature-limit and low-water cutoff devices or systems.

j. Combination Temperature and Pressure Relief Valves:  ANSI Z21.22/CSA 4.4.  Include one or more relief valve with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

4. Special Requirements:  NSF 5 construction.

5. Power-Vent System:  Exhaust fan, interlocked with burner.

6. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

If more than one commercial, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

7. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

g. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

D. Commercial, High-Efficiency, Gas Water Heaters:  Comply with ANSI Z21.10.3/CSA 4.3.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. AERCO International.

b. Bradford White Corporation.

c. Heat Transfer Products, Inc.

d. Laars Heating Systems; Waterpik Technologies, Inc.

e. Lochinvar Corporation.

f. Patterson-Kelley.

g. RBI Water Heaters; a Mestek, Inc. Company.

h. Rheem Water Heater Div.; Rheem Manufacturing Company.

i. Ruud Water Heater Div.; Rheem Manufacturing Company.

j. Smith, A. O. Water Products Company.

k. State Industries, Inc.

l. Weben-Jarco, Inc.

m. <Insert manufacturer's name.>

Verify combustion efficiency of model selected in first subparagraph below.

2. Description:  Manufacturer's proprietary design to provide at least [84] [85] [88] [95] <Insert number> percent combustion efficiency at optimum operating conditions.  Following features and attributes may be modified or omitted if water heater otherwise complies with requirements for performance.

3. Storage-Tank Construction:  ASME-code steel with [150-psig (1035-kPa)] <Insert psig (kPa)> minimum working-pressure rating.

a. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

Retain subparagraph above or first subparagraph below.  If specific lining is required, verify availability for model selected.

c. Lining:  [Cement] [Glass] [Nickel plate] [Phenolic coating] [Sheet copper] <Insert material> complying with NSF 61 barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

4. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

d. Insulation:  Comply with ASHRAE/IESNA 90.1.  Surround entire storage tank except connections and controls.

e. Jacket:  Steel with enameled finish.

f. Combination Temperature and Pressure Relief Valves:  ANSI Z21.22/CSA 4.4.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

5. Burner or Heat Exchanger:  Comply with UL 795 or approved testing agency requirements for high-efficiency water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

6. Temperature Control:  Adjustable thermostat.

7. Safety Controls:  Automatic, high-temperature-limit and low-water cutoff devices or systems.

8. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

Retain subparagraph below only if draft hood is required.

9. Draft Hood:  [Draft diverter; complying with ANSI Z21.12] <Insert different hood or other arrangement>.

If more than one commercial, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

10. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

Retain first subparagraph and associated subparagraphs below only if model selected requires electrical power.

g. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

E. Commercial, Coil-Type, Finned-Tube, Gas Water Heaters:  Comply with ANSI Z21.13 for hot-water boilers.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Ajax Boiler Inc.

b. HESco Industries, Inc.

c. Smith, A. O. Water Products Company.

d. Weben-Jarco, Inc.

e. <Insert manufacturer's name.>

2. Description:  Packaged unit with boiler, storage tank, pump, piping, and controls.

3. Boiler Construction:  ASME code with [160-psig (1100-kPa)] <Insert psig (kPa)> working-pressure rating for hot-water-boiler-type water heater.

a. Heat Exchanger:  Helix or spiral, finned-copper-tube coils with bronze headers.

b. Connections:  Factory fabricated of materials compatible with boiler.  Attach to boiler before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

4. Boiler Appurtenances:

a. Insulation:  Comply with ASHRAE/IESNA 90.1.  Surround entire boiler except connections and controls.

b. Jacket:  Steel with enameled finish.

c. Burner:  For use with coil-type, finned-tube water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

d. Temperature Control:  Adjustable, storage tank temperature-control fitting and flow switch, interlocked with circulator and burner.

e. Safety Control:  Automatic, high-temperature-limit cutoff device or system.

f. Automatic Ignition:  Intermittent electronic ignition complying with ANSI Z21.20.

5. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

6. Support:  Steel base or skids.

7. Draft Hood:  [Draft diverter; complying with ANSI Z21.12] <Insert different hood or other arrangement>.

Retain first subparagraph below if required.  Verify availability for model selected.

8. Automatic Damper:  ANSI Z21.66, [electrically operated] [mechanically activated] [thermally activated], automatic-vent-damper device with size matching draft hood.

9. Hot-Water Storage Tank:  Connected with piping to circulating pump and water heater.

a. Construction:  According to ASME Boiler and Pressure Vessel Code:  Section VIII, steel with [150-psig (1035-kPa)] [125-psig (860-kPa)] <Insert psig (kPa)> working-pressure rating.

b. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

d. Insulation:  Comply with ASHRAE/IESNA 90.1.  Surround entire storage tank except connections and controls.

e. Jacket:  Steel with enameled finish.

f. Anode Rods:  Factory installed, magnesium.

g. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005, factory installed.

h. Combination Temperature and Pressure Relief Valves:  ANSI Z21.22/CSA 4.4.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

10. Circulating Pump:  UL 778, all-bronze, centrifugal, overhung-impeller, separately coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3.  Include mechanical seals, [125-psig (860-kPa)] <Insert psig (kPa)> minimum working-pressure rating, and 225 deg F (107 deg C) continuous-water-temperature rating.

11. Piping:  Copper tubing; copper, solder-joint fittings; and brazed or flanged joints.

12. Mounting:  Water heater, tank, and accessories factory mounted on skids.

If more than one commercial, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

13. Capacity and Characteristics:

a. Hot-Water Storage-Tank Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

g. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

F. Commercial, Grid-Type, Finned-Tube, Gas Water Heaters:  Comply with ANSI Z21.13 for hot-water boilers.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Bradford White Corporation.

b. Laars Heating Systems; Waterpik Technologies, Inc.

c. Lochinvar Corporation.

d. Precision Boilers.

e. Raypak.

f. RBI Water Heaters; a Mestek, Inc. Company.

g. RECO USA.

h. Rheem Water Heater Div.; Rheem Manufacturing Company.

i. Ruud Water Heater Div.; Rheem Manufacturing Company.

j. Smith, A. O. Water Products Company.

k. <Insert manufacturer's name.>

2. Description:  Packaged unit with boiler, storage tank, pump, piping, and controls.

3. Boiler Construction:  ASME code with [160-psig (1100-kPa)] <Insert psig (kPa)> working-pressure rating for hot-water-boiler-type water heater.

a. Heat Exchanger:  Horizontal, straight, finned-copper tubes with bronze headers.

b. Connections:  Factory fabricated of materials compatible with boiler.  Attach to boiler before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

4. Boiler Appurtenances:

a. Insulation:  Comply with ASHRAE/IESNA 90.1.  Surround entire boiler except connections and controls.

b. Jacket:  Steel with enameled finish.

c. Burner:  For use with grid-type, finned-tube water heaters and for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

d. Temperature Control:  Adjustable, storage tank temperature-control fitting and flow switch, interlocked with circulator and burner.

e. Safety Control:  Automatic, high-temperature-limit cutoff device or system.

f. Automatic Ignition:  Intermittent electronic ignition complying with ANSI Z21.20.

5. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

6. Support:  Steel base or skids.

7. Draft Hood:  [Draft diverter; complying with ANSI Z21.12] <Insert different hood or other arrangement>.

Retain first subparagraph below if required.  Verify availability for model selected.

8. Automatic Damper:  ANSI Z21.66, [electrically operated] [mechanically activated] [thermally activated], automatic-vent-damper device with size matching draft hood.

9. Hot-Water Storage Tank:  Connected with piping to circulating pump and water heater.

a. Construction:  According to ASME Boiler and Pressure Vessel Code:  Section VIII, steel with [150-psig (1035-kPa)] [125-psig (860-kPa)] <Insert psig (kPa)> working-pressure rating.

b. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

d. Insulation:  Comply with ASHRAE/IESNA 90.1.  Surround entire storage tank except connections and controls.

e. Jacket:  Steel with enameled finish.

f. Anode Rods:  Factory installed, magnesium.

g. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005, factory installed.

h. Combination Temperature and Pressure Relief Valves:  ANSI Z21.22/CSA 4.4.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

10. Circulating Pump:  UL 778, all-bronze, centrifugal, overhung-impeller, separately-coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3.  Include mechanical seals, [125-psig (860-kPa)] <Insert psig (kPa)> minimum working-pressure rating, and 225 deg F (107 deg C) continuous-water-temperature rating.

11. Piping:  Copper tubing; copper, solder-joint fittings; and brazed or flanged joints.

12. Mounting:  Water heater, tank, and accessories factory mounted on skids.

If more than one commercial, gas water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

13. Capacity and Characteristics:

a. Hot-Water Storage-Tank Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Gas Pressure Required at Burner:  <Insert psig (kPa) or inches (mm)> water column.

g. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

h. Minimum Vent Diameter:  <Insert inches (mm).>

2.5 OIL-FIRED WATER HEATERS

Refer to the Oil-Fired Water Heater Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Household, Oil-Fired Water Heaters:  Comply with UL 732 for storage water heaters.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Aero Environmental Ltd.

b. Bock Water Heaters, Inc.

c. Bradford White Corporation.

d. GSW Water Heating Company.

e. Lochinvar Corporation.

f. Therma-Flow/Everhot.

g. <Insert manufacturer's name.>

2. Storage-Tank Construction:  Steel.

a. Tappings:  ASME B1.20.1 pipe thread.

b. Pressure Rating:  150 psig (1035 kPa).

c. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending lining material into tappings.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Temperature Control:  Adjustable thermostat.

g. Heat Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

h. Relief Valves:  ASME rated and stamped and complying with ASME PTC 25.3, for combination temperature and pressure relief valves.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

4. Oil Burner:  Comply with UL 296 for use with No. 2 fuel oil.

5. Draft Regulator:  Barometric type or adjustable-damper device.

If more than one oil-fired water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

6. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel-Oil Demand:  <Insert gpm (kg/s).>

e. Fuel-Oil Input:  <Insert Btu/h (W).>

f. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

g. Minimum Vent Diameter:  <Insert inches (mm).>

B. Commercial, Oil-Fired Water Heaters:  Comply with UL 732 for storage water heaters.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Aero Environmental Ltd.

b. Aldrich Company.

c. Bock Water Heaters, Inc.

d. Bradford White Corporation.

e. GSW Water Heating Company.

f. Heat Transfer Products, Inc.

g. HESco Industries, Inc.

h. Lochinvar Corporation.

i. Precision Boilers.

j. Smith, A. O. Water Products Company.

k. State Industries, Inc.

l. Therma-Flow/Everhot.

m. <Insert manufacturer's name.>

2. Storage-Tank Construction:  [ASME] [Non-ASME]-code steel with [150-psig (1035-kPa)] <Insert psig (kPa)> minimum working-pressure rating.

a. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

Retain subparagraph above or first subparagraph below.  If specific lining is required, verify availability for model selected.

c. Lining:  [Cement] [Glass] [Nickel plate] [Phenolic coating] [Sheet copper] <Insert material> complying with NSF 61 barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Temperature Control:  Adjustable thermostat.

g. Relief Valves:  ASME rated and stamped and complying with ASME PTC 25.3, for combination temperature and pressure relief valves.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

4. Oil Burners:  Comply with UL 296 for use with No. 2 fuel oil.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.  Delete if list is not required.

a. [Available ]Manufacturers:

1) Adams Manufacturing Co.

2) Aero Environmental Ltd.

3) Beckett, R. W. Corporation.

4) Carlin Combustion Technology, Inc.

5) Gordon-Piatt Group; John Zink Company, LLC.

6) Power Flame, Inc.

7) Webster Engineering Co., L.L.C.

8) <Insert manufacturer's name.>

5. Safety Control:  Automatic, high-temperature-limit cutoff device or system.

6. Draft Regulator:  Barometric type or adjustable-damper device.

7. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

If more than one oil-fired water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

8. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel-Oil Demand:  <Insert gpm (kg/s).>

e. Fuel-Oil Input:  <Insert Btu/h (W).>

f. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

g. Minimum Vent Diameter:  <Insert inches (mm).>

C. Large-Capacity, Oil-Fired Water Heaters:  Comply with UL 732 for storage water heaters except when capacity is greater than 120 gal. (454 L).

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Aldrich Company.

b. Bock Water Heaters, Inc.

c. HESco Industries, Inc.

d. Precision Boilers.

e. PVI Industries, LLC.

f. RECO USA.

g. Smith, A. O. Water Products Company.

h. <Insert manufacturer's name.>

2. Storage-Tank Construction:  ASME-code steel with [150-psig (1035-kPa)] <Insert psig (kPa)> minimum working-pressure rating.

a. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

Retain subparagraph above or first subparagraph below.  If specific lining is required, verify availability for model selected.

c. Lining:  [Cement] [Glass] [Nickel plate] [Phenolic coating] [Sheet copper] <Insert material> complying with NSF 61 barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Temperature Control:  Adjustable thermostat.

g. Safety Control:  Automatic, high-temperature-limit cutoff device or system.

h. Relief Valves:  ASME rated and stamped and complying with ASME PTC 25.3, for combination temperature and pressure relief valves.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

4. Oil Burner:  Comply with UL 296 for use with No. 2 fuel oil.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.  Delete if list is not required.

a. [Available ]Manufacturers:

1) Adams Manufacturing Co.

2) Aero Environmental Ltd.

3) Beckett, R. W. Corporation.

4) Carlin Combustion Technology, Inc.

5) Gordon-Piatt Group; John Zink Company, LLC.

6) Power Flame, Inc.

7) Webster Engineering Co., L.L.C.

8) <Insert manufacturer's name.>

5. Safety Controls:  Automatic, high-temperature-limit and low-water cutoff devices or systems.

6. Draft Regulator:  Barometric type or adjustable-damper device.

7. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

If more than one oil-fired water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

8. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel-Oil Demand:  <Insert gpm (kg/s).>

e. Fuel-Oil Input:  <Insert Btu/h (W).>

f. Electrical Characteristics:

1) Volts:  [120] [240] [277] [480] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

g. Minimum Vent Diameter:  <Insert inches (mm).>

2.6 DUAL-FUEL WATER HEATERS

Refer to the Oil-Fired Water Heater Table at the end of the Evaluations for a list of manufacturers' products.  Use this table in combination with manufacturers' catalog or product data to insert series, type, model, and designations of other characteristics.

A. Description:  Comply with ANSI Z21.10.3/CSA 4.3 or UL 732 requirements appropriate for dual-fuel, gas and oil-fired water heaters.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. Aldrich Company.

b. Bock Water Heaters, Inc.

c. HESco Industries, Inc.

d. Precision Boilers.

e. PVI Industries, LLC.

f. RECO USA.

g. Smith, A. O. Water Products Company.

h. <Insert manufacturer's name.>

2. Storage-Tank Construction:  ASME-code steel with [150-psig (1035-kPa)] <Insert psig (kPa)> minimum working-pressure rating.

a. Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

1) NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1.

2) NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

Retain subparagraph above or below.  If specific lining is required, verify availability for model selected.

c. Lining:  [Cement] [Glass] [Nickel plate] [Phenolic coating] [Sheet copper] <Insert material> complying with NSF 61 barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

3. Factory-Installed, Storage-Tank Appurtenances:

a. Anode Rod:  Replaceable magnesium.

b. Dip Tube:  Provide unless cold-water inlet is near bottom of tank.

c. Drain Valve:  Corrosion-resistant metal complying with ASSE 1005.

Option in first subparagraph below is not applicable if applying for LEED certification.

d. Insulation:  Comply with ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

e. Jacket:  Steel with enameled finish.

f. Temperature Control:  Adjustable thermostat.

g. Relief Valves:  ASME rated and stamped and complying with ASME PTC 25.3, for combination temperature and pressure relief valves.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

4. Dual-Fuel Burners:  Combination gas-oil burner assembly, complying with appropriate requirements of UL 795; or comply with UL 296 for oil burners for No. 2 fuel oil and UL 795 for [natural-gas] [LP-gas] <Insert fuel gas> fuel.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.  Delete if list is not required.

a. [Available ]Manufacturers:

1) Gordon-Piatt Group; John Zink Company, LLC.

2) Power Flame, Inc.

3) Webster Engineering Co., L.L.C.

4) <Insert manufacturer's name.>

5. Safety Control:  Automatic, high-temperature-limit cutoff device or system.

6. Vent Connection:  According to standards of authorities having jurisdiction for dual-fuel water heaters.

7. Building Automation System Interface:  Normally closed dry contacts for enabling and disabling water heater.

If more than one dual-fuel water heater is required on Project, delete subparagraph and associated subparagraphs below and schedule heaters on Drawings.

8. Capacity and Characteristics:

a. Capacity:  <Insert gal. (L).>

b. Recovery:  <Insert gph (L/s)> at [100 deg F (56 deg C)] <Insert deg F (deg C)> temperature rise.

c. Temperature Setting:  [125 deg F (52 deg C)] [140 deg F (60 deg C)] <Insert temperature>.

d. Fuel Gas Demand:  <Insert cfh (L/s).>

e. Fuel Gas Input:  <Insert Btu/h (W).>

f. Fuel-Oil Demand:  <Insert gpm (kg/s).>

g. Fuel-Oil Input:  <Insert Btu/h (W).>

h. Electrical Characteristics:

1) Volts:  [120] [240] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4) Full-Load Amperes:  <Insert value.>

5) Minimum Circuit Ampacity:  <Insert value.>

6) Maximum Overcurrent Protection:  <Insert value.>

i. Minimum Vent Diameter:  <Insert inches (mm).>

2.7 COMPRESSION TANKS

Retain this Article only if small, non-ASME-code, diaphragm tanks with a capacity of 25 gal. (95 L) or less are required.  Small tanks are usually available with 150-psig (1035-kPa) working-pressure rating.  Large tanks are usually available with 100-psig (690-kPa) working-pressure rating.  A multiple, small-tank arrangement may be used to match system pressure and volume requirements.  Other compression tanks are specified in Division 22 Section "Facility Indoor Potable-Water Storage Tanks."

A. Description:  Steel, pressure-rated tank constructed with welded joints and factory-installed, butyl-rubber diaphragm.  Include air precharge to minimum system-operating pressure at tank.

Coordinate first subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

1. [Available ]Manufacturers:

a. AMTROL Inc.

b. Armstrong Pumps, Inc.

c. Flexcon Industries.

d. Honeywell Sparco.

e. Myers, F. E.; Pentair Pump Group (The).

f. Smith, A. O.; Aqua-Air Div.

g. State Industries, Inc.

h. Taco, Inc.

i. Watts Regulator Co.

j. Wessels Co.

k. <Insert manufacturer's name.>

2. Construction:

a. Tappings:  Factory-fabricated steel, welded to tank before testing and labeling.  Include ASME B1.20.1 pipe thread.

b. Interior Finish:  Comply with NSF 61 barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

c. Air-Charging Valve:  Factory installed.

If more than one compression tank is required on Project, delete subparagraph and associated subparagraphs below and schedule tanks on Drawings.

3. Capacity and Characteristics:

a. Working-Pressure Rating:  [100 psig (690 kPa)] [150 psig (1035 kPa)] <Insert psig (kPa)>.

b. Capacity Acceptable:  [2 gal. (7.6 L)] [4 gal. (15.1 L)] [7 gal. (26.5 L)] [10 gal. (37.9 L)] <Insert volume> minimum.

c. Air Precharge Pressure:  <Insert system pressure.>

2.8 WATER HEATER ACCESSORIES

A. Gas Shutoff Valves:  ANSI Z21.15/CGA 9.1, manually operated.  Furnish for installation in piping.

Delete first paragraph below if not required.

B. Gas Pressure Regulators:  ANSI Z21.18, appliance type.  Include pressure rating, capacity, and pressure differential required between gas supply and water heater.

C. Gas Automatic Valves:  ANSI Z21.21, appliance, electrically operated, on-off automatic valve.

D. Combination Temperature and Pressure Relief Valves:  Include relieving capacity at least as great as heat input, and include pressure setting less than water heater working-pressure rating.  Select each relief valve with sensing element that extends into storage tank.

1. Gas Water Heaters:  ANSI Z21.22/CSA 4.4.

2. Oil-Fired Water Heaters:  ASME rated and stamped and complying with ASME PTC 25.3.

E. Pressure Relief Valves:  Include pressure setting less than working-pressure rating of water heater.

1. Gas Water Heaters:  ANSI Z21.22/CSA 4.4.

2. Oil-Fired Water Heaters:  ASME rated and stamped and complying with ASME PTC 25.3.

Indicate on Drawings where each type of water heater support, in four paragraphs below, is required.  Delete support types not required.  Water heaters can also be installed at or above ceilings on suspended platforms or brackets.

F. Water Heater Stand and Drain Pan Units:  High-density-polyethylene-plastic, 18-inch- (457-mm-) high, enclosed-base stand complying with IAPMO PS 103 and IAS No. 2.  Include integral or separate drain pan with raised edge and NPS 1 (DN 25) drain outlet with ASME B1.20.1 pipe thread.

G. Water Heater Stands:  Water heater manufacturer's factory-fabricated steel stand for floor mounting and capable of supporting water heater and water.  Provide dimension that will support bottom of water heater a minimum of 18 inches (457 mm) above the floor.

H. Water Heater Mounting Brackets:  Water heater manufacturer's factory-fabricated steel bracket for wall mounting and capable of supporting water heater and water.

I. Drain Pans:  Corrosion-resistant metal with raised edge.  Provide dimensions not less than base of water heater and include drain outlet not less than NPS 3/4 (DN 20).

Retain first paragraph below only if required for multiple water heater arrangement.  Verify availability with manufacturers.  Some water heater manufacturers can provide piping manifold kits for their water heaters.  Larger manifolds can be field fabricated from water piping and valves.

J. Piping Manifold Kits:  Water heater manufacturer's factory-fabricated inlet and outlet piping arrangement for multiple-unit installation.  Include piping and valves for field assembly that is capable of isolating each water heater and of providing balanced flow through each water heater.

Option in paragraph below is not applicable if applying for LEED certification.

K. Piping-Type Heat Traps:  Field-fabricated piping arrangement according to ASHRAE/IESNA 90.1-2004[ or ASHRAE 90.2-2004].

2.9 SOURCE QUALITY CONTROL

A. Test and inspect water heater storage tanks, specified to be ASME-code construction, according to ASME Boiler and Pressure Vessel Code.

Retain first paragraph below if tank testing by manufacturer is required.  Retain option if testing of only commercial water heater tanks is required.

B. Hydrostatically test[ commercial] water heater storage tanks before shipment to minimum of one and one-half times pressure rating.

C. Prepare test reports.

PART 3 -  EXECUTION

3.1 WATER HEATER INSTALLATION

A. Install commercial water heaters on concrete bases.

1. Exception:  Omit concrete bases for commercial water heaters if installation on stand, bracket, suspended platform, or direct on floor is indicated.

Coordinate sizes and locations of concrete bases.  Verify structural requirements with structural engineer.

2. Concrete base construction requirements are specified in Division 22 Section "Common Work Results for Plumbing."

B. Install water heaters level and plumb, according to layout drawings, original design, and referenced standards.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices needing service are accessible.

Retain first paragraph below only if seismic restraint is required.

C. Install seismic restraints for commercial water heaters.  Anchor to substrate.

D. Install gas water heaters according to NFPA 54.

E. Install gas shutoff valves on gas supplies to gas water heaters without shutoff valves.

F. Install gas pressure regulators on gas supplies to gas water heaters without gas pressure regulators if gas pressure regulators are required to reduce gas pressure at burner.

G. Install automatic gas valves on gas supplies to gas water heaters, if required for operation of safety control.

H. Install oil-fired water heaters according to NFPA 31.

I. Install combination temperature and pressure relief valves in top portion of storage tanks.  Use relief valves with sensing elements that extend into tanks.  Extend commercial-water-heater, relief-valve outlet, with drain piping same as domestic water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

J. Install[ combination temperature and] pressure relief valves in water piping for water heaters without storage.  Extend commercial-water-heater relief-valve outlet, with drain piping same as domestic water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

K. Install water heater drain piping as indirect waste to spill by positive air gap into open drains or over floor drains.  Install hose-end drain valves at low points in water piping for water heaters that do not have tank drains.  Refer to Division 22 Section "Domestic Water Piping Specialties" for hose-end drain valves.

L. Install thermometer on outlet piping of water heaters.  Refer to Division 22 Section "Meters and Gages for Plumbing Piping" for thermometers.

Retain first paragraph below only if required.

M. Install pressure gage(s) on[ inlet and] outlet piping of commercial, fuel-fired water heater piping.  Refer to Division 22 Section "Meters and Gages for Plumbing Piping" for pressure gages.

N. Assemble and install inlet and outlet piping manifold kits for multiple water heaters.  Fabricate, modify, or arrange manifolds for balanced water flow through each water heater.  Include shutoff valve and thermometer in each water heater inlet and outlet, and throttling valve in each water heater outlet.  Refer to Division 22 Section "General-Duty Valves for Plumbing Piping" for general-duty valves and to Division 22 Section "Meters and Gages for Plumbing Piping" for thermometers.

O. Install piping-type heat traps on inlet and outlet piping of water heater storage tanks without integral or fitting-type heat traps.

P. Fill water heaters with water.

Retain paragraph below only if required.

Q. Charge compression tanks with air.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 22 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to water heaters to allow service and maintenance.  Arrange piping for easy removal of water heaters.

C. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

D. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with last paragraph above; revise to suit Project.

1. Leak Test:  After installation, test for leaks.  Repair leaks and retest until no leaks exist.

2. Operational Test:  After electrical circuitry has been energized, confirm proper operation.

3. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace water heaters that do not pass tests and inspections and retest as specified above.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain [instantaneous] [and] [commercial] water heaters.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 223400

FUEL-FIRED DOMESTIC WATER HEATERS
223400 - 1

