Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
09/03 (R 06/05)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 224700 - DRINKING FOUNTAINS AND WATER COOLERS
Edit the Section title to read either "Drinking Fountains" or "Water Coolers" if only one of these two types of fixtures is specified in this Section.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following [drinking fountains] [and] [water coolers] and related components:

Adjust list below to suit Project.

1. Drinking fountains.

2. Pressure water coolers.

3. Water-station water coolers.

4. Remote water coolers.

5. Fixture supports.

1.3 DEFINITIONS

Definitions below are from applicable standards, references, and model plumbing codes.  See Evaluations for a comprehensive list of definitions.  Retain terms that remain after this Section has been edited.  Edit terms only if required.

A. Accessible [Drinking Fountain] [or] [Water Cooler]:  Fixture that can be approached and used by people with disabilities.

B. Cast Polymer:  Dense, cast-filled-polymer plastic.

C. Drinking Fountain:  Fixture with nozzle for delivering stream of water for drinking.

D. Fitting:  Device that controls flow of water into or out of fixture.

E. Fixture:  Drinking fountain or water cooler unless one is specifically indicated.

F. Remote Water Cooler:  Electrically powered equipment for generating cooled drinking water.

G. Water Cooler:  Electrically powered fixture for generating and delivering cooled drinking water.

1.4 SUBMITTALS

A. Product Data:  For each fixture indicated.  Include rated capacities, furnished specialties, and accessories.

B. Shop Drawings:  Diagram power, signal, and control wiring.

C. Field quality-control test reports.

D. Operation and Maintenance Data:  For fixtures to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

First paragraph below is appropriate for private commercial projects.  Delete Public Laws 90-480 and 101-336 if not required by authorities having jurisdiction.

B. Regulatory Requirements:  Comply with requirements in ICC A117.1, "Accessible and Usable Buildings and Facilities"[; Public Law 90-480, "Architectural Barriers Act" ; and Public Law 101-336, "Americans with Disabilities Act" ;] for fixtures for people with disabilities.

C. NSF Standard:  Comply with NSF 61, "Drinking Water System Components--Health Effects," for fixture materials that will be in contact with potable water.

Retain paragraph below for drinking fountains.

D. ARI Standard:  Comply with ARI's "Directory of Certified Drinking Water Coolers" for style classifications.

Retain both paragraphs below for water coolers.

E. ARI Standard:  Comply with ARI 1010, "Self-Contained, Mechanically Refrigerated Drinking-Water Coolers," for water coolers and with ARI's "Directory of Certified Drinking Water Coolers" for type and style classifications.

F. ASHRAE Standard:  Comply with ASHRAE 34, "Designation and Safety Classification of Refrigerants," for water coolers.  Provide HFC 134a (tetrafluoroethane) refrigerant, unless otherwise indicated.

1.6 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Filter Cartridges:  Equal to <Insert number> percent of amount installed for each type and size indicated, but no fewer than <Insert number> of each.

PART 2 -  PRODUCTS

Articles in Part 2 specify drinking fountains and water coolers.  Retain and edit only those articles applicable to Project.  See Editing Instruction No. 2 in the Evaluations for cautions about combinations of fixture components.

2.1 DRINKING FOUNTAINS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Refer to the table for drinking fountains in the Evaluations for lists of manufacturers' products.  Use this table in combination with manufacturers' catalogs or product data to insert series, type, model, and designation of other characteristics.

Copy and edit paragraph and subparagraphs below for each freestanding-type drinking fountain.

A. Drinking Fountains, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Filtrine Manufacturing Company; Drinking Water Division.

b. Halsey Taylor.

c. Haws Corporation.

d. Most Dependable Fountains, Inc.

e. Murdock, Inc.

f. Oasis Corporation.

g. Stern-Williams Co., Inc.

h. Sunroc Corp.

i. <Insert manufacturer's name.>

4. Description:  [Accessible, ]Style F, freestanding drinking fountain.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Pedestal:

1) Material:  [Concrete] [Painted cast iron or steel] <Insert material>.

2) Shape:  [Rectangular] [Round] <Insert shape> [with offset to receptor] [with side receptor(s)].

b. Receptor(s):

1) Number:  [One] [Two] [Three].

2) Material:  [Bronze] [Chrome-plated brass or stainless steel] <Insert material>.

3) Shape:  [Rectangular] [Round] [Rounded front] <Insert shape>.

4) Bubbler:  One for each receptor, with adjustable stream regulator, located on deck.

c. Controls:  [Foot pedal] [Push bar] [Push button] <Insert control> with adjustable stream regulator.

d. Access to Internal Components:  Panel in pedestal.

e. Supply:  [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] with ball, gate, or globe valve.

f. Drain:  Grid with NPS 1-1/4 (DN 32) minimum [horizontal waste and trap complying with ASME A112.18.2] [waste to drainage system].

Copy and edit paragraph and subparagraphs below for each antifreeze, freestanding-type drinking fountain.

B. Drinking Fountains, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Murdock, Inc.

b. <Insert manufacturer's name.>

4. Description:  [Accessible, ]Style F, antifreeze, freestanding drinking fountain designed to operate without draining into ground.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs below may be reduced or omitted.

a. Pedestal:  Rectangular, painted cast iron or steel.

b. Receptor:  Rectangular, chrome-plated brass or stainless steel with bubbler.

c. Control:  Foot pedal with control valve assembly.

d. Supply:  NPS 1/2 (DN 15) with underground shutoff and flow-control valve assembly.

e. Drain:  Grid with [NPS 1 (DN 25)] [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)] <Insert pipe size> minimum waste to drainage system.

f. Bury Depth, Grade to Valve Components:  [36 inches (915 mm)] [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert depth>.

Copy and edit paragraph and subparagraphs below for each wall-mounting-type drinking fountain.

C. Drinking Fountains, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of three lists below.

Select from manufacturers below for metal drinking fountains.

a. Elkay Manufacturing Co.

b. Filtrine Manufacturing Company; Drinking Water Division.

c. Halsey Taylor.

d. Haws Corporation.

e. Murdock, Inc.

f. Oasis Corporation.

g. Stern-Williams Co., Inc.

h. Sunroc Corp.

i. <Insert manufacturer's name.>

Select from manufacturers below for cast-polymer drinking fountains.

j. Elkay Manufacturing Co.

k. Filtrine Manufacturing Company; Drinking Water Division.

l. Halsey Taylor.

m. Haws Corporation.

n. Stern-Williams Co., Inc.

o. Sunroc Corp.

p. <Insert manufacturer's name.>

Select from manufacturers below for vitreous-china drinking fountains:

q. American Standard, Inc.

r. Crane Plumbing, L.L.C./Fiat Products.

s. Eljer.

t. Kohler Co.

u. Sunroc Corp.

v. <Insert manufacturer's name.>

4. Description:  [Accessible, ]Style W, wall-mounting drinking fountain.

a. Material:  [Bronze] [Metal] [Cast polymer] [Stainless steel] [Vitreous china complying with ASME 112.19.2M for drinking fountains with backsplash].

b. Receptor Shape:  [Rectangular] [Round] [Rounded front] <Insert shape>.

Retain first subparagraph below only for stainless-steel drinking fountains and only if required.  Include size if necessary.

c. Back Panel:  Stainless-steel wall plate behind drinking fountain.

d. Bubblers:  [One] [Two] [Three], with adjustable stream regulator, located on deck.

e. Control:  [Push button] [Push bar] <Insert control>.

f. Supply:  NPS 3/8 (DN 10) with ball, gate, or globe valve.

g. Drain:  Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap complying with ASME A112.18.2.

h. Support:  Type I, water cooler carrier.  Refer to "Fixture Supports" Article.

Copy and edit paragraph and subparagraphs below for each wall-mounting, semirecessed-type drinking fountain.

D. Drinking Fountains, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of two lists below.

Select from manufacturers below for metal drinking fountains.

a. Elkay Manufacturing Co.

b. Filtrine Manufacturing Company; Drinking Water Division.

c. Halsey Taylor.

d. Haws Corporation.

e. Oasis Corporation.

f. Sunroc Corp.

g. <Insert manufacturer's name.>

Select from manufacturers below for vitreous-china drinking fountains.

h. Crane Plumbing, L.L.C./Fiat Products.

i. Kohler Co.

j. <Insert manufacturer's name.>

4. Description:  [Accessible, ]Style WS, wall-mounting, semirecessed drinking fountain.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs below may be reduced or omitted.

a. Material:  [Stainless steel] [Bronze] [Vitreous china complying with ASME A112.19.2M for semirecessed drinking fountains].

b. Receptor Shape:  Concave with projecting bowl.

c. Bubbler:  One, with adjustable stream regulator, located on deck.

d. Control:  [Push button] [Push bar] <Insert control>.

e. Supply:  NPS 3/8 (DN 10) with ball, gate, or globe valve.

f. Drain:  Integral punched grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap complying with ASME A112.18.2.

g. Support:  Mounting frame or brackets for attaching to substrate.

Copy and edit paragraph and subparagraphs below for each stainless-steel, recessed-type drinking fountain.

E. Drinking Fountains, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Filtrine Manufacturing Company; Drinking Water Division.

c. Halsey Taylor.

d. Haws Corporation.

e. Oasis Corporation.

f. Sunroc Corp.

g. <Insert manufacturer's name.>

4. Description:  Style RE, stainless-steel, recessed drinking fountain.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in six subparagraphs below may be reduced or omitted.

a. Receptor Shape:  Concave with flush wall flange.

b. Bubbler:  One, with adjustable stream regulator, located on deck.

c. Control:  Push [button] [bar].

d. Supply:  NPS 3/8 (DN 10) with ball, gate, or globe valve.

e. Drain:  Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap complying with ASME A112.18.2.

f. Support:  Mounting frame or brackets for attaching to substrate.

2.2 PRESSURE WATER COOLERS

Copy and edit paragraph and subparagraphs below for each freestanding- or flush-to-wall-type water cooler.

A. Water Coolers, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Halsey Taylor.

c. Haws Corporation.

d. Larco, Inc.

e. Oasis Corporation.

f. Sunroc Corp.

g. <Insert manufacturer's name.>

4. Description:  ARI 1010, Type PB, pressure with bubbler, [Style F, freestanding] [or] [Style FW, flush-to-wall] water cooler.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet:  [All stainless steel] [Steel with powder-coat-finish] [Vinyl-covered steel with stainless-steel top] <Insert material>.

b. Bubbler:  One, with adjustable stream regulator, located on deck.

c. Control:  [Push button] [Foot pedal] <Insert control>.

d. Supply:  NPS 3/8 (DN 10) with ball, gate, or globe valve.

Retain first subparagraph below only if required.

e. Filter:  One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

f. Drain:  Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap complying with ASME A112.18.2.

g. Cooling System:  Electric, with[ precooler,] hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

1) Capacity:  [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] [10 gph (0.0105 L/s)] [14 gph (0.0147 L/s)] <Insert value> of 50 deg F (10 deg C) cooled water from 80 deg F (27 deg C) inlet water and 90 deg F (32 deg C) ambient air temperature.

2) Electrical Characteristics:  [1/6] [1/5] [1/4] hp; 120-V ac; single phase; 60 Hz.

Copy and edit paragraph and subparagraphs below for each freestanding-type water cooler.

B. Water Coolers, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Oasis Corporation.

b. <Insert manufacturer's name.>

4. Description:  ARI 1010, Type PBC, pressure with bubbler and compartment, Style F, freestanding water cooler.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in seven subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet: [All stainless steel] [Vinyl-covered steel with stainless-steel top] <Insert material> with refrigerated compartment in front panel.

b. Bubbler:  One, with adjustable stream regulator, located on deck.

c. Control:  [Push button] <Insert control>.

d. Supply:  NPS 3/8 (DN 10) with ball, gate, or globe valve.

Retain first subparagraph below only if required.

e. Filter:  One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

f. Drain:  Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap complying with ASME A112.18.2.

g. Cooling System:  Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

1) Capacity:  [3 gph (0.0032 L/s)] <Insert value> of 50 deg F (10 deg C) cooled water from 80 deg F (27 deg C) inlet water and 90 deg F (32 deg C) ambient air temperature.

2) Electrical Characteristics:  [1/8] <Insert value> hp; 120-V ac; single phase; 60 Hz.

Copy and edit paragraph and subparagraphs below for each wall-mounting-type water cooler.

C. Water Coolers, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Halsey Taylor.

c. Haws Corporation.

d. Larco, Inc.

e. Oasis Corporation.

f. Sunroc Corp.

g. <Insert manufacturer's name.>

4. Description:  [Accessible, ]ARI 1010, Type PB, pressure with bubbler, Style W, wall-mounting water cooler for [adult] [child]-mounting height.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs and associated subparagraphs below may be reduced or omitted.  Verify availability of skirt kit in first subparagraph if required for selected fixture.

a. Cabinet:  [Single] [Bilevel with two attached cabinets] [Bilevel with two attached cabinets and with bilevel skirt kit], [all stainless steel] [vinyl-covered steel with stainless-steel top] <Insert material>.

b. Bubbler:  One, with adjustable stream regulator, located on each cabinet deck.

c. Control:  [Push button] [Push bar] <Insert control>.

d. Supply:  NPS 3/8 (DN 10) with ball, gate, or globe valve.

Retain first subparagraph below only if required.

e. Filter:  One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

f. Drain(s):  Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap complying with ASME A112.18.1.

g. Cooling System:  Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

1) Capacity:  [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] <Insert value> of 50 deg F (10 deg C) cooled water from 80 deg F (27 deg C) inlet water and 90 deg F (32 deg C) ambient air temperature.

2) Electrical Characteristics:  [1/6] [1/5] [1/4] [1/3] hp; 120-V ac; single phase; 60 Hz.

h. Support:  Type [I] [II], water cooler carrier.  Refer to "Fixture Supports" Article.

Copy and edit paragraph and subparagraphs below for each semirecessed-type water cooler.

D. Water Coolers, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Halsey Taylor.

c. Haws Corporation.

d. Oasis Corporation.

e. Sunroc Corp.

f. <Insert manufacturer's name.>

4. Description:  [Accessible, ]ARI 1010, Type PB, pressure with bubbler, Style WS, semirecessed water cooler.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet: [All stainless steel] [Vinyl-covered steel with stainless-steel top] <Insert material>.

b. Bubbler:  One, with adjustable stream regulator, located on deck.

c. Control:  [Push button] [Push bar] <Insert control>.

d. Supply:  NPS 3/8 (DN 10) with ball, gate, or globe valve.

Retain first subparagraph below only if required.

e. Filter:  One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

f. Drain:  Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap complying with ASME A112.18.2.

g. Cooling System:  Electric, with [precooler, ]hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

1) Capacity:  [8 gph (0.0084 L/s)] [12 gph (0.0126 L/s)] <Insert value> of 50 deg F (10 deg C) cooled water from 80 deg F (27 deg C) inlet water and 90 deg F (32 deg C) ambient air temperature.

2) Electrical Characteristics:  [1/6] [1/5] hp; 120-V ac; single phase; 60 Hz.

h. Support:  Mounting frame or brackets for attaching to substrate.

Copy and edit paragraph and subparagraphs below for each recessed-type water cooler.

E. Water Coolers, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Halsey Taylor.

c. Haws Corporation.

d. Oasis Corporation.

e. Sunroc Corp.

f. <Insert manufacturer's name.>

4. Description:  ARI 1010, Type PB, pressure with bubbler, Style RE, recessed water cooler.

If-basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in nine subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet:  All stainless steel.

b. Bubbler:  One, with adjustable stream regulator, located on deck.

c. Control:  Push [button] [bar].

d. Supply:  NPS 3/8 (DN 10) with ball, gate, or globe valve.

Retain first subparagraph below only if required.

e. Filter:  One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

f. Drain:  Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap complying with ASME A112.18.2.

g. Cooling System:  Electric, with [precooler, ]hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

1) Capacity:  [8 gph (0.0084 L/s)] [12 gph (0.0126 L/s)] <Insert value> of 50 deg F (10 deg C) cooled water from 80 deg F (27 deg C) inlet water and 90 deg F (32 deg C) ambient air temperature.

2) Electrical Characteristics:  [1/6] [1/5] hp; 120-V ac; single phase; 60 Hz.

h. Ventilation Grille:  Stainless steel, located [above] [below] fountain.

i. Support:  Mounting frame for attaching to substrate.

2.3 WATER-STATION WATER COOLERS

Only two manufacturers were found that make this type of water cooler.  These units are not listed by ARI but are made to comply with ARI 1010.  Units are often custom designed and fabricated to suit intended applications.  Edit this Article as required for specific variations and options.

Copy and edit paragraph and subparagraphs below for each water-station configuration, freestanding, cabinet-type water cooler with top-mounting glass fillers.

A. Water Coolers, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Filtrine Manufacturing Company; Drinking Water Division.

b. Larco, Inc.

c. <Insert manufacturer's name.>

4. Description:  Water-station configuration, freestanding, cabinet water cooler with top-mounting glass fillers.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet:  [All stainless steel] [Enameled-steel panels with stainless-steel top], 0.05 inch (1.3 mm) thick; and [32 inches (813 mm)] [36 inches (915 mm)] high.  <Insert width and depth if required.>

b. Receptors:  [Two] [Four] stainless-steel bowls, with grid drain and bottom outlet in top;[ with two] facing front[ and two facing back].

c. Glass Fillers:  [Two] [Four], [push-back type] [pedestal type], on top, over receptors.

Delete first subparagraph below if not required, or retain and edit to suit Project.

d. Tray Slides:  One on front[ and one on back], stainless steel.

e. Supply:  NPS 1/2 (DN 15) with ball, gate, or globe valve, and connected to filter, chiller, and each glass filler.

f. Filter:  One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

g. Drain:  Waste piping from each receptor connected to [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], [trap and waste to wall] [indirect waste to floor receptor] complying with ASME A112.18.2.

h. Cooling System:  Electric, complying with ARI 1010, for Type R remote water coolers.

1) Chassis:  Galvanized or corrosion-resistant-coated steel.

2) Chiller:  Hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, and refrigerant.

3) Storage Tank:  [2 gal. (7.6 L)] [4 gal. (15.1 L)] [6 gal. (22.7 L)] [14 gal. (53 L)] [25 gal. (95 L)], stainless steel.

4) Controls:  Adjustable thermostat.

5) One-Hour Peak Capacity Rate:  [8 gph (0.0084 L/s)] [12 gph (0.0126 L/s)] [18 gph (0.0189 L/s)] [29 gph (0.0305 L/s)] [50 gph (0.0526 L/s)] <Insert value> of 50 deg F (10 deg C) cooled water from 80 deg F (27 deg C) inlet water and 90 deg F (32 deg C) ambient air temperature.

6) Electrical Characteristics:  [1/5] [1/4] [1/3] [1/2] [3/4] hp; [120] [240] [277] [480]-V ac; single phase; 60 Hz.

Copy and edit paragraph and subparagraphs below for each water-station configuration, freestanding, cabinet-type water cooler with front-mounting glass fillers.

B. Water Coolers, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Filtrine Manufacturing Company; Drinking Water Division.

b. Larco, Inc.

c. <Insert manufacturer's name.>

4. Description:  Water-station configuration, freestanding, cabinet water cooler with front-mounting glass fillers.

If basis-of-design product manufacturer's name, product name or designation, and description above are explicit enough, requirements in eight subparagraphs and associated subparagraphs below may be reduced or omitted.

a. Cabinet:  [All stainless steel] [Enameled-steel panels with stainless-steel top], 0.05 inch (1.3 mm) thick; and [42 inches (1067 mm)] [48 inches (1219 mm)] high.  <Insert width and depth if required.>

b. Receptors:  [One] [Two] stainless-steel tray(s), with antisplash design, drain, and bottom outlet, in vertical panel(s)[, with one] facing front[ and one facing back].

c. Glass Fillers:  [Two] [Four], [push-back type,] on vertical panel(s), over receptor(s).

d. Shelves:  [One] [Two], stainless steel, on each side panel.

e. Supply:  NPS 1/2 (DN 15) with ball, gate, or globe valve, and connected to filter, chiller, and each glass filler.

f. Filter:  One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

g. Drain:  [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)], [trap and waste to wall] [indirect waste to floor receptor] complying with ASME A112.18.2.

h. Cooling System:  Electric, complying with ARI 1010, for Type R remote water coolers.

1) Chassis:  Galvanized or corrosion-resistant-coated steel.

2) Chiller:  Hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, and refrigerant.

3) Storage Tank:  [6 gal. (22.7 L)] [14 gal. (53 L)] [25 gal. (95 L)] [30 gal. (113.6 L)] [40 gal. (151.4 L)], stainless steel.

4) Controls:  Adjustable thermostat.

5) One-Hour Peak Capacity Rate:  [18 gph (0.0189 L/s)] [29 gph (0.0305 L/s)] [50 gph (0.0526 L/s)] [65 gph (0.0684 L/s)] [85 gph (0.0894 L/s)] <Insert value> of 50 deg F (10 deg C) cooled water from 80 deg F (27 deg C) inlet water and 90 deg F (32 deg C) ambient air temperature.

6) Electrical Characteristics:  [1/3] [1/2] [3/4] [1] [1-1/2] hp; [120] [240] [277] [480]-V ac; single phase; 60 Hz.

2.4 REMOTE WATER COOLERS

Caution:  Equipment in this Article is suitable only for small cooled-water systems.  Large, central, cooled-water systems are beyond the scope of this Section.

A. Water Coolers, <Insert drawing designation>:

Retain one of first three subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

3. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

a. Elkay Manufacturing Co.

b. Filtrine Manufacturing Company; Drinking Water Division.

c. Halsey Taylor.

d. Haws Corporation.

e. Oasis Corporation.

f. Sunroc Corp.

g. <Insert manufacturer's name.>

4. Description:  ARI 1010, Style R, remote chiller equipment for installation separate from drinking fountains.[ Include] [filter,] [reverse-osmosis system] [and] [ ultra-violet-disinfection equipment][.]

a. Cooling System:  Electric.

1) Chassis:  Galvanized or corrosion-resistant-coated steel.

2) Chiller:  Hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, and refrigerant.

Storage capacity is usually small.  Delete storage capacity in first subparagraph below unless critical.

3) Storage Tank:  [0.5 gal. (1.9 L)] [4 gal. (15.1 L)] <Insert gal. (L)>, stainless steel.

4) Controls:  Adjustable thermostat.

5) Capacity:  [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] [14 gph (0.0147 L/s)] <Insert value> of 50 deg F (10 deg C) cooled water from 80 deg F (27 deg C) inlet water and 90 deg F (32 deg C) ambient air temperature.

6) Electrical Characteristics:  [1/5] [1/4] [1/3] <Insert value> hp; [120] [240] [277] [480]-V ac; single phase; 60 Hz.

Retain subparagraph below only if required.

b. Ventilation Grille:  Stainless steel, <Insert size>.

Retain subparagraph below only if required.  Reverse-osmosis systems and UV-disinfection equipment is available, but cost is excessive for the flow rates of these chillers.  Other filters are specified in Division 22 Section "Domestic Water Filtration Equipment."

c. Filter:  One or more water filters complying with NSF 42 and NSF 53 for cyst and lead reduction to below EPA standards; with capacity sized for unit peak flow rate.

2.5 FIXTURE SUPPORTS

Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Josam Co.

2. MIFAB Manufacturing, Inc.

3. Smith, Jay R. Mfg. Co.

4. Tyler Pipe; Wade Div.

5. Watts Drainage Products Inc.; a div. of Watts Industries, Inc.

6. Zurn Plumbing Products Group; Specification Drainage Operation.

7. <Insert manufacturer's name.>

C. Description:  ASME A112.6.1M, water cooler carriers.  Include vertical, steel uprights with feet and tie rods and bearing plates with mounting studs matching fixture to be supported.

1. Type I:  Hanger-type carrier with two vertical uprights.

2. Type II:  Bilevel, hanger-type carrier with three vertical uprights.

3. Supports for Accessible Fixtures:  Include rectangular, vertical, steel uprights instead of steel pipe uprights.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in for water and waste piping systems to verify actual locations of piping connections before fixture installation.  Verify that sizes and locations of piping and types of supports match those indicated.

B. Examine walls and floors for suitable conditions where fixtures are to be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATIONS

A. Use carrier off-floor supports for wall-mounting fixtures, unless otherwise indicated.

B. Use mounting frames for recessed water coolers, unless otherwise indicated.

C. Set freestanding and pedestal drinking fountains on floor.

D. Set remote water coolers on floor, unless otherwise indicated.

E. Use chrome-plated brass or copper tube, fittings, and valves in locations exposed to view.  Plain copper tube, fittings, and valves may be used in concealed locations.

3.3 INSTALLATION

A. Install off-floor supports affixed to building substrate and attach wall-mounting fixtures, unless otherwise indicated.

B. Install mounting frames affixed to building construction and attach recessed water coolers to mounting frames, unless otherwise indicated.

C. Install fixtures level and plumb.  For fixtures indicated for children, install at height required by authorities having jurisdiction.

D. Install water-supply piping with shutoff valve on supply to each fixture to be connected to water distribution piping.  Use ball, gate, or globe valve.  Install valves in locations where they can be easily reached for operation.  Valves are specified in Division 22 Section "General-Duty Valves for Plumbing Piping."

E. Install trap and waste piping on drain outlet of each fixture to be connected to sanitary drainage system.

F. Install pipe escutcheons at wall penetrations in exposed, finished locations.  Use deep-pattern escutcheons where required to conceal protruding pipe fittings.  Escutcheons are specified in Division 22 Section "Common Work Results for Plumbing."

Delete paragraph below if sealants are provided in Division 07 Section "Joint Sealants."

G. Seal joints between fixtures and walls and floors using sanitary-type, one-part, mildew-resistant, silicone sealant.  Match sealant color to fixture color.  Sealants are specified in Division 07 Section "Joint Sealants."

3.4 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 22 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping.  Use size fittings required to match fixtures.

C. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

D. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.5 FIELD QUALITY CONTROL

Retain this Article for water coolers.

A. Water Cooler Testing:  After electrical circuitry has been energized, test for compliance with requirements.  Test and adjust controls and safeties.

1. Remove and replace malfunctioning units and retest as specified above.

2. Report test results in writing.

3.6 ADJUSTING

A. Adjust fixture flow regulators for proper flow and stream height.

B. Adjust water cooler temperature settings.

3.7 CLEANING

A. After completing fixture installation, inspect unit.  Remove paint splatters and other spots, dirt, and debris.  Repair damaged finish to match original finish.

B. Clean fixtures, on completion of installation, according to manufacturer's written instructions.

END OF SECTION 224700

	DRINKING FOUNTAINS AND WATER COOLERS
	224700 - 1



