Copyright 2005 AIA
MASTERSPEC Full Length
03/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 230516 - EXPANSION FITTINGS AND LOOPS FOR HVAC PIPING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Metal-bellows expansion joints.

2. Expansion compensators.

3. Rubber expansion joints.

4. Flexible-hose expansion joints.

5. Packed slip expansion joints.

6. Flexible ball joints.

7. Pipe bends and loops.

8. Alignment guides and anchors.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. BR:  Butyl rubber.

B. Buna-N:  Nitrile rubber.

C. CR:  Chlorosulfonated polyethylene synthetic rubber.

D. CSM:  Chlorosulfonyl-polyethylene rubber.

E. EPDM:  Ethylene-propylene-diene terpolymer rubber.

F. NR:  Natural rubber.

G. PTFE:  Polytetrafluoroethylene plastic.

1.4 PERFORMANCE REQUIREMENTS

A. Compatibility:  Products shall be suitable for piping system fluids, materials, working pressures, and temperatures.

B. Capability:  Products shall absorb 200 percent of maximum axial movement between anchors.

1.5 SUBMITTALS

First paragraph below is defined in Division 01 Section "Submittal Procedures" as "Action Submittal."

A. Product Data:  For each type of product indicated.

First paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

B. Delegated-Design Submittal:  For each anchor and alignment guide indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Design Calculations:  Calculate requirements for thermal expansion of piping systems and for selecting and designing expansion joints, loops, and bends.

2. Anchor Details:  Detail fabrication of each anchor indicated.  Show dimensions and methods of assembly and attachment to building structure.

3. Alignment Guide Details:  Detail field assembly and attachment to building structure.

4. Schedule:  Indicate type, manufacturer's number, size, material, pressure rating, end connections, and location for each expansion joint.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

C. Welding certificates.

Retain first paragraph below for material or product certificates from manufacturers.

D. Product Certificates:  For each type of pipe expansion joint, signed by product manufacturer.

E. Maintenance Data:  For pipe expansion joints to include in maintenance manuals.

1.6 QUALITY ASSURANCE

Retain "Welding Qualifications" Paragraph below if shop or field welding is required.  If retaining, also retain "Welding certificates" Paragraph in "Submittals" Article.

A. Welding Qualifications:  Qualify procedures and personnel according to the following:

Retain applicable subparagraphs below.

1. Steel Shapes and Plates:  AWS D1.1, "Structural Welding Code - Steel."

2. Welding to Piping:  ASME Boiler and Pressure Vessel Code:  Section IX.

PART 2 -  PRODUCTS

2.1 EXPANSION JOINTS

Coordinate expansion-joint pressure and temperature ratings with piping systems.

A. Metal-Bellows Expansion Joints:  ASTM F 1120, circular-corrugated-bellows type with external tie rods.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Adsco Manufacturing, LLC.

b. Anamet, Inc.

c. Badger Industries.

d. Expansion Joint Systems, Inc.

e. Flex-Hose Co., Inc.

f. Flexicraft Industries.

g. Flex-Pression, Ltd.

h. Flex-Weld, Inc.

i. Hyspan Precision Products, Inc.

j. Metraflex, Inc.

k. Piping Technology & Products, Inc.

l. Proco Products, Inc.

m. Senior Flexonics, Inc.; Pathway Division.

n. Tozen America Corp.

o. Unaflex Inc.

p. WahlcoMetroflex.

q. <Insert manufacturer's name.>

3. Metal-Bellows Expansion Joints for Copper Piping:  [Single] [Single- or multiple] [Multiple]-ply phosphor-bronze bellows, copper pipe end connections, and brass shrouds.

4. Metal-Bellows Expansion Joints for Stainless-Steel Waterway:  Single-ply stainless-steel bellows, stainless-steel-pipe end connections, and steel shroud.

5. Metal-Bellows Expansion Joints for Steel Piping:  [Single] [Single- or multiple] [Multiple]-ply stainless-steel bellows, steel pipe end connections, and carbon-steel shroud.

6. Minimum Pressure Rating:  [150 psig (1035 kPa)] [175 psig (1200 kPa)] <Insert measurement>, unless otherwise indicated.

7. Configuration:  [Single] [Single- or double] [Double]-bellows type[ with base], unless otherwise indicated.

8. End Connections:  [Flanged] [Flanged or weld] [Weld].

B. Expansion Compensators:  Double-ply corrugated steel, stainless-steel, or copper-alloy bellows in a housing with internal guides, antitorque device, and removable end clip for positioning.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Adsco Manufacturing, LLC.

b. Flexicraft Industries.

c. Flex-Pression, Ltd.

d. Flex-Weld, Inc.

e. Hyspan Precision Products, Inc.

f. Metraflex, Inc.

g. Senior Flexonics, Inc.; Pathway Division.

h. Unaflex Inc.

i. <Insert manufacturer's name.>

3. Minimum Pressure Rating:  [150 psig (1035 kPa)] [175 psig (1200 kPa)] <Insert measurement>, unless otherwise indicated.

4. Configuration for Copper Piping:  Two-ply phosphor-bronze or stainless-steel bellows and bronze or stainless-steel shroud.

5. Configuration for Steel Piping:  Two-ply stainless-steel bellows and carbon-steel shroud.

6. End Connections for Copper Tubing NPS 2 (DN 50) and Smaller:  [Solder joint] [Solder joint or threaded] [Threaded].

7. End Connections for Copper Tubing NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  [Solder joint] [Solder joint or threaded] [Threaded].

8. End Connections for Steel Pipe NPS 2 (DN 50) and Smaller:  Threaded.

9. End Connections for Steel Pipe NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  [Flanged] [Flanged or threaded] [Threaded] [Weld].

C. Rubber Expansion Joints:  ASTM F 1123, fabric-reinforced rubber with external control rods and complying with FSA's "Technical Handbook:  Non-Metallic Expansion Joints and Flexible Pipe Connectors."

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Flex-Hose Co., Inc.

b. Flexicraft Industries.

c. Flex-Weld, Inc.

d. Garlock Sealing Technologies.

e. General Rubber Corp.

f. Mason Industries, Inc.; Mercer Rubber Co.

g. Metraflex, Inc.

h. MG Piping Products Co.

i. Proco Products, Inc.

j. Red Valve Company, Inc.

k. Senior Flexonics, Inc.; Pathway Division.

l. Tozen America Corp.

m. Unaflex Inc.

n. Vibration Mountings & Controls, Inc.

o. <Insert manufacturer's name.>

3. Arch Type:  [Single] [Single or multiple] [Multiple] arches.

4. Spherical Type:  [Single] [Single or multiple] [Multiple] spheres.

Pressure-temperature ratings in first three subparagraphs below are generally minimum values.  Consult manufacturers' literature for options available.

a. Minimum Pressure and Temperature Ratings for NPS 1-1/2 to NPS 4 (DN 40 to DN 100):  [150 psig (1035 kPa) at 220 deg F (104 deg C)] <Insert other>.

b. Minimum Pressure and Temperature Ratings for NPS 5 and NPS 6 (DN 125 and DN 150):  [140 psig (966 kPa) at 200 deg F (93 deg C)] <Insert other>.

c. Minimum Pressure and Temperature Ratings for NPS 8 to NPS 12 (DN 200 to DN 300):  [140 psig (966 kPa) at 180 deg F (82 deg C)] <Insert other>.

Retain only those materials in first subparagraph below that are required.  Indicate materials on Drawings if more than one is required.  See Evaluations for discussion about rubber materials.

5. Material:  [BR] [Buna-N] [CR] [CSM] [EPDM] [NR].

6. End Connections:  Full-faced, integral, steel flanges with steel retaining rings.

D. Flexible-Hose Expansion Joints:  Manufactured assembly with two flexible-metal-hose legs joined by long-radius, 180-degree return bend or center section of flexible hose; with inlet and outlet elbow fittings, corrugated-metal inner hoses, and braided outer sheaths.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Flex-Hose Co., Inc.

b. Flexicraft Industries.

c. Flex-Pression, Ltd.

d. Metraflex, Inc.

e. <Insert manufacturer's name.>

Retain one of first two subparagraphs below to suit pressure and temperature requirements of systems in which these devices are installed.

3. Flexible-Hose Expansion Joints for Copper Piping:  Copper-alloy fittings with [solder-] <Insert other> joint end connections.

a. NPS 2 (DN 50) and Smaller:  Bronze hoses and single-braid bronze sheaths with 450 psig at 70 deg F (3100 kPa at 21 deg C) and 340 psig at 450 deg F (2340 kPa at 232 deg C) ratings.

b. NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Stainless-steel hoses and single-braid, stainless-steel sheaths with 300 psig at 70 deg F (2070 kPa at 21 deg C) and 225 psig at 450 deg F (1550 kPa at 232 deg C) ratings.

4. Flexible-Hose Expansion Joints for Copper Piping:  Copper-alloy fittings with [solder-] <Insert other> joint end connections.

a. NPS 2 (DN 50) and Smaller:  Bronze hoses and double-braid bronze sheaths with 700 psig at 70 deg F (4830 kPa at 21 deg C) and 500 psig at 450 deg F (3450 kPa at 232 deg C) ratings.

b. NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Stainless-steel hoses and double-braid, stainless-steel sheaths with 420 psig at 70 deg F (2890 kPa at 21 deg C) and 315 psig at 450 deg F (2170 kPa at 232 deg C) ratings.

Retain one of two subparagraphs below to suit pressure and temperature requirements of systems in which these devices are installed.

5. Flexible-Hose Expansion Joints for Steel Piping:  Carbon-steel fittings with threaded end connections for NPS 2 (DN 50) and smaller and [flanged] [weld] end connections for NPS 2-1/2 (DN 65) and larger.

a. NPS 2 (DN 50) and Smaller:  Stainless-steel hoses and single-braid, stainless-steel sheaths with 450 psig at 70 deg F (3100 kPa at 21 deg C) and 325 psig at 600 deg F (2250 kPa at 315 deg C) ratings.

b. NPS 2-1/2 to NPS 6 (DN 65 to DN 150):  Stainless-steel hoses and single-braid, stainless-steel sheaths with 200 psig at 70 deg F (1380 kPa at 21 deg C) and 145 psig at 600 deg F (1000 kPa at 315 deg C) ratings.

c. NPS 8 to NPS 12 (DN 200 to DN 300):  Stainless-steel hoses and single-braid, stainless-steel sheaths with 125 psig at 70 deg F (860 kPa at 21 deg C) and 90 psig at 600 deg F (625 kPa at 315 deg C) ratings.

6. Flexible-Hose Expansion Joints for Steel Piping:  Carbon-steel fittings with threaded end connections for NPS 2 (DN 50) and smaller and [flanged] [weld] end connections for NPS 2-1/2 (DN 65) and larger.

a. NPS 2 (DN 50) and Smaller:  Stainless-steel hoses and double-braid, stainless-steel sheaths with 700 psig at 70 deg F (4830 kPa at 21 deg C) and 515 psig at 600 deg F (3550 kPa at 315 deg C) ratings.

b. NPS 2-1/2 to NPS 6 (DN 65 to DN 150):  Stainless-steel hoses and double-braid, stainless-steel sheaths with 275 psig at 70 deg F (1900 kPa at 21 deg C) and 200 psig at 600 deg F (1380 kPa at 315 deg C) ratings.

c. NPS 8 (DN 200) and Larger:  Stainless-steel hoses and double-braid, stainless-steel sheaths with 165 psig at 70 deg F (1130 kPa at 21 deg C) and 120 psig at 600 deg F (830 kPa at 315 deg C) ratings.

Coordinate expansion-joint pressure and temperature ratings with piping systems.

E. Packed Slip Expansion Joints:  ASTM F 1007, carbon-steel, packing type designed for repacking under pressure and pressure rated for 250 psig at 400 deg F (1725 kPa at 204 deg C) minimum.  Include asbestos-free PTFE packing, compound limit stops, and drip connection if used for steam piping.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Adsco Manufacturing, LLC.

b. Advanced Thermal Systems, Inc.

c. Hyspan Precision Products, Inc.

d. <Insert manufacturer's name.>

3. Configuration:  [Single] [Single- and double] [Double]-joint class[ with base, unless otherwise indicated].

4. End Connections:  Flanged or weld ends to match piping system.

F. Flexible Ball Joints:  Carbon-steel assembly with asbestos-free composition packing, designed for 360-degree rotation and angular deflection, and 250 psig at 400 deg F (1725 kPa at 204 deg C) minimum pressure rating; complying with ASME Boiler and Pressure Vessel Code:  Section II, "Materials," and with ASME B31.9, "Building Services Piping," for materials and design of pressure-containing parts and bolting.

1. Angular Deflection for NPS 6 (DN 150) and Smaller:  30-degree minimum.

2. Angular Deflection for NPS 8 (DN 200) and Larger:  15-degree minimum.

NPS 2-1/2 (DN 65) and larger weld end connections are available if required.

3. End Connections for NPS 2 (DN 50) and Smaller:  Threaded.

4. End Connections for NPS 2-1/2 (DN 65) and Larger:  Flanged.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain subparagraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

5. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Advanced Thermal Systems, Inc.

b. Hyspan Precision Products, Inc.

c. <Insert manufacturer's name.>

2.2 ALIGNMENT GUIDES

Indicate alignment-guide length and maximum spider travel on Drawings.

A. Description:  Steel, factory fabricated, with bolted two-section outer cylinder and base for alignment of piping and two-section guiding spider for bolting to pipe.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Adsco Manufacturing, LLC.

b. Advanced Thermal Systems, Inc.

c. Flex-Hose Co., Inc.

d. Flexicraft Industries.

e. Flex-Weld, Inc.

f. Hyspan Precision Products, Inc.

g. Metraflex, Inc.

h. Piping Technology & Products, Inc.

i. Senior Flexonics, Inc.; Pathway Division.

j. <Insert manufacturer's name.>

2.3 MATERIALS FOR ANCHORS

A. Steel Shapes and Plates:  ASTM A 36/A 36M.

B. Bolts and Nuts:  ASME B18.10 or ASTM A 183, steel, hex head.

C. Washers:  ASTM F 844, steel, plain, flat washers.

D. Mechanical Fasteners:  Insert-wedge-type stud with expansion plug anchor for use in hardened portland cement concrete, and tension and shear capacities appropriate for application.

Stainless-steel studs are available.

1. Stud:  Threaded, zinc-coated carbon steel.

2. Expansion Plug:  Zinc-coated steel.

3. Washer and Nut:  Zinc-coated steel.

E. Chemical Fasteners:  Insert-type-stud bonding system anchor for use with hardened portland cement concrete, and tension and shear capacities appropriate for application.

1. Bonding Material:  ASTM C 881, Type IV, Grade 3, 2-component epoxy resin suitable for surface temperature of hardened concrete where fastener is to be installed.

Stainless-steel studs are available.

2. Stud:  ASTM A 307, zinc-coated carbon steel with continuous thread on stud, unless otherwise indicated.

3. Washer and Nut:  Zinc-coated steel.

F. Concrete:  Portland cement mix, 3000 psi (20.7 MPa) minimum.  Comply with requirements in Division 03 Section "Cast-in-Place Concrete" for formwork, reinforcement, and concrete.

G. Grout:  ASTM C 1107, factory-mixed and -packaged, dry, hydraulic-cement, nonshrink, nonmetallic grout; suitable for interior and exterior applications.

1. Properties:  Nonstaining, noncorrosive, and nongaseous.

2. Design Mix:  5000-psi (34.5-MPa), 28-day compressive strength.

PART 3 -  EXECUTION

3.1 EXPANSION-JOINT INSTALLATION

A. Install manufactured, nonmetallic expansion joints according to FSA's "Technical Handbook:  Non-Metallic Expansion Joints and Flexible Pipe Connectors."

B. Install expansion joints of sizes matching size of piping in which they are installed.

C. Install alignment guides to allow expansion and to avoid end-loading and torsional stress.

3.2 PIPE BEND AND LOOP INSTALLATION

See the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment," which states that cold springing is not recommended for most HVAC piping.  If retaining first paragraph below, show dimensions of loops and locations of guides and anchors on Drawings.

A. Install pipe bends and loops cold-sprung in tension or compression as required to partly absorb tension or compression produced during anticipated change in temperature.

Coordinate paragraph below with structural Sections and Drawings if welding is included in structural work.

B. Attach pipe bends and loops to anchors.

1. Steel Anchors:  Attach by welding.  Comply with ASME B31.9 and ASME Boiler and Pressure Vessel Code:  Section IX, "Welding and Brazing Qualifications."

2. Concrete Anchors:  Attach by fasteners.  Follow fastener manufacturer's written instructions.

3.3 SWING CONNECTIONS

A. Connect risers and branch connections to mains with at least [five] <Insert number> pipe fittings, including tee in main.

B. Connect risers and branch connections to terminal units with at least [four] <Insert number> pipe fittings, including tee in riser.

C. Connect mains and branch connections to terminal units with at least [four] <Insert number> pipe fittings, including tee in main.

3.4 ALIGNMENT-GUIDE INSTALLATION

Show locations and quantity of guides on Drawings.

A. Install guides on piping adjoining pipe expansion fittings and loops.

Coordinate paragraph below with structural Sections and Drawings if welding is included in structural work.

B. Attach guides to pipe and secure to building structure.

3.5 ANCHOR INSTALLATION

A. Install anchors at locations to prevent stresses from exceeding those permitted by ASME B31.9 and to prevent transfer of loading and stresses to connected equipment.

Coordinate first paragraph below with structural Sections and Drawings if welding is included in structural work.

B. Fabricate and install steel anchors by welding steel shapes, plates, and bars to piping and to structure.  Comply with ASME B31.9 and AWS D1.1.

C. Construct concrete anchors of poured-in-place concrete of dimensions indicated and include embedded fasteners.

D. Install pipe anchors according to expansion-joint manufacturer's written instructions if expansion joints or compensators are indicated.

E. Use grout to form flat bearing surfaces for expansion fittings, guides, and anchors installed on or in concrete.

END OF SECTION 230516

	EXPANSION FITTINGS AND LOOPS FOR HVAC PIPING
	230516 - 1



