Copyright 2004 and 2005 AIA
MASTERSPEC
12/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 230548 - VIBRATION AND SEISMIC CONTROLS FOR HVAC PIPING AND EQUIPMENT
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Isolation pads.

2. Isolation mounts.

3. Restrained elastomeric isolation mounts.

4. [Freestanding] [Restrained] [Freestanding and restrained] spring isolators.

5. Housed spring mounts.

6. Elastomeric hangers.

7. Spring hangers.

8. Spring hangers with vertical-limit stops.

9. Pipe riser resilient supports.

10. Resilient pipe guides.

11. [Freestanding] [Restrained] [Freestanding and restrained] air-mounting system.

12. Restrained vibration isolation roof-curb rails.

13. Seismic snubbers.

14. Restraining braces and cables.

15. [Steel] [Inertia] [Steel and inertia], vibration isolation equipment bases.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. IBC:  International Building Code.

B. ICC-ES:  ICC-Evaluation Service.

C. OSHPD:  Office of Statewide Health Planning and Development for the State of California.

1.4 PERFORMANCE REQUIREMENTS

Retain first paragraph and subparagraphs below for outdoor equipment.

A. Wind-Restraint Loading:

Obtain values for items in subparagraphs below from Project structural engineer or from SEI/ASCE 7.

1. Basic Wind Speed:  <Insert value>.

2. Building Classification Category:  [I] [II] [III] [IV].

3. Minimum 10 lb/sq. ft. (48.8 kg/sq. m) multiplied by the maximum area of the HVAC component projected on a vertical plane that is normal to the wind direction, and 45 degrees either side of normal.

B. Seismic-Restraint Loading:

Obtain values for items in subparagraphs and associated subparagraphs below from Project structural engineer or from SEI/ASCE 7.  If the code at Project site is other than the IBC or NFPA 5000, revise parameters to comply with applicable code.

Specify design spectral response acceleration at short periods (0.2 second) and at 1 second based on site class in subparagraph below.  Typical values range from 2 to 200 percent.  Design spectral response acceleration is required for seismic force calculations to size seismic restraints.  For each seismic restraint, include component importance factor, component response modification factor, and component amplification factor in the HVAC Vibration-Control and Seismic-Restraint Device Schedule.

1. Site Class as Defined in the IBC:  [A] [B] [C] [D] [E] [F].

In subparagraph below, retain Seismic Use Group or Building Category for Project structure from three classifications defined in the IBC.

2. Assigned Seismic Use Group or Building Category as Defined in the IBC:  [I] [II] [III].

Retain first three subparagraphs below if these values are not included in the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.  Factors below often vary among supported equipment.  However, it is possible to specify maximum values for these factors for various classes of equipment or for all equipment instead of scheduling each piece of equipment.

a. Component Importance Factor:  [1.0] [1.5] <Insert value>.

b. Component Response Modification Factor:  [1.5] [2.5] [3.5] [5.0] <Insert value>.

c. Component Amplification Factor:  [1.0] [2.5] <Insert value>.

3. Design Spectral Response Acceleration at Short Periods (0.2 Second):  <Insert percent>.

4. Design Spectral Response Acceleration at 1-Second Period:  <Insert percent>.

1.5 SUBMITTALS

A. Product Data: For the following:

1. Include rated load, rated deflection, and overload capacity for each vibration isolation device.

2. Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of seismic-restraint component used.

See Evaluations for a discussion on seismic-restraint capacities and rating services.

a. Tabulate types and sizes of seismic restraints, complete with report numbers and rated strength in tension and shear as evaluated by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

b. Annotate to indicate application of each product submitted and compliance with requirements.

3. Interlocking Snubbers:  Include ratings for horizontal, vertical, and combined loads.

Paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

B. Delegated-Design Submittal:  For vibration isolation and seismic-restraint details indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Design Calculations:  Calculate static and dynamic loading due to equipment weight and operation, seismic[ and wind] forces required to select vibration isolators, seismic[ and wind] restraints, and for designing vibration isolation bases.

a. Coordinate design calculations with wind load calculations required for equipment mounted outdoors.  Comply with requirements in other Division 22 Sections for equipment mounted outdoors.

2. Riser Supports:  Include riser diagrams and calculations showing anticipated expansion and contraction at each support point, initial and final loads on building structure, spring deflection changes, and seismic loads.  Include certification that riser system has been examined for excessive stress and that none will exist.

3. Vibration Isolation Base Details:  Detail overall dimensions, including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails, base weights, equipment static loads, power transmission, component misalignment, and cantilever loads.

Retain subparagraph and associated subparagraphs below only if seismic design requirements apply but calculations have not been made and details or charts on Drawings do not describe seismic restraints in detail.  Retaining subparagraph will require Contractor to submit seismic-restraint Delegated-Design Drawings prepared by a professional engineer.  Revise to suit local requirements.

Retain option in subparagraph and first associated subparagraph below if Project includes equipment mounted outdoors.

4. Seismic[- and Wind]-Restraint Details:

a. Design Analysis:  To support selection and arrangement of seismic[ and wind] restraints.  Include calculations of combined tensile and shear loads.

b. Details:  Indicate fabrication and arrangement.  Detail attachments of restraints to the restrained items and to the structure.  Show attachment locations, methods, and spacings.  Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events.  Indicate association with vibration isolation devices.

Retain first subparagraph below if Project includes equipment mounted outdoors.

c. Coordinate seismic-restraint and vibration isolation details with wind-restraint details required for equipment mounted outdoors.  Comply with requirements in other Division 22 Sections for equipment mounted outdoors.

d. Preapproval and Evaluation Documentation:  By [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction], showing maximum ratings of restraint items and the basis for approval (tests or calculations).

Retain paragraph below if seismic bracing of piping, ducts, equipment, and other HVAC system components will be installed in congested areas.

C. Coordination Drawings:  Show coordination of seismic bracing for HVAC piping and equipment with other systems and equipment in the vicinity, including other supports and seismic restraints.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

D. Welding certificates.

Coordinate paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For [professional engineer] [and] [testing agency].

Retain option in paragraph below if authorities having jurisdiction require independent testing.

F. Air-Mounting System Performance Certification:  Include natural frequency, load, and damping test data[ performed by an independent agency].

Retain paragraph below if Contractor is responsible for field quality-control testing.

G. Field quality-control test reports.

Retain paragraph below for air-mounting systems.

H. Operation and Maintenance Data:  For air-mounting systems to include in operation and maintenance manuals.

1.6 QUALITY ASSURANCE

If an independent testing agency is required, see Division 01 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, use first paragraph below to specify 29 CFR 1910.7.  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph below if Contractor selects testing agency.

A. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

B. Comply with seismic-restraint requirements in the IBC unless requirements in this Section are more stringent.

Delete first paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

C. Welding:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

D. Seismic-restraint devices shall have horizontal and vertical load testing and analysis and shall bear anchorage preapproval OPA number from OSHPD, preapproval by ICC-ES, or preapproval by another agency acceptable to authorities having jurisdiction, showing maximum seismic-restraint ratings.  Ratings based on independent testing are preferred to ratings based on calculations.  If preapproved ratings are not available, submittals based on independent testing are preferred.  Calculations (including combining shear and tensile loads) to support seismic-restraint designs must be signed and sealed by a qualified professional engineer.

PART 2 -  PRODUCTS

2.1 VIBRATION ISOLATORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Ace Mountings Co., Inc.

2. Amber/Booth Company, Inc.

3. California Dynamics Corporation.

4. Isolation Technology, Inc.

5. Kinetics Noise Control.

6. Mason Industries.

7. Vibration Eliminator Co., Inc.

8. Vibration Isolation.

9. Vibration Mountings & Controls, Inc.

10. <Insert manufacturer's name>.

Copy paragraph and subparagraph below for each type of pad configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

D. Pads <Insert drawing designation>:  Arranged in single or multiple layers of sufficient stiffness for uniform loading over pad area, molded with a nonslip pattern and galvanized-steel baseplates, and factory cut to sizes that match requirements of supported equipment.

Verify availability of various pad materials with manufacturers.

1. Resilient Material:  Oil- and water-resistant [neoprene] [rubber] [hermetically sealed compressed fiberglass].

Copy paragraph and subparagraphs below for each type of mount configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

E. Mounts <Insert drawing designation>:  Double-deflection type, with molded, oil-resistant rubber, hermetically sealed compressed fiberglass, or neoprene isolator elements with factory-drilled, encapsulated top plate for bolting to equipment and with baseplate for bolting to structure.  Color-code or otherwise identify to indicate capacity range.

1. Materials:  Cast-ductile-iron or welded steel housing containing two separate and opposing, oil-resistant rubber or neoprene elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

2. Neoprene:  Shock-absorbing materials compounded according to the standard for bridge-bearing neoprene as defined by AASHTO.

Copy paragraph and subparagraphs below for each type of restrained mount configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

F. Restrained Mounts <Insert drawing designation>:  All-directional mountings with seismic restraint.

1. Materials:  Cast-ductile-iron or welded steel housing containing two separate and opposing, oil-resistant rubber or neoprene elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

2. Neoprene:  Shock-absorbing materials compounded according to the standard for bridge-bearing neoprene as defined by AASHTO.

Copy paragraph and subparagraphs below for each type of spring isolator configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

G. Spring Isolators <Insert drawing designation>:  Freestanding, laterally stable, open-spring isolators.

1. Outside Spring Diameter:  Not less than 80 percent of the compressed height of the spring at rated load.

2. Minimum Additional Travel:  50 percent of the required deflection at rated load.

3. Lateral Stiffness:  More than 80 percent of rated vertical stiffness.

4. Overload Capacity:  Support 200 percent of rated load, fully compressed, without deformation or failure.

5. Baseplates:  Factory drilled for bolting to structure and bonded to 1/4-inch- (6-mm-) thick, rubber isolator pad attached to baseplate underside.  Baseplates shall limit floor load to 500 psig (3447 kPa).

6. Top Plate and Adjustment Bolt:  Threaded top plate with adjustment bolt and cap screw to fasten and level equipment.

Copy paragraph and subparagraphs below for each type of restrained spring isolator configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

H. Restrained Spring Isolators <Insert drawing designation>:  Freestanding, steel, open-spring isolators with seismic or limit-stop restraint.

1. Housing:  Steel with resilient vertical-limit stops to prevent spring extension due to weight being removed; factory-drilled baseplate bonded to 1/4-inch- (6-mm-) thick, neoprene or rubber isolator pad attached to baseplate underside; and adjustable equipment mounting and leveling bolt that acts as blocking during installation.

2. Restraint:  Seismic or limit stop as required for equipment and authorities having jurisdiction.

3. Outside Spring Diameter:  Not less than 80 percent of the compressed height of the spring at rated load.

4. Minimum Additional Travel:  50 percent of the required deflection at rated load.

5. Lateral Stiffness:  More than 80 percent of rated vertical stiffness.

6. Overload Capacity:  Support 200 percent of rated load, fully compressed, without deformation or failure.

Copy paragraph and subparagraphs below for each type of housed spring mount configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

I. Housed Spring Mounts <Insert drawing designation>:  Housed spring isolator with integral seismic snubbers.

1. Housing:  Ductile-iron or steel housing to provide all-directional seismic restraint.

2. Base:  Factory drilled for bolting to structure.

3. Snubbers:  Vertically adjustable to allow a maximum of 1/4-inch (6-mm) travel up or down before contacting a resilient collar.

Copy paragraph below for each type of elastomeric hanger configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

J. Elastomeric Hangers <Insert drawing designation>:  Single or double-deflection type, fitted with molded, oil-resistant elastomeric isolator elements bonded to steel housings with threaded connections for hanger rods.  Color-code or otherwise identify to indicate capacity range.

Copy paragraph and subparagraphs below for each type of spring hanger configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

K. Spring Hangers <Insert drawing designation>:  Combination coil-spring and elastomeric-insert hanger with spring and insert in compression.

1. Frame:  Steel, fabricated for connection to threaded hanger rods and to allow for a maximum of 30 degrees of angular hanger-rod misalignment without binding or reducing isolation efficiency.

2. Outside Spring Diameter:  Not less than 80 percent of the compressed height of the spring at rated load.

3. Minimum Additional Travel:  50 percent of the required deflection at rated load.

4. Lateral Stiffness:  More than 80 percent of rated vertical stiffness.

5. Overload Capacity:  Support 200 percent of rated load, fully compressed, without deformation or failure.

6. Elastomeric Element:  Molded, oil-resistant rubber or neoprene.  Steel-washer-reinforced cup to support spring and bushing projecting through bottom of frame.

7. Self-centering hanger rod cap to ensure concentricity between hanger rod and support spring coil.

Copy paragraph and subparagraphs below for each type of spring hanger with vertical-limit stop configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

L. Spring Hangers with Vertical-Limit Stop <Insert drawing designation>:  Combination coil-spring and elastomeric-insert hanger with spring and insert in compression and with a vertical-limit stop.

1. Frame:  Steel, fabricated for connection to threaded hanger rods and to allow for a maximum of 30 degrees of angular hanger-rod misalignment without binding or reducing isolation efficiency.

2. Outside Spring Diameter:  Not less than 80 percent of the compressed height of the spring at rated load.

3. Minimum Additional Travel:  50 percent of the required deflection at rated load.

4. Lateral Stiffness:  More than 80 percent of rated vertical stiffness.

5. Overload Capacity:  Support 200 percent of rated load, fully compressed, without deformation or failure.

6. Elastomeric Element:  Molded, oil-resistant rubber or neoprene.

7. Adjustable Vertical Stop:  Steel washer with neoprene washer "up-stop" on lower threaded rod.

8. Self-centering hanger rod cap to ensure concentricity between hanger rod and support spring coil.

Copy first paragraph below for each type of pipe riser resilient support configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

M. Pipe Riser Resilient Support <Insert drawing designation>:  All-directional, acoustical pipe anchor consisting of 2 steel tubes separated by a minimum of 1/2-inch- (13-mm-) thick neoprene.  Include steel and neoprene vertical-limit stops arranged to prevent vertical travel in both directions.  Design support for a maximum load on the isolation material of 500 psig (3.45 MPa) and for equal resistance in all directions.

N. Resilient Pipe Guides:  Telescopic arrangement of 2 steel tubes or post and sleeve arrangement separated by a minimum of 1/2-inch- (13-mm-) thick neoprene.  Where clearances are not readily visible, a factory-set guide height with a shear pin to allow vertical motion due to pipe expansion and contraction shall be fitted.  Shear pin shall be removable and reinsertable to allow for selection of pipe movement.  Guides shall be capable of motion to meet location requirements.

2.2 AIR-MOUNTING SYSTEMS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. California Dynamics Corporation.

2. Firestone Industrial Products Company.

3. Kinetics Noise Control.

4. Mason Industries.

5. Vibration Eliminator Co., Inc.

6. <Insert manufacturer's name>.

Copy paragraph and subparagraphs below for each type of air mount configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

D. Air Mounts <Insert drawing designation>:  Freestanding, single or multiple, compressed-air bellows.

1. Assembly:  Upper and lower steel sections connected by a replaceable, flexible, nylon-reinforced neoprene bellows.

2. Maximum Natural Frequency:  3 Hz.

3. Operating Pressure Range:  25 to 100 psig (172 to 690 kPa).

4. Burst Pressure:  At least three times manufacturer's published maximum operating pressure.

5. Leveling Valves:  Minimum of 3 required to maintain leveling within plus or minus 1/8 inch (3 mm).

Copy paragraph and subparagraphs below for each type of restrained air mount configuration required for Project.  Use drawing designation and coordinate with the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

E. Restrained Air Mounts <Insert drawing designation>:  Housed compressed-air bellows.

1. Assembly:  Upper and lower steel sections connected by a replaceable, flexible, nylon-reinforced neoprene bellows and spring, with angle-iron frame having vertical-limit stops and channel-section top with leveling adjustment and attachment screws.

2. Maximum Natural Frequency:  3 Hz.

3. Operating Pressure Range:  25 to 100 psig (172 to 690 kPa).

4. Burst Pressure:  At least three times manufacturer's published maximum operating pressure.

5. Leveling Valves:  Minimum of 3 required to maintain leveling within plus or minus 1/8 inch (3 mm).

2.3 RESTRAINED VIBRATION ISOLATION ROOF-CURB RAILS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Amber/Booth Company, Inc.

2. California Dynamics Corporation.

3. Isolation Technology, Inc.

4. Kinetics Noise Control.

5. Mason Industries.

6. Thybar Corporation.

7. Vibration Eliminator Co., Inc.

8. Vibration Isolation.

9. Vibration Mountings & Controls, Inc.

10. <Insert manufacturer's name>.

Retain option in first two paragraphs below if required by authorities having jurisdiction.

D. General Requirements for Restrained Vibration Isolation Roof-Curb Rails:  Factory-assembled, fully enclosed, insulated, air- and watertight curb rail designed to resiliently support equipment and to withstand seismic[ and wind] forces.

E. Lower Support Assembly:  Formed sheet-metal section containing adjustable and removable steel springs that support upper frame.  Upper frame shall provide continuous support for equipment and shall be captive to resiliently resist seismic[ and wind] forces.  Lower support assembly shall have a means for attaching to building structure and a wood nailer for attaching roof materials, and shall be insulated with a minimum of 2 inches (50 mm) of rigid, glass-fiber insulation on inside of assembly.

F. Spring Isolators:  Adjustable, restrained spring isolators shall be mounted on 1/4-inch- (6-mm-) thick, elastomeric vibration isolation pads and shall have access ports, for level adjustment, with removable waterproof covers at all isolator locations.  Isolators shall be located so they are accessible for adjustment at any time during the life of the installation without interfering with the integrity of the roof.

1. Restrained Spring Isolators:  Freestanding, steel, open-spring isolators with seismic[ or wind] restraint.

a. Housing:  Steel with resilient vertical-limit stops and adjustable equipment mounting and leveling bolt.

b. Outside Spring Diameter:  Not less than 80 percent of the compressed height of the spring at rated load.

c. Minimum Additional Travel:  50 percent of the required deflection at rated load.

d. Lateral Stiffness:  More than 80 percent of rated vertical stiffness.

e. Overload Capacity:  Support 200 percent of rated load, fully compressed, without deformation or failure.

2. Pads:  Arranged in single or multiple layers of sufficient stiffness for uniform loading over pad area, molded with a nonslip pattern and galvanized-steel baseplates, and factory cut to sizes that match requirements of supported equipment.

a. Resilient Material:  Oil- and water-resistant [standard neoprene] [natural rubber] [hermetically sealed compressed fiberglass].

G. Snubber Bushings:  All-directional, elastomeric snubber bushings at least 1/4 inch (6 mm) thick.

H. Water Seal:  Galvanized sheet metal with EPDM seals at corners, attached to upper support frame, extending down past wood nailer of lower support assembly, and counterflashed over roof materials.

2.4 VIBRATION ISOLATION EQUIPMENT BASES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Amber/Booth Company, Inc.

2. California Dynamics Corporation.

3. Isolation Technology, Inc.

4. Kinetics Noise Control.

5. Mason Industries.

6. Vibration Eliminator Co., Inc.

7. Vibration Isolation.

8. Vibration Mountings & Controls, Inc.

9. <Insert manufacturer's name>.

D. Steel Base <Insert drawing designation>:  Factory-fabricated, welded, structural-steel bases and rails.

1. Design Requirements:  Lowest possible mounting height with not less than 1-inch (25-mm) clearance above the floor.  Include equipment anchor bolts and auxiliary motor slide bases or rails.

Retain first subparagraph below if steel bases are required for pumps.

a. Include supports for suction and discharge elbows for pumps.

2. Structural Steel:  Steel shapes, plates, and bars complying with ASTM A 36/A 36M.  Bases shall have shape to accommodate supported equipment.

3. Support Brackets:  Factory-welded steel brackets on frame for outrigger isolation mountings and to provide for anchor bolts and equipment support.

E. Inertia Base <Insert drawing designation>:  Factory-fabricated, welded, structural-steel bases and rails ready for placement of cast-in-place concrete.

1. Design Requirements:  Lowest possible mounting height with not less than 1-inch (25-mm) clearance above the floor.  Include equipment anchor bolts and auxiliary motor slide bases or rails.

Retain first subparagraph below if inertia bases are required for pumps.

a. Include supports for suction and discharge elbows for pumps.

2. Structural Steel:  Steel shapes, plates, and bars complying with ASTM A 36/A 36M.  Bases shall have shape to accommodate supported equipment.

3. Support Brackets:  Factory-welded steel brackets on frame for outrigger isolation mountings and to provide for anchor bolts and equipment support.

4. Fabrication:  Fabricate steel templates to hold equipment anchor-bolt sleeves and anchors in place during placement of concrete.  Obtain anchor-bolt templates from supported equipment manufacturer.

2.5 SEISMIC-RESTRAINT DEVICES

Coordinate specifications for seismic-restraint components in this Article with structural engineer and with Drawings.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Amber/Booth Company, Inc.

2. California Dynamics Corporation.

3. Cooper B-Line, Inc.; a division of Cooper Industries.

4. Hilti, Inc.

5. Kinetics Noise Control.

6. Loos & Co.; Cableware Division.

7. Mason Industries.

8. TOLCO Incorporated; a brand of NIBCO INC.

9. Unistrut; Tyco International, Ltd.

10. <Insert manufacturer's name>.

See Evaluations for a discussion on seismic-restraint capacities and rating services.

D. General Requirements for Restraint Components:  Rated strengths, features, and applications shall be as defined in reports by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

1. Structural Safety Factor:  Allowable strength in tension, shear, and pullout force of components shall be at least [four] <Insert number> times the maximum seismic forces to which they will be subjected.

E. Snubbers:  Factory fabricated using welded structural-steel shapes and plates, anchor bolts, and replaceable resilient isolation washers and bushings.

1. Anchor bolts for attaching to concrete shall be seismic-rated, drill-in, and stud-wedge or female-wedge type.

2. Resilient Isolation Washers and Bushings:  Oil- and water-resistant neoprene.

3. Maximum 1/4-inch (6-mm) air gap, and minimum 1/4-inch- (6-mm-) thick resilient cushion.

F. Channel Support System:  MFMA-3, shop- or field-fabricated support assembly made of slotted steel channels with accessories for attachment to braced component at one end and to building structure at the other end and other matching components and with corrosion-resistant coating; and rated in tension, compression, and torsion forces.

G. Restraint Cables:  [ASTM A 603 galvanized] [ASTM A 492 stainless]-steel cables with end connections made of steel assemblies with thimbles, brackets, swivel, and bolts designed for restraining cable service; and with a minimum of two clamping bolts for cable engagement.

Retain first paragraph below for strengthening resistance of hanger rods against seismic forces that may cause buckling of rods; delete if detailed on Drawings.  Use with either channel- or cable-type bracing assemblies when required to counter seismic forces.  Detail fabrication and indicate locations on Drawings.

H. Hanger Rod Stiffener:  [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod.

I. Bushings for Floor-Mounted Equipment Anchor Bolts:  Neoprene bushings designed for rigid equipment mountings, and matched to type and size of anchor bolts and studs.

J. Bushing Assemblies for Wall-Mounted Equipment Anchorage:  Assemblies of neoprene elements and steel sleeves designed for rigid equipment mountings, and matched to type and size of attachment devices used.

K. Resilient Isolation Washers and Bushings:  One-piece, molded, oil- and water-resistant neoprene, with a flat washer face.

Expansion-type anchor bolts are not permitted by SEI/ASCE 7 for nonisolated equipment in excess of 10 hp (7.46 kW).

L. Mechanical Anchor Bolts:  Drilled-in and stud-wedge or female-wedge type in zinc-coated steel for interior applications and stainless steel for exterior applications.  Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.  Minimum length of eight times diameter.

M. Adhesive Anchor Bolts:  Drilled-in and capsule anchor system containing polyvinyl or urethane methacrylate-based resin and accelerator, or injected polymer or hybrid mortar adhesive.  Provide anchor bolts and hardware with zinc-coated steel for interior applications and stainless steel for exterior applications.  Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.

2.6 FACTORY FINISHES

Specify field-painting requirements in Division 09 painting Sections.  Verify compatibility of factory finishes with field-applied coats.

A. Finish:  Manufacturer's standard prime-coat finish ready for field painting.

Edit paragraph and subparagraphs below to include custom colors.  Coordinate custom-color requirements with sample submittal requirements.

B. Finish:  Manufacturer's standard paint applied to factory-assembled and -tested equipment before shipping.

1. Powder coating on springs and housings.

2. All hardware shall be galvanized.  Hot-dip galvanize metal components for exterior use.

3. Baked enamel or powder coat for metal components on isolators for interior use.

4. Color-code or otherwise mark vibration isolation and seismic[- and wind]-control devices to indicate capacity range.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and equipment to receive vibration isolation and seismic[- and wind]-control devices for compliance with requirements for installation tolerances and other conditions affecting performance.

B. Examine roughing-in of reinforcement and cast-in-place anchors to verify actual locations before installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATIONS

A. Multiple Pipe Supports:  Secure pipes to trapeze member with clamps approved for application by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

Indicate on Drawings, by details, schedules, or a combination of both, the locations where hanger rods for individual pipes and hanger rods for trapeze hangers require hanger rod stiffeners.

B. Hanger Rod Stiffeners:  Install hanger rod stiffeners where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods due to seismic forces.

C. Strength of Support and Seismic-Restraint Assemblies:  Where not indicated, select sizes of components so strength will be adequate to carry present and future static and seismic loads within specified loading limits.

3.3 VIBRATION-CONTROL AND SEISMIC-RESTRAINT DEVICE INSTALLATION

A. Comply with requirements in Division 07 Section "Roof Accessories" for installation of roof curbs, equipment supports, and roof penetrations.

B. Equipment Restraints:

Indicate type and quantity of snubbers described in first subparagraph below on Drawings or in the HVAC Vibration-Control and Seismic-Restraint Device Schedule on Drawings.

1. Install seismic snubbers on HVAC equipment mounted on vibration isolators.  Locate snubbers as close as possible to vibration isolators and bolt to equipment base and supporting structure.

2. Install resilient bolt isolation washers on equipment anchor bolts where clearance between anchor and adjacent surface exceeds 0.125 inch (3.2 mm).

3. Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] providing required submittals for component.

C. Piping Restraints:

1. Comply with requirements in MSS SP-127.

In first subparagraph below, options for 40 and 80 feet (12 and 24 m) are recommended by MSS SP-127.  Consider reducing these dimensions based on the configuration of piping.

2. Space lateral supports a maximum of [40 feet (12 m)] <Insert dimension> o.c., and longitudinal supports a maximum of [80 feet (24 m)] <Insert dimension> o.c.

3. Brace a change of direction longer than 12 feet (3.7 m).

D. Install cables so they do not bend across edges of adjacent equipment or building structure.

E. Install seismic-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] providing required submittals for component.

F. Install bushing assemblies for anchor bolts for floor-mounted equipment, arranged to provide resilient media between anchor bolt and mounting hole in concrete base.

G. Install bushing assemblies for mounting bolts for wall-mounted equipment, arranged to provide resilient media where equipment or equipment-mounting channels are attached to wall.

H. Attachment to Structure:  If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at upper truss chords of bar joists, or at concrete members.

I. Drilled-in Anchors:

1. Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors.  Do not damage existing reinforcing or embedded items during coring or drilling.  Notify the structural engineer if reinforcing steel or other embedded items are encountered during drilling.  Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

2. Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

3. Wedge Anchors:  Protect threads from damage during anchor installation.  Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

4. Adhesive Anchors:  Clean holes to remove loose material and drilling dust prior to installation of adhesive.  Place adhesive in holes proceeding from the bottom of the hole and progressing toward the surface in such a manner as to avoid introduction of air pockets in the adhesive.

5. Set anchors to manufacturer's recommended torque, using a torque wrench.

6. Install zinc-coated steel anchors for interior and stainless-steel anchors for exterior applications.

3.4 ACCOMMODATION OF DIFFERENTIAL SEISMIC MOTION

Coordinate this Article with Drawings.

A. Install flexible connections in piping where they cross seismic joints, where adjacent sections or branches are supported by different structural elements, and where the connections terminate with connection to equipment that is anchored to a different structural element from the one supporting the connections as they approach equipment.  Comply with requirements in Division 22 Section "Hydronic Piping" for piping flexible connections.

3.5 FIELD QUALITY CONTROL

Retain one of first two paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control test reports" Paragraph in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. Provide evidence of recent calibration of test equipment by a testing agency acceptable to authorities having jurisdiction.

2. Schedule test with Owner, through Architect, before connecting anchorage device to restrained component (unless postconnection testing has been approved), and with at least seven days' advance notice.

3. Obtain Architect's approval before transmitting test loads to structure.  Provide temporary load-spreading members.

4. Test at least [four] <Insert number> of each type and size of installed anchors and fasteners selected by Architect.

5. Test to 90 percent of rated proof load of device.

6. Measure isolator restraint clearance.

7. Measure isolator deflection.

8. Verify snubber minimum clearances.

Retain first three subparagraphs below if air-mounting systems are included in Project.

9. Air-Mounting System Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

10. Air-Mounting System Operational Test:  Test the compressed-air leveling system.

11. Test and adjust air-mounting system controls and safeties.

12. If a device fails test, modify all installations of same type and retest until satisfactory results are achieved.

D. Remove and replace malfunctioning units and retest as specified above.

E. Prepare test and inspection reports.

3.6 ADJUSTING

A. Adjust isolators after piping system is at operating weight.

B. Adjust limit stops on restrained spring isolators to mount equipment at normal operating height.  After equipment installation is complete, adjust limit stops so they are out of contact during normal operation.

Retain first paragraph below for air-mounting systems.

C. Adjust air-spring leveling mechanism.

D. Adjust active height of spring isolators.

E. Adjust restraints to permit free movement of equipment within normal mode of operation.

3.7 DEMONSTRATION

Retain this Article for air-mounting systems.

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain air-mounting systems.  Refer to Division 01 Section "Demonstration And Training."

3.8 HVAC VIBRATION-CONTROL AND SEISMIC-RESTRAINT DEVICE SCHEDULE

Revise schedule below to suit Project.  Do not duplicate requirements in Part 2.  Refer to a completed example in the Evaluations for an explanation on how to use schedules.  If a schedule is not included on Drawings, retain below to indicate location and type of required vibration isolators and seismic restraints.

Copy and re-edit paragraph and subparagraphs below for each piece of supported or suspended equipment required.

A. Supported or Suspended Equipment:  <Insert name and drawing designation>.

1. Equipment Location:  <Insert room number>.

2. Pads:

a. Material:  [Neoprene] [Rubber] [Hermetically sealed compressed fiberglass].

b. Thickness:  <Insert inches (mm)>.

c. Number of Pads:  <Insert number> thick.

3. Isolator Type:  <Insert generic name or designation used in Part 2>.

4. Base Type:  <Insert generic name or designation used in Part 2>.

5. Minimum Deflection:  <Insert inches (mm)>.

6. Component Importance Factor:  [1.0] [1.5].

7. Component Response Modification Factor:  [1.5] [2.5] [3.5] [5.0].

8. Component Amplification Factor:  [1.0] [2.5].

END OF SECTION 230548

	VIBRATION AND SEISMIC CONTROLS FOR HVAC PIPING AND EQUIPMENT
	230548 - 1



