Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
06/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 232300 - REFRIGERANT PIPING
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes refrigerant piping used for air-conditioning applications.

1.3 PERFORMANCE REQUIREMENTS

If more than one type of refrigerant is required for Project, retain applicable paragraphs and subparagraphs below and indicate on Drawings which piping circuit requires which refrigerant.

A. Line Test Pressure for Refrigerant R-22:

1. Suction Lines for Air-Conditioning Applications:  185 psig (1276 kPa).

2. Suction Lines for Heat-Pump Applications:  325 psig (2241 kPa).

3. Hot-Gas and Liquid Lines:  325 psig (2241 kPa).

B. Line Test Pressure for Refrigerant R-134a:

1. Suction Lines for Air-Conditioning Applications:  115 psig (793 kPa).

2. Suction Lines for Heat-Pump Applications:  225 psig (1551 kPa).

3. Hot-Gas and Liquid Lines:  225 psig (1551 kPa).

C. Line Test Pressure for Refrigerant R-407C:

1. Suction Lines for Air-Conditioning Applications:  230 psig (1586 kPa).

2. Suction Lines for Heat-Pump Applications:  380 psig (2620 kPa).

3. Hot-Gas and Liquid Lines:  380 psig (2620 kPa).

D. Line Test Pressure for Refrigerant R-410A:

1. Suction Lines for Air-Conditioning Applications:  300 psig (2068 kPa).

2. Suction Lines for Heat-Pump Applications:  535 psig (3689 kPa).

3. Hot-Gas and Liquid Lines:  535 psig (3689 kPa).

1.4 SUBMITTALS

A. Product Data:  For each type of valve and refrigerant piping specialty indicated.  Include pressure drop, based on manufacturer's test data, for the following:

1. Thermostatic expansion valves.

2. Solenoid valves.

3. Hot-gas bypass valves.

4. Filter dryers.

5. Strainers.

6. Pressure-regulating valves.

B. Shop Drawings:  Show layout of refrigerant piping and specialties, including pipe, tube, and fitting sizes, flow capacities, valve arrangements and locations, slopes of horizontal runs, oil traps, double risers, wall and floor penetrations, and equipment connection details.  Show interface and spatial relationships between piping and equipment.

1. Shop Drawing Scale:  [1/4 inch equals 1 foot (1:50)] <Insert value>.

Retain subparagraph below to have Contractor size and design refrigeration piping.

2. Refrigerant piping indicated on Drawings is schematic only.  Size piping and design actual piping layout, including oil traps, double risers, specialties, and pipe and tube sizes to accommodate, as a minimum, equipment provided, elevation difference between compressor and evaporator, and length of piping to ensure proper operation and compliance with warranties of connected equipment.

Retain first paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

C. Welding certificates.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For refrigerant valves and piping specialties to include in maintenance manuals.

1.5 QUALITY ASSURANCE

Retain first paragraph below for welding refrigerant piping and vessels.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.

A. Welding:  Qualify procedures and personnel according to ASME Boiler and Pressure Vessel Code:  Section IX, "Welding and Brazing Qualifications."

B. Comply with ASHRAE 15, "Safety Code for Refrigeration Systems."

C. Comply with ASME B31.5, "Refrigeration Piping and Heat Transfer Components."

1.6 PRODUCT STORAGE AND HANDLING

A. Store piping in a clean and protected area with end caps in place to ensure that piping interior and exterior are clean when installed.

1.7 COORDINATION

A. Coordinate size and location of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

PART 2 -  PRODUCTS

Coordinate first two articles below with piping applications articles in Part 3.  See "Writing Guide" Article in the Evaluations.  Materials included in this Section are examples listed in the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment," Chapter 41, "Pipe, Tubes, and Fittings."

2.1 COPPER TUBE AND FITTINGS

A. Copper Tube:  [ASTM B 88, Type K or L (ASTM B 88M, Type A or B)] [ASTM B 280, Type ACR].

B. Wrought-Copper Fittings:  ASME B16.22.

C. Wrought-Copper Unions:  ASME B16.22.

See Evaluations for discussions of solder and brazing materials.

D. Solder Filler Metals:  ASTM B 32.  Use 95-5 tin antimony or alloy HB solder to join copper socket fittings on copper pipe.

E. Brazing Filler Metals:  AWS A5.8.

F. Flexible Connectors:

1. Body:  Tin-bronze bellows with woven, flexible, tinned-bronze-wire-reinforced protective jacket.

2. End Connections:  Socket ends.

3. Offset Performance:  Capable of minimum 3/4-inch (20-mm) misalignment in minimum 7-inch- (180-mm-) long assembly.

4. Pressure Rating:  Factory test at minimum 500 psig (3450 kPa).

5. Maximum Operating Temperature:  250 deg F (121 deg C).

2.2 STEEL PIPE AND FITTINGS

A. Steel Pipe:  ASTM A 53/A 53M, black steel with plain ends; Type, Grade, and wall thickness as selected in Part 3 piping applications articles.

B. Wrought-Steel Fittings:  ASTM A 234/A 234M, for welded joints.

C. Steel Flanges and Flanged Fittings:  ASME B16.5, steel, including bolts, nuts, and gaskets, bevel-welded end connection, and raised face.

D. Welding Filler Metals:  Comply with AWS D10.12/D10.12M for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

E. Flanged Unions:

1. Body:  Forged-steel flanges for NPS 1 to NPS 1-1/2 (DN 25 to DN 40) and ductile iron for NPS 2 to NPS 3 (DN 50 to DN 80).  Apply rust-resistant finish at factory.

2. Gasket:  Fiber asbestos free.

3. Fasteners:  Four plated-steel bolts, with silicon bronze nuts.  Apply rust-resistant finish at factory.

4. End Connections:  Brass tailpiece adapters for solder-end connections to copper tubing.

5. Offset Performance:  Capable of minimum 3/4-inch (20-mm) misalignment in minimum 7-inch- (180-mm-) long assembly.

6. Pressure Rating:  Factory test at minimum 400 psig (2760 kPa).

7. Maximum Operating Temperature:  330 deg F (165 deg C).

F. Flexible Connectors:

1. Body:  Stainless-steel bellows with woven, flexible, stainless-steel-wire-reinforced protective jacket

2. End Connections:

a. NPS 2 (DN 50) and Smaller:  With threaded-end connections.

b. NPS 2-1/2 (DN 65) and Larger:  With flanged-end connections.

3. Offset Performance:  Capable of minimum 3/4-inch (20-mm) misalignment in minimum 7-inch- (180-mm-) long assembly.

4. Pressure Rating:  Factory test at minimum 500 psig (3450 kPa).

5. Maximum Operating Temperature:  250 deg F (121 deg C).

2.3 VALVES AND SPECIALTIES

A. Diaphragm Packless Valves:

1. Body and Bonnet:  Forged brass or cast bronze; globe design with straight-through or angle pattern.

2. Diaphragm:  Phosphor bronze and stainless steel with stainless-steel spring.

3. Operator:  Rising stem and hand wheel.

4. Seat:  Nylon.

5. End Connections:  Socket, union, or flanged.

6. Working Pressure Rating:  500 psig (3450 kPa).

7. Maximum Operating Temperature:  275 deg F (135 deg C).

B. Packed-Angle Valves:

1. Body and Bonnet:  Forged brass or cast bronze.

2. Packing:  Molded stem, back seating, and replaceable under pressure.

3. Operator:  Rising stem.

4. Seat:  Nonrotating, self-aligning polytetrafluoroethylene.

5. Seal Cap:  Forged-brass or valox hex cap.

6. End Connections:  Socket, union, threaded, or flanged.

7. Working Pressure Rating:  500 psig (3450 kPa).

8. Maximum Operating Temperature:  275 deg F (135 deg C).

C. Check Valves:

1. Body:  Ductile iron, forged brass, or cast bronze; globe pattern.

2. Bonnet:  Bolted ductile iron, forged brass, or cast bronze; or brass hex plug.

3. Piston:  Removable polytetrafluoroethylene seat.

4. Closing Spring:  Stainless steel.

Retain first subparagraph below for optional manual opening feature.

5. Manual Opening Stem:  Seal cap, plated-steel stem, and graphite seal.

6. End Connections:  Socket, union, threaded, or flanged.

7. Maximum Opening Pressure:  0.50 psig (3.4 kPa).

8. Working Pressure Rating:  500 psig (3450 kPa).

9. Maximum Operating Temperature:  275 deg F (135 deg C).

D. Service Valves:

1. Body:  Forged brass with brass cap including key end to remove core.

2. Core:  Removable ball-type check valve with stainless-steel spring.

3. Seat:  Polytetrafluoroethylene.

4. End Connections:  Copper spring.

5. Working Pressure Rating:  500 psig (3450 kPa).

Solenoid valves in first paragraph and subparagraphs below are made normally closed and normally open.  Normally closed are direct acting and pilot operated.  Holding coils are available in several voltages.

E. Solenoid Valves:  Comply with ARI 760 and UL 429; listed and labeled by an NRTL.

1. Body and Bonnet:  Plated steel.

2. Solenoid Tube, Plunger, Closing Spring, and Seat Orifice:  Stainless steel.

3. Seat:  Polytetrafluoroethylene.

4. End Connections:  Threaded.

5. Electrical:  Molded, watertight coil in NEMA 250 enclosure of type required by location with 1/2-inch (16-GRC) conduit adapter, and [24] [115] [208]-V ac coil.

6. Working Pressure Rating:  400 psig (2760 kPa).

7. Maximum Operating Temperature:  240 deg F (116 deg C).

Subparagraph below is an optional feature.

8. Manual operator.

F. Safety Relief Valves:  Comply with ASME Boiler and Pressure Vessel Code; listed and labeled by an NRTL.

1. Body and Bonnet:  Ductile iron and steel, with neoprene O-ring seal.

2. Piston, Closing Spring, and Seat Insert:  Stainless steel.

3. Seat Disc:  Polytetrafluoroethylene.

4. End Connections:  Threaded.

5. Working Pressure Rating:  400 psig (2760 kPa).

6. Maximum Operating Temperature:  240 deg F (116 deg C).

G. Thermostatic Expansion Valves:  Comply with ARI 750.

1. Body, Bonnet, and Seal Cap:  Forged brass or steel.

2. Diaphragm, Piston, Closing Spring, and Seat Insert:  Stainless steel.

3. Packing and Gaskets:  Non-asbestos.

4. Capillary and Bulb:  Copper tubing filled with refrigerant charge.

5. Suction Temperature:  [40 deg F (4.4 deg C)] <Insert temperature>.

6. Superheat:  [Adjustable] [Nonadjustable].

7. Reverse-flow option (for heat-pump applications).

8. End Connections:  Socket, flare, or threaded union.

9. Working Pressure Rating:  [700 psig (4820 kPa)] [450 psig (3100 kPa)] <Insert value>.

H. Hot-Gas Bypass Valves:  Comply with UL 429; listed and labeled by an NRTL.

1. Body, Bonnet, and Seal Cap:  Ductile iron or steel.

2. Diaphragm, Piston, Closing Spring, and Seat Insert:  Stainless steel.

3. Packing and Gaskets:  Non-asbestos.

4. Solenoid Tube, Plunger, Closing Spring, and Seat Orifice:  Stainless steel.

5. Seat:  Polytetrafluoroethylene.

6. Equalizer:  [Internal] [External].

7. Electrical:  Molded, watertight coil in NEMA 250 enclosure of type required by location with 1/2-inch (16-GRC) conduit adapter, and [24] [115] [208]-V ac coil.

8. End Connections:  Socket.

9. Set Pressure:  <Insert psig (kPa).>

10. Throttling Range:  Maximum 5 psig (34 kPa).

11. Working Pressure Rating:  500 psig (3450 kPa).

12. Maximum Operating Temperature:  240 deg F (116 deg C).

I. Straight-Type Strainers:

1. Body:  Welded steel with corrosion-resistant coating.

2. Screen:  100-mesh stainless steel.

3. End Connections:  Socket or flare.

4. Working Pressure Rating:  500 psig (3450 kPa).

5. Maximum Operating Temperature:  275 deg F (135 deg C).

J. Angle-Type Strainers:

1. Body:  Forged brass or cast bronze.

2. Drain Plug:  Brass hex plug.

3. Screen:  100-mesh monel.

4. End Connections:  Socket or flare.

5. Working Pressure Rating:  500 psig (3450 kPa).

6. Maximum Operating Temperature:  275 deg F (135 deg C).

K. Moisture/Liquid Indicators:

1. Body:  Forged brass.

2. Window:  Replaceable, clear, fused glass window with indicating element protected by filter screen.

3. Indicator:  Color coded to show moisture content in ppm.

4. Minimum Moisture Indicator Sensitivity:  Indicate moisture above 60 ppm.

5. End Connections:  Socket or flare.

6. Working Pressure Rating:  500 psig (3450 kPa).

7. Maximum Operating Temperature:  240 deg F (116 deg C).

L. Replaceable-Core Filter Dryers:  Comply with ARI 730.

1. Body and Cover:  Painted-steel shell with ductile-iron cover, stainless-steel screws, and neoprene gaskets.

2. Filter Media:  10 micron, pleated with integral end rings; stainless-steel support.

3. Desiccant Media:  Activated [alumina] [charcoal].

Retain first subparagraph below for heat pumps.

4. Designed for reverse flow (for heat-pump applications).

5. End Connections:  Socket.

Retain first subparagraph below for suction-line filter dryers.

6. Access Ports:  NPS 1/4 (DN 8) connections at entering and leaving sides for pressure differential measurement.

7. Maximum Pressure Loss:  [2 psig (14 kPa)] <Insert value>.

8. Rated Flow:  <Insert tons (kW).>

9. Working Pressure Rating:  500 psig (3450 kPa).

10. Maximum Operating Temperature:  240 deg F (116 deg C).

M. Permanent Filter Dryers:  Comply with ARI 730.

1. Body and Cover:  Painted-steel shell.

2. Filter Media:  10 micron, pleated with integral end rings; stainless-steel support.

3. Desiccant Media:  Activated [alumina] [charcoal].

Retain first subparagraph below for heat pumps.

4. Designed for reverse flow (for heat-pump applications).

5. End Connections:  Socket.

Retain first subparagraph below for suction-line filter dryers.

6. Access Ports:  NPS 1/4 (DN 8) connections at entering and leaving sides for pressure differential measurement.

7. Maximum Pressure Loss:  [2 psig (14 kPa)] <Insert value>.

8. Rated Flow:  <Insert tons (kW).>

9. Working Pressure Rating:  500 psig (3450 kPa).

10. Maximum Operating Temperature:  240 deg F (116 deg C).

N. Mufflers:

1. Body:  Welded steel with corrosion-resistant coating.

2. End Connections:  Socket or flare.

3. Working Pressure Rating:  500 psig (3450 kPa).

4. Maximum Operating Temperature:  275 deg F (135 deg C).

O. Receivers:  Comply with ARI 495.

Retain first subparagraph below for receivers larger than 6 inches (150 mm).

1. Comply with ASME Boiler and Pressure Vessel Code; listed and labeled by an NRTL.

2. Comply with UL 207; listed and labeled by an NRTL.

3. Body:  Welded steel with corrosion-resistant coating.

4. Tappings:  Inlet, outlet, liquid level indicator, and safety relief valve.

5. End Connections:  Socket or threaded.

6. Working Pressure Rating:  500 psig (3450 kPa).

7. Maximum Operating Temperature:  275 deg F (135 deg C).

P. Liquid Accumulators:  Comply with ARI 495.

1. Body:  Welded steel with corrosion-resistant coating.

2. End Connections:  Socket or threaded.

3. Working Pressure Rating:  500 psig (3450 kPa).

4. Maximum Operating Temperature:  275 deg F (135 deg C).

2.4 REFRIGERANTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Atofina Chemicals, Inc.

2. DuPont Company; Fluorochemicals Div.

3. Honeywell, Inc.; Genetron Refrigerants.

4. INEOS Fluor Americas LLC.

5. <Insert manufacturer's name.>

C. ASHRAE 34, R-22:  Monochlorodifluoromethane.

D. ASHRAE 34, R-134a:  Tetrafluoroethane.

E. ASHRAE 34, R-407C:  Difluoromethane/Pentafluoroethane/1,1,1,2-Tetrafluoroethane.

F. ASHRAE 34, R-410A:  Pentafluoroethane/Difluoromethane.

PART 3 -  EXECUTION

If more than one refrigerant is required for Project, retain appropriate refrigerant piping articles below and indicate refrigerant type for each piping line on Drawings.

3.1 PIPING APPLICATIONS FOR REFRIGERANT R-22

Retain one or both paragraphs below.  Retain first paragraph to require all piping to be Type ACR, annealed temper.  Type ACR, annealed-temper tubing is available only in sizes NPS 1-1/2 (DN 40) and smaller.  Retain second paragraph if pipe sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all piping be of same tube type and joining method.  Retain both paragraphs to require piping larger than NPS 1-1/2 (DN 40) to be different than Type ACR, annealed temper.  Delete both paragraphs if suction lines are part of a heat-pump installation.

A. Suction Lines [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

B. Suction Lines [NPS 4 (DN 100) and Smaller] [NPS 2 to NPS 4 (DN 50 to DN 100)] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain one of three paragraphs below.  Retain first paragraph to require all piping to be Type ACR, annealed temper.  Type ACR, annealed-temper tubing is available only in sizes NPS 1-1/2 (DN 40) and smaller.  Retain second paragraph if pipe sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all piping be of same tube type and joining method.  Retain third paragraph and subparagraphs to require different tube type and joining methods for various pipe sizes.

C. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

D. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

E. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:

Retain one of first two subparagraphs below.

1. [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range>:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

2. [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

3. [NPS 2 to NPS 3 (DN 50 to DN 80)] <Insert pipe size range>:  Copper, Type K (A), annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

4. [NPS 4 (DN 100)] <Insert pipe size>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

Retain one of three paragraphs below.  Retain first paragraph to require all safety-relief-valve discharge piping to be steel.  Retain second paragraph to require all pipe sizes to be copper of same tube type and joining method.  Retain third paragraph and subparagraphs to require different tube type and joining methods for various pipe sizes.

F. Safety-Relief-Valve Discharge Piping:  Schedule 40, black-steel and wrought-steel fittings with welded joints.

G. Safety-Relief-Valve Discharge Piping:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

H. Safety-Relief-Valve Discharge Piping:

Retain one of first two subparagraphs below.

1. [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range>:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

2. [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with brazed joints.

3. [NPS 2 to NPS 3 (DN 50 to DN 80)] <Insert pipe size range>:  Copper, Type K (A), annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

4. [NPS 4 (DN 100)] <Insert pipe size>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

3.2 PIPING APPLICATIONS FOR REFRIGERANT R-134a

Retain one or both paragraphs below.  Retain first paragraph to require all piping to be Type ACR, annealed temper.  Type ACR, annealed-temper tubing is available only in sizes NPS 1-1/2 (DN 40) and smaller.  Retain second paragraph if pipe sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all piping be of same tube type and joining method.  Retain both paragraphs to require piping larger than NPS 1-1/2 (DN 40) to be different than Type ACR, annealed temper.  Delete both paragraphs if suction lines are part of a heat-pump installation.

A. Suction Lines [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

B. Suction Lines [NPS 4 (DN 100) and Smaller] [NPS 2 to NPS 4 (DN 50 to DN 100)] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain one of three paragraphs below.  Retain first paragraph to require all piping to be Type ACR, annealed temper.  Type ACR, annealed-temper tubing is available only in sizes NPS 1-1/2 (DN 40) and smaller.  Retain second paragraph if pipe sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all piping be of same tube type and joining method.  Retain third paragraph and subparagraphs to require different tube type and joining methods for various pipe sizes.

C. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

D. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

E. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:

Retain one of first two subparagraphs below.

1. [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range>:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

2. [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

3. [NPS 4 (DN 100)] <Insert pipe size>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain one of three paragraphs below.  Retain first paragraph to require all safety-relief-valve discharge piping to be steel.  Retain second paragraph to require all pipe sizes to be copper of same tube type and joining method.  Retain third paragraph and subparagraphs to require different tube type and joining methods for various pipe sizes.

F. Safety-Relief-Valve Discharge Piping:  Schedule 40, black-steel and wrought-steel fittings with welded joints.

G. Safety-Relief-Valve Discharge Piping:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

H. Safety-Relief-Valve Discharge Piping:

Retain one of first two subparagraphs below.

1. [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range>:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

2. [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered]joints.

3. [NPS 4 (DN 100)] <Insert pipe size>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

3.3 PIPING APPLICATIONS FOR REFRIGERANT R-407C

Retain one or both paragraphs below.  Retain first paragraph to require all piping to be Type ACR, annealed temper.  Type ACR, annealed-temper tubing is available only in sizes NPS 1-1/2 (DN 40) and smaller.  Retain second paragraph if pipe sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all piping be of same tube type and joining method.  Retain both paragraphs to require piping larger than NPS 1-1/2 (DN 40) to be different than Type ACR, annealed temper.  Delete both paragraphs if suction lines are part of a heat-pump installation.

A. Suction Lines [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

B. Suction Lines [NPS 4 (DN 100) and Smaller] [NPS 2 to NPS 4 (DN 50 to DN 100)] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain one of three paragraphs below.  Retain first paragraph to require all piping to be Type ACR, annealed temper.  Type ACR, annealed-temper tubing is available only in sizes NPS 1-1/2 (DN 40) and smaller; however, brazed ACR can withstand pressure of this service only up to NPS 1 (DN 25).  Retain second paragraph if pipe sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all piping be of same tube type and joining method.  Retain third paragraph and subparagraphs to require different tube type and joining methods for various pipe sizes.

C. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

D. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

E. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:

Retain one of first two subparagraphs below.

1. [NPS 1 (DN 25) and Smaller] <Insert pipe size range>:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

2. [NPS 1 (DN 25) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

3. [NPS 1-1/4 to NPS 2 (DN 32 to DN 50)] <Insert pipe size range>:  Copper, Type K (A), annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

4. [NPS 4 (DN 100)] <Insert pipe size>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

Retain one of three paragraphs below.  Retain first paragraph to require all safety-relief-valve discharge piping to be steel.  Retain second paragraph to require all pipe sizes to be copper of same tube type and joining method.  Retain third paragraph and subparagraphs to require different tube type and joining methods for various pipe sizes.

F. Safety-Relief-Valve Discharge Piping:  Schedule 40, black-steel and wrought-steel fittings with welded joints.

G. Safety-Relief-Valve Discharge Piping:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

H. Safety-Relief-Valve Discharge Piping:

Retain one of first two subparagraphs below.

1. [NPS 1 (DN 25) and Smaller] <Insert pipe size range>:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

2. [NPS 1 (DN 25) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered]joints.

3. [NPS 1-1/4 to NPS 2 (DN 32 to DN 50)] <Insert pipe size range>:  Copper, Type K (A), annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

4. [NPS 4 (DN 100)] <Insert pipe size>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

3.4 PIPING APPLICATIONS FOR REFRIGERANT R-410A

Retain one of three paragraphs below.  Retain first paragraph to require all piping to be Type ACR, annealed temper.  Type ACR, annealed temper tubing is only available in sizes NPS 1-1/2 (DN 40) and smaller.  Retain second or third paragraph if pipe sizes exceed NPS 1-1/2 (DN 40) and it is desirable to have all piping be of same tube type and joining method.  Retain second and third paragraphs to require piping larger than NPS 1-1/2 (DN 40) to be different than Type ACR, annealed temper.  Delete all three paragraphs if suction lines are part of a heat-pump installation.

A. Suction Lines [NPS 1-1/2 (DN 40) and Smaller] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type ACR, annealed-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

B. Suction Lines [NPS 3-1/2 (DN 90) and Smaller] [NPS 2 to NPS 3-1/2 (DN 50 to DN 90)] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type [ACR] [L (B)], drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

C. Suction Lines [NPS 4 (DN 100) and Smaller] <Insert pipe size range> for Conventional Air-Conditioning Applications:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with soldered joints.

Retain one or more of first six paragraphs below.  Each material and each joining method is limited by the pressure rating on the resulting material and joining methods.  See Pressure Ratings of Copper Tube Joints, psig (kPa) Table in the Evaluations for pressure-rating limitations.  Retain first paragraph for tubing not larger than NPS 5/8 (DN 18) and it is desirable to have all piping be of same tube type and joining method.

D. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type [ACR] [L (B)], annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain paragraph below for tubing not larger than NPS 1 (DN 25) and it is desirable to have all piping be of same tube type and joining method.

E. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type K (A), annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain paragraph below for tubing not larger than NPS 1-1/4 (DN 32) and it is desirable to have all piping be of same tube type and joining method.

F. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with 95-5 tin-antimony soldered joints.

Retain paragraph below for tubing not larger than NPS 2 (DN 50) and it is desirable to have all piping be of same tube type and joining method.

G. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with Alloy HB soldered joints.

Retain paragraph and subparagraphs below to require different tube type and joining methods for various pipe sizes.

H. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications]:

1. [NPS 5/8 (DN 18) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [L (B)], annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

2. [NPS 3/4 to NPS 1 (DN 20 to DN 25) and Smaller] <Insert pipe size range>:  Copper, Type K (A), annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

3. [NPS 1-1/4 (DN 32) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with 95-5 tin-antimony soldered joints.

4. [NPS 1-1/2 to NPS 2 (DN 40 to DN 50)] <Insert pipe size range>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with Alloy HB soldered joints.

Retain paragraph below if required pipe sizes exceed copper pipe sizes in paragraph and subparagraphs above.

I. Hot-Gas and Liquid Lines[, and Suction Lines for Heat-Pump Applications] [NPS 2 to NPS 4 (DN 50 to DN 100)] <Insert pipe size range>:  Schedule 40, black-steel and wrought-steel fittings with welded joints.

Retain one of six paragraphs below.  Each material and each joining method is limited by the pressure rating on the resulting material and joining methods.  See Pressure Ratings of Copper Tube Joints, psig (kPa) Table in the Evaluations for pressure-rating limitations.  Retain first paragraph for tubing not larger than NPS 5/8 (DN 18) and it is desirable to have all piping be of same tube type and joining method.

J. Safety-Relief-Valve Discharge Piping:  Copper, Type [ACR] [L (B)], annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain paragraph below for tubing not larger than NPS 1 (DN 25) and it is desirable to have all piping be of same tube type and joining method.

K. Safety-Relief-Valve Discharge Piping:  Copper, Type K (A), annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

Retain paragraph below for tubing not larger than NPS 1-1/4 (DN 32) and it is desirable to have all piping be of same tube type and joining method.

L. Safety-Relief-Valve Discharge Piping:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with 95-5 tin-antimony soldered joints.

Retain paragraph below for tubing not larger than NPS 2 (DN 50) and it is desirable to have all piping be of same tube type and joining method.

M. Safety-Relief-Valve Discharge Piping:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with Alloy HB soldered joints.

Retain paragraph and subparagraphs below to require different tube type and joining methods for various pipe sizes.

N. Safety-Relief-Valve Discharge Piping:

1. [NPS 5/8 (DN 18) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [L (B)], annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

2. [NPS 3/4 to NPS 1 (DN 20 to DN 25) and Smaller] <Insert pipe size range>:  Copper, Type K (A), annealed- or drawn-temper tubing and wrought-copper fittings with [brazed] [or] [soldered] joints.

3. [NPS 1-1/4 (DN 32) and Smaller] <Insert pipe size range>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with 95-5 tin-antimony soldered joints.

4. [NPS 1-1/2 to NPS 2 (DN 40 to DN 50)] <Insert pipe size range>:  Copper, Type [ACR] [K (A)] [L (B)], drawn-temper tubing and wrought-copper fittings with Alloy HB soldered joints.

Retain paragraph below if required pipe sizes exceed copper pipe sizes in paragraph and subparagraphs above.

O. Safety-Relief-Valve Discharge Piping [NPS 2 to NPS 4 (DN 50 to DN 100)] <Insert pipe size range>:  Schedule 40, black-steel and wrought-steel fittings with welded joints.

3.5 VALVE AND SPECIALTY APPLICATIONS

Delete first paragraph below if valves are specified in Division 23 Section "Packaged Compressor and Condenser Units."

A. Install [diaphragm packless] [packed-angle] valves in suction and discharge lines of compressor.

B. Install service valves for gage taps at inlet and outlet of hot-gas bypass valves and strainers if they are not an integral part of valves and strainers.

Retain first paragraph below if suction line will be exposed to air temperatures less than 75 deg F (24 deg C) during compressor operation.

C. Install a check valve at the compressor discharge and a liquid accumulator at the compressor suction connection.

D. Except as otherwise indicated, install [diaphragm packless] [packed-angle] valves on inlet and outlet side of filter dryers.

Retain paragraph below only for systems that cannot be shut down for a short time to replace the filter dryer.

E. Install a full-sized, three-valve bypass around filter dryers.

Retain first paragraph below for solenoid valves on systems with multiple thermostatic expansion valves.  Retain for hot-gas bypass valve if not integral to the valve.

F. Install solenoid valves upstream from each expansion valve and hot-gas bypass valve.  Install solenoid valves in horizontal lines with coil at top.

G. Install thermostatic expansion valves as close as possible to distributors on evaporators.

1. Install valve so diaphragm case is warmer than bulb.

In first subparagraph below, verify proper location for bulb with valve manufacturer.

2. Secure bulb to clean, straight, horizontal section of suction line using two bulb straps.  Do not mount bulb in a trap or at bottom of the line.

3. If external equalizer lines are required, make connection where it will reflect suction-line pressure at bulb location.

H. Install safety relief valves where required by ASME Boiler and Pressure Vessel Code.  Pipe safety-relief-valve discharge line to outside according to ASHRAE 15.

I. Install moisture/liquid indicators in liquid line at the inlet of the thermostatic expansion valve or at the inlet of the evaporator coil capillary tube.

J. Install strainers upstream from and adjacent to the following unless they are furnished as an integral assembly for device being protected:

Edit list below for equipment required for Project.

1. Solenoid valves.

2. Thermostatic expansion valves.

3. Hot-gas bypass valves.

4. Compressor.

K. Install filter dryers in liquid line between compressor and thermostatic expansion valve[, and in the suction line at the compressor].

Consult refrigeration equipment manufacturer to determine the need for a receiver.

L. Install receivers sized to accommodate pump-down charge.

See Evaluations for discussion of flexible connectors.

M. Install flexible connectors at compressors.

3.6 PIPING INSTALLATION

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems; indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.  Install piping as indicated unless deviations to layout are approved on Shop Drawings.

B. Install refrigerant piping according to ASHRAE 15.

C. Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

D. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

E. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

F. Install piping adjacent to machines to allow service and maintenance.

G. Install piping free of sags and bends.

H. Install fittings for changes in direction and branch connections.

I. Select system components with pressure rating equal to or greater than system operating pressure.

J. Refer to Division 23 Sections "Instrumentation and Control for HVAC" and "Sequence of Operation" for solenoid valve controllers, control wiring, and sequence of operation.

K. Install piping as short and direct as possible, with a minimum number of joints, elbows, and fittings.

L. Arrange piping to allow inspection and service of refrigeration equipment.  Install valves and specialties in accessible locations to allow for service and inspection.  Install access doors or panels as specified in Division 08 Section "Access Doors and Frames" if valves or equipment requiring maintenance is concealed behind finished surfaces.

M. Install refrigerant piping in protective conduit where installed belowground.

N. Install refrigerant piping in rigid or flexible conduit in locations where exposed to mechanical injury.

O. Slope refrigerant piping as follows:

See Evaluations for discussion of oil entrainment.  Refer to the 2002 ASHRAE HANDBOOK - "Refrigeration" for discussion of methods for managing oil entrainment in refrigerant gas and liquid.

1. Install horizontal hot-gas discharge piping with a uniform slope downward away from compressor.

2. Install horizontal suction lines with a uniform slope downward to compressor.

Use double-suction riser for maximum compressor efficiencies if load variation is expected.

3. Install traps and double risers to entrain oil in vertical runs.

4. Liquid lines may be installed level.

P. When brazing or soldering, remove solenoid-valve coils and sight glasses; also remove valve stems, seats, and packing, and accessible internal parts of refrigerant specialties.  Do not apply heat near expansion-valve bulb.

Retain first paragraph and subparagraphs below for steel pipe.  Review the cost of steel pipe using these procedures versus the cost of copper piping.  Also consider limiting the size of the refrigerant system and its piping to avoid the use of steel pipe.

Q. Before installation of steel refrigerant piping, clean pipe and fittings using the following procedures:

1. Shot blast the interior of piping.

2. Remove coarse particles of dirt and dust by drawing a clean, lintless cloth through tubing by means of a wire or electrician's tape.

3. Draw a clean, lintless cloth saturated with trichloroethylene through the tube or pipe.  Continue this procedure until cloth is not discolored by dirt.

4. Draw a clean, lintless cloth, saturated with compressor oil, squeezed dry, through the tube or pipe to remove remaining lint.  Inspect tube or pipe visually for remaining dirt and lint.

5. Finally, draw a clean, dry, lintless cloth through the tube or pipe.

6. Safety-relief-valve discharge piping is not required to be cleaned but is required to be open to allow unrestricted flow.

R. Install pipe sleeves at penetrations in exterior walls and floor assemblies.

S. Seal penetrations through fire and smoke barriers according to Division 07 Section "Penetration Firestopping."

T. Install piping with adequate clearance between pipe and adjacent walls and hangers or between pipes for insulation installation.

U. Install sleeves through floors, walls, or ceilings, sized to permit installation of full-thickness insulation.

V. Seal pipe penetrations through exterior walls according to Division 07 Section "Joint Sealants" for materials and methods.

W. Identify refrigerant piping and valves according to Division 23 Section "Identification for HVAC Piping and Equipment."

3.7 PIPE JOINT CONSTRUCTION

A. Ream ends of pipes and tubes and remove burrs.  Bevel plain ends of steel pipe.

B. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

Retain first paragraph below for steel pipe.

C. Fill pipe and fittings with an inert gas (nitrogen or carbon dioxide), during brazing or welding, to prevent scale formation.

D. Soldered Joints:  Construct joints according to ASTM B 828 or CDA's "Copper Tube Handbook."

E. Brazed Joints:  Construct joints according to AWS's "Brazing Handbook," Chapter "Pipe and Tube."

1. Use Type BcuP, copper-phosphorus alloy for joining copper socket fittings with copper pipe.

2. Use Type BAg, cadmium-free silver alloy for joining copper with bronze or steel.

F. Threaded Joints:  Thread steel pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads unless dry-seal threading is specified.

2. Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.  Do not use pipe sections that have cracked or open welds.

G. Steel pipe can be threaded, but threaded joints must be seal brazed or seal welded.

H. Welded Joints:  Construct joints according to AWS D10.12/D10.12M.

I. Flanged Joints:  Select appropriate gasket material, size, type, and thickness for service application.  Install gasket concentrically positioned.  Use suitable lubricants on bolt threads.

3.8 HANGERS AND SUPPORTS

Piping hangers and supports must accommodate expansion and contraction, vibration, dead load of piping and its contents, and seismic-bracing requirements.

A. Hanger, support, and anchor products are specified in Division 23 Section "Hangers and Supports for HVAC Piping and Equipment."

B. Install the following pipe attachments:

1. Adjustable steel clevis hangers for individual horizontal runs less than 20 feet (6 m) long.

2. Roller hangers and spring hangers for individual horizontal runs 20 feet (6 m) or longer.

3. Pipe Roller:  MSS SP-58, Type 44 for multiple horizontal piping 20 feet (6 m) or longer, supported on a trapeze.

4. Spring hangers to support vertical runs.

5. Copper-clad hangers and supports for hangers and supports in direct contact with copper pipe.

C. Install hangers for copper tubing with the following maximum spacing and minimum rod sizes:

Verify actual supported loads for hanger sizes and spacing.  Consult structural engineer.  Spacing and sizes in subparagraphs below are from the 2000 ASHRAE HANDBOOK - "HVAC Systems and Equipment."

1. NPS 1/2 (DN 15):  Maximum span, 60 inches (1500 mm); minimum rod size, 1/4 inch (6.4 mm).

2. NPS 5/8 (DN 18):  Maximum span, 60 inches (1500 mm); minimum rod size, 1/4 inch (6.4 mm).

3. NPS 1 (DN 25):  Maximum span, 72 inches (1800 mm); minimum rod size, 1/4 inch (6.4 mm).

4. NPS 1-1/4 (DN 32):  Maximum span, 96 inches (2400 mm); minimum rod size, 3/8 inch (9.5 mm).

5. NPS 1-1/2 (DN 40):  Maximum span, 96 inches (2400 mm); minimum rod size, 3/8 inch (9.5 mm).

6. NPS 2 (DN 50):  Maximum span, 96 inches (2400 mm); minimum rod size, 3/8 inch (9.5 mm).

7. NPS 2-1/2 (DN 65):  Maximum span, 108 inches (2700 mm); minimum rod size, 3/8 inch (9.5 mm).

8. NPS 3 (DN 80):  Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (9.5 mm).

9. NPS 4 (DN 100):  Maximum span, 12 feet (3.7 m); minimum rod size, 1/2 inch (13 mm).

D. Install hangers for steel piping with the following maximum spacing and minimum rod sizes:

1. NPS 2 (DN 50):  Maximum span, 10 feet (3 m); minimum rod size, 3/8 inch (9.5 mm).

2. NPS 2-1/2 (DN 65):  Maximum span, 11 feet (3.4 m); minimum rod size, 3/8 inch (9.5 mm).

3. NPS 3 (DN 80):  Maximum span, 12 feet (3.7 m); minimum rod size, 3/8 inch (9.5 mm).

4. NPS 4 (DN 100):  Maximum span, 14 feet (4.3 m); minimum rod size, 1/2 inch (13 mm).

E. Support multifloor vertical runs at least at each floor.

3.9 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

B. Tests and Inspections:

1. Comply with ASME B31.5, Chapter VI.

2. Test refrigerant piping, specialties, and receivers.  Isolate compressor, condenser, evaporator, and safety devices from test pressure if they are not rated above the test pressure.

3. Test high- and low-pressure side piping of each system separately at not less than the pressures indicated in Part 1 "Performance Requirements" Article.

a. Fill system with nitrogen to the required test pressure.

b. System shall maintain test pressure at the manifold gage throughout duration of test.

c. Test joints and fittings with electronic leak detector or by brushing a small amount of soap and glycerin solution over joints.

d. Remake leaking joints using new materials, and retest until satisfactory results are achieved.

3.10 SYSTEM CHARGING

A. Charge system using the following procedures:

1. Install core in filter dryers after leak test but before evacuation.

2. Evacuate entire refrigerant system with a vacuum pump to 500 micrometers (67 Pa).  If vacuum holds for 12 hours, system is ready for charging.

3. Break vacuum with refrigerant gas, allowing pressure to build up to 2 psig (14 kPa).

4. Charge system with a new filter-dryer core in charging line.

3.11 ADJUSTING

Retain first paragraph below for adjustable thermostatic expansion valves.

A. Adjust thermostatic expansion valve to obtain proper evaporator superheat.

B. Adjust high- and low-pressure switch settings to avoid short cycling in response to fluctuating suction pressure.

C. Adjust set-point temperature of air-conditioning or chilled-water controllers to the system design temperature.

D. Perform the following adjustments before operating the refrigeration system, according to manufacturer's written instructions:

1. Open shutoff valves in condenser water circuit.

2. Verify that compressor oil level is correct.

3. Open compressor suction and discharge valves.

4. Open refrigerant valves except bypass valves that are used for other purposes.

5. Check open compressor-motor alignment and verify lubrication for motors and bearings.

E. Replace core of replaceable filter dryer after system has been adjusted and after design flow rates and pressures are established.

END OF SECTION 23 2300

	REFRIGERANT PIPING
	232300 - 1



