Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
09/03 (R 06/05)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233413 - AXIAL HVAC FANS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Tubeaxial fans.

2. Vaneaxial fans.

3. Mixed-flow fans.

1.3 PERFORMANCE REQUIREMENTS

Select one of two paragraphs in this Article.

A. Project Altitude:  Base fan performance ratings on [actual Project site elevations above] sea level.

B. Operating Limits:  Classify according to AMCA 99.

1.4 SUBMITTALS

A. Product Data:  Include rated capacities, furnished specialties, and accessories for each type of product indicated and include the following:

1. Certified fan performance curves with system operating conditions indicated.

2. Certified fan sound-power ratings.

3. Motor ratings and electrical characteristics, plus motor and electrical accessories.

4. Material thickness and finishes, including color charts.

5. Dampers, including housings, linkages, and operators.

6. Fan speed controllers.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

2. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

3. Vibration Isolation Base Details:  Detail fabrication, including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails, and base weights.

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Show fan room layout and relationships between components and adjacent structural and mechanical elements.  Show support locations, type of support, and weight on each support.  Indicate and certify field measurements.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For axial fans to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

AMCA compliance is an optional requirement and not necessarily available from all manufacturers.

B. AMCA Compliance:  Products shall comply with performance requirements and shall be licensed to use the AMCA-Certified Ratings Seal.

C. NEMA Compliance:  Motors and electrical accessories shall comply with NEMA standards.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Deliver fans as factory-assembled units, to the extent allowable by shipping limitations, with protective crating and covering.

B. Disassemble and reassemble units, as required for moving to final locations, according to manufacturer's written instructions.

C. Lift and support units with manufacturer's designated lifting or supporting points.

1.7 COORDINATION

Edit first paragraph below to delete or add types of construction.

A. Coordinate size and location of structural-steel support members.

B. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Belts:  [One] <Insert number> set(s) for each belt-driven unit.

PART 2 -  PRODUCTS

2.1 TUBEAXIAL FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan Company.

3. Airmaster Fan Co.

4. American Coolair Corp.

5. American Fan Company.

6. Ammerman; General Resource Corp.

7. Barry Blower Div.; Penn Ventilation Companies, Inc.

8. Bayley Fans; a division of Lau Industries, Inc.

9. Carnes Company HVAC.

10. Chicago Blower Corporation.

11. Cincinnati Fan.

12. CML Northern Blower, Inc.

13. Greenheck.

14. Hartzell Fan, Inc.

15. Howden Fan Co.

16. Industrial Air; a division of Lau Industries, Inc.

17. Loren Cook Company.

18. Madison Manufacturing.

19. New Philadelphia Fan Co.

20. New York Blower Company (The).

21. Stanley Fans.

22. Trane.

23. <Insert manufacturer's name.>

D. Description:  Fan wheel and housing, factory-mounted motor with belt drive or direct drive, an inlet cone section, and accessories.

E. Housings:  [Steel] [Galvanized steel] [Aluminum] [Fiberglass-reinforced plastic] [Stainless steel] with flanged inlet and outlet connections.

Retain one of three paragraphs below.

F. Wheel Assemblies:  Cast or extruded aluminum with airfoil-shaped blades mounted on cast-iron wheel plate keyed to shaft with solid-steel key.

G. Wheel Assemblies:  Fiberglass-reinforced plastic cured under pressure with airfoil-shaped blades keyed to stainless steel shaft.

H. Wheel Assemblies:  Cast aluminum, machined and fitted to shaft.

Retain first paragraph and subparagraphs below for belt-driven fans.

I. Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  [1.2] [1.3] [1.4] [1.5].

2. Fan Shaft:  Turned, ground, and polished steel designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

3. Fan Pulleys:  Cast iron with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is designer's choice.

4. Motor Pulleys:  Adjustable pitch for use with motors through [5] <Insert value> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

5. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

Belt guards are optional.

6. Belt Guards:  Fabricate of steel for motors mounted on outside of fan cabinet.

7. Motor Mount:  Adjustable base.

8. Shaft Bearings:  Radial, self-aligning ball or roller bearings.

Retain one of first two subparagraphs below.

a. Ball-Bearing Rating Life:  ABMA 9, [L10 of 100,000 hours] <Insert life>.

b. Roller-Bearing Rating Life:  ABMA 11, [L10 of 100,000 hours] <Insert life>.

c. Extend lubrication lines to outside of casing and terminate with grease fittings.

J. Accessories:

Retain only applicable subparagraphs below.

1. Companion Flanges:  Rolled flanges of same material as housing.

2. Inspection Door:  Bolted door allowing limited access to internal parts of fan, of same material as housing.

3. Propeller Access Section Door:  Short duct section bolted to fan [inlet] [outlet] [inlet and outlet] allowing access to internal parts of fan for inspection and cleaning, of same material as housing.

4. Swingout Construction:  Assembly allowing entire fan section to swing out from duct for cleaning and servicing, of same material as housing.

5. Mounting Clips:  [Horizontal ceiling] [Vertical mounting] clips welded to fan housing, of same material as housing.

6. Horizontal Support:  Pair of supports bolted to fan housing, of same material as housing.

7. Vertical Support:  Short duct section with welded brackets bolted to fan housing, of same material as housing.

8. Inlet and Outlet Screens:  Wire-mesh screen on fans not connected to ductwork, of same material as housing.

9. Backdraft Dampers:  Butterfly style, for bolting to the discharge of fan or outlet cone, of same material as housing.

10. Shaft Seal:  Elastomeric seal and Teflon wear plate, suitable for up to 300 deg F (149 deg C).

11. Motor Cover:  Cover with side vents to dissipate motor heat, of same material as housing.

12. Inlet Vanes:  Adjustable; with peripheral control linkage operated from outside of airstream, bronze sleeve bearings on each end of vane support, and provision for manual or automatic operation of same material as housing.

13. Inlet Bell:  Curved inlet for when fan is not attached to duct, [of same material as housing] [aluminum].

14. Inlet Cones:  Round-to-round transition of same material as housing.

15. Outlet Cones:  Round-to-round transition of same material as housing.

16. Stack Cap:  Vertical discharge assembly with backdraft dampers, of same material as housing.

K. Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."  If different characteristics are required, add subparagraphs to suit Project.

Retain first subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type:  [Totally enclosed, fan cooled] [Totally enclosed, nonventilated].

2. Direct-Driven Units:  Encase motor in housing outside of airstream[, factory wired to disconnect switch located on outside of fan housing].

L. Factory Finishes:

1. Sheet Metal Parts:  Prime coat before final assembly.

2. Exterior Surfaces:  Baked-enamel finish coat after assembly.

Retain coatings for special protection applications.  Review manufacturer's data for specific trade names and literature.

3. Coatings:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

a. Apply to finished housings.

b. Apply to fan wheels.

If Project has more than one type or configuration of tubeaxial fan, delete paragraph and subparagraphs below and schedule tubeaxial fans on Drawings.

M. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Brake Horsepower:  <Insert value.>

5. Drive Type:  [Direct] [Belt].

6. Fan Rpm:  <Insert value.>

7. Motor Size:  <Insert value> hp.

8. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Minimum Circuit Ampacity:  <Insert value.>

e. Maximum Overcurrent Protection:  <Insert value.>

9. Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

10. Vibration Isolators:  [Spring isolators] [Restrained spring isolators] <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

2.2 VANEAXIAL FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan Company.

3. Airmaster Fan Co.

4. American Coolair Corp.

5. American Fan Company.

6. Ammerman; General Resource Corp.

7. Barry Blower Div.; Penn Ventilation Companies, Inc.

8. Bayley Fans; a division of Lau Industries, Inc.

9. Carnes Company HVAC.

10. Chicago Blower Corporation.

11. Cincinnati Fan.

12. CML Northern Blower, Inc.

13. Greenheck.

14. Hartzell Fan, Inc.

15. Howden Fan Co.

16. Industrial Air; a division of Lau Industries, Inc.

17. Loren Cook Company.

18. Madison Manufacturing.

19. New Philadelphia Fan Co.

20. New York Blower Company (The).

21. Stanley Fans.

22. Trane.

23. <Insert manufacturer's name.>

D. Description:  Fan wheel and housing, straightening vane section, factory-mounted motor with belt drive or direct drive, an inlet cone section, and accessories.

1. Variable-Pitch Fans:  Internally mounted [pneumatic] [electric] [electronic] actuator, externally mounted positive positioner, and mechanical-blade-pitch indicator.

E. Housings:  [Steel] [Galvanized steel] [Aluminum] [Fiberglass-reinforced plastic] [Stainless steel].

1. Inlet and Outlet Connections:  Flanges.

2. Guide Vane Section:  Integral guide vanes downstream from fan wheel designed to straighten airflow.

Retain one of three paragraphs below.

F. Wheel Assemblies:  Cast aluminum with airfoil-shaped blades mounted on cast-iron wheel plate keyed to shaft with solid-steel key.

G. Wheel Assemblies:  Fiberglass-reinforced plastic cured under pressure with airfoil-shaped blades keyed to stainless steel shaft.

H. Wheel Assemblies:  Cast-aluminum hub assembly, machined and fitted with threaded bearing wells to receive blade-bearing assemblies with replaceable, cast-aluminum blades; factory mounted and balanced.

Retain first paragraph and subparagraphs below for belt-driven fans.

I. Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  [1.2] [1.3] [1.4] [1.5].

2. Fan Shaft:  Turned, ground, and polished steel designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

3. Fan Pulleys:  Cast iron with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is designer's choice.

4. Motor Pulleys:  Adjustable pitch for use with motors through [5]<Insert value> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

5. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

6. Belt Guards:  Fabricate of steel for motors mounted on outside of fan cabinet.

7. Motor Mount:  Adjustable base.

8. Shaft Bearings:  Radial, self-aligning ball or roller bearings.

Retain one of first two subparagraphs below.

a. Ball-Bearing Rating Life:  ABMA 9, [L10 of 100,000 hours] <Insert life>.

b. Roller-Bearing Rating Life:  ABMA 11, [L10 of 100,000 hours] <Insert life>.

c. Extend lubrication lines to outside of casing and terminate with grease fittings.

J. Accessories:

Retain only applicable subparagraphs below.

1. Companion Flanges:  Rolled flanges of same material as housing.

2. Inspection Door:  Bolted door allowing limited access to internal parts of fan, of same material as housing.

3. Propeller Access Section Door:  Short duct section bolted to fan [inlet] [outlet] [inlet and outlet] allowing access to internal parts of fan for inspection and cleaning, of same material as housing.

4. Swingout Construction:  Assembly allowing entire fan section to swing out from duct for cleaning and servicing, of same material as housing.

5. Mounting Clips:  [Horizontal ceiling] [Vertical mounting] clips welded to fan housing, of same material as housing.

6. Horizontal Support:  Pair of supports bolted to fan housing, of same material as housing.

7. Vertical Support:  Short duct section with welded brackets bolted to fan housing, of same material as housing.

8. Inlet and Outlet Screens:  Wire-mesh screen on fans not connected to ductwork of same material as housing.

9. Backdraft Dampers:  Butterfly style, for mounting with flexible connection to the discharge of fan or direct mounted to the discharge diffuser section of same material as housing.

Stall alarm in first subparagraph below may be used to activate an alarm, to activate controls to adjust blade pitch, or to shut down fan.

10. Stall Alarm Probe:  Sensing probe capable of detecting fan operation in stall and signaling control devices.  Control devices and sequence of operation are specified in Division 23 Sections "Instrumentation and Control for HVAC" and "Sequence of Operations for HVAC Controls."

11. Flow Measurement Port:  Pressure measurement taps installed in the inlet of fan to detect and signal airflow readings to temperature-control systems.  Control devices and sequence of operation are specified in Division 23 Sections "Instrumentation and Control for HVAC" and "Sequence of Operations for HVAC Controls."

12. Shaft Seal:  Elastomeric seal and Teflon wear plate, suitable for up to300 deg F (148 deg C).

13. Motor Cover:  Cover with side vents to dissipate motor heat, of same material as housing.

14. Inlet Vanes:  Adjustable; with peripheral control linkage operated from outside of airstream, bronze sleeve bearings on each end of vane support, and provision for manual or automatic operation of same material as housing.

15. Inlet Bell:  Curved inlet for when fan is not attached to duct, of same material as housing.

16. Inlet Cones:  Round-to-round transition of same material as housing.

17. Outlet Cones:  Round-to-round transition of same material as housing.

18. Stack Cap:  Vertical discharge assembly with backdraft dampers, of same material as housing.

K. Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."  If different characteristics are required, add subparagraphs to suit Project.

Retain first subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type:  [Totally enclosed, fan cooled] [Totally enclosed, nonventilated].

2. Direct-Driven Units:  Encase motor in housing outside of airstream[, factory wired to disconnect switch located on outside of fan housing].

L. Factory Finishes:

1. Sheet Metal Parts:  Prime coat before final assembly.

2. Exterior Surfaces:  Baked-enamel finish coat after assembly.

Retain coatings for special protection applications.  Review manufacturer's data for specific trade names and literature.

3. Coatings:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

a. Apply to finished housings.

b. Apply to fan wheels.

If Project has more than one type or configuration of vaneaxial fan, delete paragraph and subparagraphs below and schedule vaneaxial fans on Drawings.

M. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Brake Horsepower:  <Insert value.>

5. Drive Type:  [Direct] [Belt].

6. Fan Rpm:  <Insert value>.

7. Motor Size:  <Insert value> hp.

8. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Minimum Circuit Ampacity:  <Insert value.>

e. Maximum Overcurrent Protection:  <Insert value.>

9. Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

10. Vibration Isolators:  [Spring isolators] [Restrained spring isolators] <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

2.3 MIXED-FLOW FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Loren Cook Company.

2. Greenheck.

3. Howden Fan Co.

4. New Philadelphia Fan Co.

5. <Insert manufacturer's name.>

D. Description:  Fan wheel and housing,[ straightening vane section,] factory-mounted motor with belt drive, and accessories.

E. Housings:  [Steel] [Galvanized steel] [Aluminum].

1. Inlet and Outlet Connections:  Outer mounting frame and companion flanges.

2. Guide Vane Section:  Integral guide vanes downstream from fan wheel designed to straighten airflow.

Retain subparagraph below only for fans configured this way.

3. Mixed-Flow Outlet Connection:  [One] [Two] flanged discharge(s) perpendicular to fan inlet.

F. Wheel Assemblies:  Cast aluminum with airfoil-shaped blades mounted on cast-iron wheel plate keyed to shaft with solid-steel key.

Retain first paragraph and subparagraphs below for belt-driven fans.

G. Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  [1.2] [1.3] [1.4] [1.5].

2. Fan Shaft:  Turned, ground, and polished steel designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

3. Fan Pulleys:  Cast iron with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is designer's choice.

4. Motor Pulleys:  Adjustable pitch for use with motors through [5] <Insert value> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

5. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

6. Motor Mount:  Adjustable base.

7. Shaft Bearings:  Radial, self-aligning ball or roller bearings.

Retain one of first two subparagraphs below.

a. Ball-Bearing Rating Life:  ABMA 9, [L10 of 100,000 hours] <Insert life>.

b. Roller-Bearing Rating Life:  ABMA 11, [L10 of 100,000 hours] <Insert life>.

c. Extend lubrication lines to outside of casing and terminate with grease fittings.

H. Accessories:

Retain only applicable subparagraphs below.

1. Mounting Clips:  [Horizontal ceiling] [Vertical mounting] clips welded to fan housing, of same material as housing.

2. Inlet and Outlet Screens:  Wire-mesh screen on fans not connected to ductwork of same material as housing.

3. Backdraft Dampers:  Butterfly style, for mounting with flexible connection to the discharge of fan or direct mounted to the discharge diffuser section of same material as housing.

4. Motor Cover:  Cover with side vents to dissipate motor heat, of same material as housing.

5. Inlet Bell:  Curved inlet for when fan is not attached to duct, of same material as housing.

6. Inlet Cones:  Round-to-round transition of same material as housing.

7. Outlet Cones:  Round-to-round transition of same material as housing.

8. Stack Cap:  Vertical discharge assembly with backdraft dampers, of same material as housing.

I. Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."  If different characteristics are required, add subparagraphs to suit Project.

Retain first subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type:  [Totally enclosed, fan cooled] [Totally enclosed, nonventilated].

2. Direct-Driven Units:  Encase motor in housing outside of airstream[, factory wired to disconnect switch located on outside of fan housing].

J. Factory Finishes:

1. Sheet Metal Parts:  Prime coat before final assembly.

2. Exterior Surfaces:  Baked-enamel finish coat after assembly.

Retain coatings for special protection applications.  Review manufacturer's data for specific trade names and literature.

3. Coatings:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

a. Apply to finished housings.

b. Apply to fan wheels.

If Project has more than one type or configuration of mixed-flow fan, delete paragraph and subparagraphs below and schedule mixed-flow fans on Drawings.

K. Capacities and Characteristics:

1. Airflow:  <Insert cfm (L/s).>

2. External Static Pressure:  <Insert inches wg (Pa).>

3. Fan Diameter:  <Insert inches (mm).>

4. Brake Horsepower:  <Insert value.>

5. Drive Type:  [Direct] [Belt].

6. Fan Rpm:  <Insert value.>

7. Motor Size:  <Insert value> hp.

8. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Minimum Circuit Ampacity:  <Insert value.>

e. Maximum Overcurrent Protection:  <Insert value.>

9. Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

10. Sound Power:  <Insert sones.>

11. Vibration Isolators:  [Spring isolators] [Restrained spring isolators] <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

2.4 SOURCE QUALITY CONTROL

Sound-power rating information may only be available from manufacturers on request.  Refer to discussion on sound and vibration control in the Evaluations.

A. Sound-Power Level Ratings:  Comply with AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data."  Factory test fans according to AMCA 300, "Reverberant Room Method for Sound Testing of Fans."  Label fans with the AMCA-Certified Ratings Seal.

B. Fan Performance Ratings:  Establish flow rate, pressure, power, air density, speed of rotation, and efficiency by factory tests and ratings according to AMCA 210, "Laboratory Methods of Testing Fans for Rating."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install axial fans level and plumb.

Retain and edit three paragraphs and associated subparagraph below for floor-mounting units; delete if vibration and seismic controls are specified in Part 2 "Capacities and Characteristics" paragraphs or are indicated on Drawings.  If not scheduled, identify required vibration- and seismic-control device by using the titles of devices described in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" and identify its required static deflection.

B. Support floor-mounting units using [spring isolators] [restrained spring isolators] <Insert device> having a static deflection of [1 inch (25 mm)] <Insert deflection>.  Vibration- and seismic-control devices are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Secure vibration and seismic controls to concrete bases using anchor bolts cast in concrete base.

C. Install floor-mounting units on concrete bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03 Section "Cast-in-Place Concrete."

Retain paragraph above for projects not in seismic areas; retain paragraph below for projects in seismic areas.

D. Install floor-mounting units on concrete bases designed to withstand, without damage to equipment, the seismic force required by authorities having jurisdiction.  Concrete, reinforcement, and formwork requirements are specified in Division 03 Section "Cast-in-Place Concrete."

Retain and edit first paragraph below for suspended units; delete if vibration and seismic controls are specified in Part 2 "Capacities and Characteristics" paragraphs or are indicated on Drawings.  If not scheduled, identify required vibration- and seismic-control device by using the titles of devices described in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" and identify its required static deflection.

E. Support suspended units from structure using threaded steel rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stops] <Insert device> having a static deflection of [1 inch (25 mm)] <Insert deflection>.  Vibration-control devices are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

F. Install units with clearances for service and maintenance.

G. Label fans according to requirements specified in Division 23 Section "Identification for HVAC Piping and Equipment."

3.2 CONNECTIONS

Coordinate duct installations and specialty arrangements with schematics on Drawings and with requirements specified in duct systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Duct installation and connection requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of ducts and duct accessories.  Make final duct connections with flexible connectors.  Flexible connectors are specified in Division 23 Section "Air Duct Accessories."

B. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

C. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. Verify that shipping, blocking, and bracing are removed.

2. Verify that unit is secure on mountings and supporting devices and that connections to ducts and electrical components are complete.  Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

3. Verify that cleaning and adjusting are complete.

4. Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation.  Reconnect fan drive system, align and adjust belts, and install belt guards.

5. Adjust belt tension.

6. Adjust damper linkages for proper damper operation.

7. Verify lubrication for bearings and other moving parts.

8. Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in fully open position.

9. Disable automatic temperature-control operators, energize motor and confirm proper motor rotation and unit operation, adjust fan to indicated rpm, and measure and record motor voltage and amperage.

10. Shut unit down and reconnect automatic temperature-control operators.

11. Remove and replace malfunctioning units and retest as specified above.

B. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3.4 ADJUSTING

A. Adjust damper linkages for proper damper operation.

B. Adjust belt tension.

C. Lubricate bearings.

END OF SECTION 233413

	AXIAL HVAC FANS
	233413 - 1



