Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
09/03 (R 06/05)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233416 - CENTRIFUGAL HVAC FANS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Airfoil centrifugal fans.

2. Backward-inclined centrifugal fans.

3. Forward-curved centrifugal fans.

4. Plenum fans.

5. Plug fans.

1.3 PERFORMANCE REQUIREMENTS

A. Project Altitude:  Base fan performance ratings on [actual Project site elevations above] sea level.

B. Operating Limits:  Classify according to AMCA 99.

1.4 SUBMITTALS

A. Product Data:  Include rated capacities, furnished specialties, and accessories for each type of product indicated and include the following:

1. Certified fan performance curves with system operating conditions indicated.

2. Certified fan sound-power ratings.

3. Motor ratings and electrical characteristics, plus motor and electrical accessories.

4. Material thickness and finishes, including color charts.

5. Dampers, including housings, linkages, and operators.

B. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

2. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

3. Vibration Isolation Base Details:  Detail fabrication, including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails, and base weights.

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Show fan room layout and relationships between components and adjacent structural and mechanical elements.  Show support locations, type of support, and weight on each support.  Indicate and certify field measurements.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For centrifugal fans to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

AMCA compliance is an optional requirement and not necessarily available from all manufacturers.

B. AMCA Compliance:  Products shall comply with performance requirements and shall be licensed to use the AMCA-Certified Ratings Seal.

C. NEMA Compliance:  Motors and electrical accessories shall comply with NEMA 1.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Deliver fans as factory-assembled units, to the extent allowable by shipping limitations, with protective crating and covering.

B. Disassemble and reassemble units, as required for moving to the final location, according to manufacturer's written instructions.

C. Lift and support units with manufacturer's designated lifting or supporting points.

1.7 COORDINATION

Edit first paragraph below to delete or add types of construction.

A. Coordinate size and location of structural-steel support members.

B. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Belts:  [One] <Insert number> set(s) for each belt-driven unit.

PART 2 -  PRODUCTS

2.1 AIRFOIL CENTRIFUGAL FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. ABB Fan Group North America.

2. Acme Engineering & Mfg. Corp.

3. Aerovent; a Twin City Fan Company.

4. Airmaster Fan Co.

5. Ammerman; General Resource Corp.

6. Bayley Fans; a division of Lau Industries, Inc.

7. Carrier Corporation.

8. Central Blower Company.

9. Chicago Blower Corporation.

10. Cincinnati Fan.

11. CML Northern Blower Inc.

12. Howden Fan Co.

13. Industrial Air; a division of Lau Industries, Inc.

14. Loren Cook Company.

15. Madison Manufacturing.

16. New Philadelphia Fan Co.

17. New York Blower Company (The).

18. Trane.

19. <Insert manufacturer's name.>

D. Description:  Factory-fabricated, -assembled, -tested, and -finished, belt-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor [and disconnect switch], drive assembly, and support structure.

E. Housings:  Formed panels to make curved-scroll housings with shaped cutoff, with doors or panels to allow access to internal parts and components.

1. Panel Bracing:  Steel angle- or channel-iron member supports for mounting and supporting fan scroll, wheel, motor, and accessories.

Split housings are an optional configuration.

2. Horizontally split, bolted-flange housing.

3. Spun inlet cone with flange.

4. Outlet flange.

F. Airfoil Wheels:  Single-width-single-inlet and double-width-double-inlet construction with curved inlet flange; heavy backplate; hollow die-formed, airfoil-shaped blades continuously welded at tip flange and backplate;[ and] cast-iron or cast-steel hub riveted to backplate and fastened to shaft with set screws[; and special coating].

G. Shafts:  Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with final alignment and belt adjustment made after installation.

1. Turned, ground, and polished hot-rolled steel with keyway.  Ship with protective coating of lubricating oil.

2. Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

Retain one of first three paragraphs and associated subparagraphs below or retain all appropriate types and indicate types in equipment schedule.  Verify availability with manufacturers; other bearing types may be available.

H. Prelubricated and Sealed Shaft Bearings:  Self-aligning, pillow-block-type ball bearings.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

I. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, tapered roller bearings with double-locking collars and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

J. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, ball or roller bearings with adapter mount and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

K. Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  [1.5] [1.4] [1.3] [1.2].

2. Fan Pulleys:  Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is designer's choice.

3. Motor Pulleys:  Adjustable pitch for use with motors through [5] <Insert number> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

4. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

5. Belt Guards:  Fabricate to comply with OSHA and SMACNA requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated.  Secure to fan or fan supports without short circuiting vibration isolation.  Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

6. Motor Mount:  Adjustable for belt tensioning.

L. Accessories:

Retain applicable subparagraphs below.  Verify availability with manufacturers.

1. Scroll Access Doors:  Shaped to conform to scroll, with quick-opening latches and gaskets.

2. Cleanout Door:  [Bolted] [Quick-opening, latch-type] gasketed door allowing access to fan scroll, of same material as housing.

3. Scroll Drain Connection:  NPS 1 (DN 25) steel pipe coupling welded to low point of fan scroll.

4. Companion Flanges:  Rolled flanges for duct connections of same material as housing.

5. Variable Inlet Vanes:  With blades supported at both ends with two permanently lubricated bearings of same material as housing.  Variable mechanism terminating in single control lever with control shaft for double-width fans.

6. Discharge Dampers:  Assembly with [parallel] [opposed] blades constructed of two plates formed around and to shaft, channel frame, and sealed ball bearings; with blades linked outside of airstream to single control lever of same material as housing.

7. Inlet Screens:  Grid screen of same material as housing.

8. Shaft Cooler:  Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

9. Spark-Resistant Construction:  AMCA 99.

10. Shaft Seals:  Airtight seals installed around shaft on drive side of single-width fans.

11. Weather Cover:  Enameled-steel sheet with ventilation slots, bolted to housing.

M. Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."  If different characteristics are required, add subparagraphs to suit Project.

Retain subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type:  Totally enclosed, fan cooled.

If Project has more than one type or configuration of centrifugal fan, delete paragraph and subparagraphs below and schedule fans on Drawings.

N. Capacities And Characteristics:

1. Housing Material:  [Reinforced steel] [Shaped fiberglass-reinforced plastic] [Aluminum] [Stainless steel].

2. Special Housing Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

3. Wheel Size (Diameter):  <Insert inches (mm).>

4. Wheel Material:  [Steel] [Aluminum] [One-piece fiberglass-reinforced plastic] [Stainless steel].

5. Special Wheel Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

6. Airflow:  <Insert cfm (L/s).>

7. Static Pressure:  <Insert inches wg (Pa).>

8. Class:  [I] [II] [III].

9. Brake Horsepower:  <Insert value.>

10. Drive Type:  [Belt] [Direct].

11. Fan Rpm:  <Insert value.>

12. Outlet Velocity:  <Insert fpm (m/s).>

13. Motor Size:  <Insert value> hp.

14. Motor Rpm:  <Insert value.>

15. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Minimum Circuit Ampacity:  <Insert value.>

e. Maximum Overcurrent Protection:  <Insert value.>

16. Discharge Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

17. Inlet Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

18. Vibration Isolators:  [Spring isolators] [Restrained spring isolators] <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

19. Spark Arrestance Class:  [A] [B] [C].

2.2 BACKWARD-INCLINED CENTRIFUGAL FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. ABB Fan Group North America.

2. Acme Engineering & Mfg. Corp.

3. Aerovent; a Twin City Fan Company.

4. Airmaster Fan Co.

5. Ammerman; General Resource Corp.

6. Bayley Fans; a division of Lau Industries, Inc.

7. Carrier Corporation.

8. Central Blower Company.

9. Chicago Blower Corporation.

10. Cincinnati Fan.

11. CML Northern Blower Inc.

12. Howden Fan Co.

13. Industrial Air; a division of Lau Industries, Inc.

14. Loren Cook Company.

15. Madison Manufacturing.

16. New Philadelphia Fan Co.

17. New York Blower Company (The).

18. Trane.

19. <Insert manufacturer's name.>

D. Description:  Factory-fabricated, -assembled, -tested, and -finished, belt-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor [and disconnect switch], drive assembly, and support structure.

E. Housings:  Formed panels to make curved-scroll housings with shaped cutoff; with doors or panels to allow access to internal parts and components.

1. Panel Bracing:  Steel angle- or channel-iron member supports for mounting and supporting fan scroll, wheel, motor, and accessories.

Split housings are an optional configuration.

2. Horizontally split, bolted-flange housing.

3. Spun inlet cone with flange.

4. Outlet flange.

F. Backward-Inclined Wheels:  Single-width-single-inlet and double-width-double-inlet construction with curved inlet flange, backplate, backward-inclined blades[ welded or riveted to flange and backplate; cast-iron or cast-steel hub riveted to backplate] and fastened to shaft with set screws.

G. Shafts:  Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with final alignment and belt adjustment made after installation.

1. Turned, ground, and polished hot-rolled steel with keyway.  Ship with a protective coating of lubricating oil.

2. Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

Retain one of first three paragraphs and associated subparagraphs below or retain all appropriate types and indicate types in equipment schedule.  Verify availability with manufacturers; other bearing types may be available.

H. Prelubricated and Sealed Shaft Bearings:  Self-aligning, pillow-block-type ball bearings.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

I. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, tapered roller bearings with double-locking collars and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

J. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, ball or roller bearings with adapter mount and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

K. Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  [1.5] [1.4] [1.3] [1.2].

2. Fan Pulleys:  Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is designer's choice.

3. Motor Pulleys:  Adjustable pitch for use with motors through [5] <Insert number> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

4. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

5. Belt Guards:  Fabricate to comply with OSHA and SMACNA requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated.  Secure to fan or fan supports without short circuiting vibration isolation.  Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

6. Motor Mount:  Adjustable for belt tensioning.

L. Accessories:

Retain applicable subparagraphs below.  Verify availability with manufacturers.

1. Scroll Access Doors:  Shaped to conform to scroll, with quick-opening latches and gaskets.

2. Cleanout Door:  [Bolted] [Quick-opening, latch-type] gasketed door allowing access to fan scroll, of same material as housing.

3. Scroll Drain Connection:  NPS 1 (DN 25) steel pipe coupling welded to low point of fan scroll.

4. Companion Flanges:  Rolled flanges for duct connections of same material as housing.

5. Variable Inlet Vanes:  With blades supported at both ends with two permanently lubricated bearings of same material as housing.  Variable mechanism terminating in single control lever with control shaft for double-width fans.

6. Discharge Dampers:  Assembly with [parallel] [opposed] blades constructed of two plates formed around and to shaft, channel frame, and sealed ball bearings; with blades linked outside of airstream to single control lever of same material as housing.

7. Inlet Screens:  Grid screen of same material as housing.

8. Shaft Cooler:  Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

9. Spark-Resistant Construction:  AMCA 99.

10. Shaft Seals:  Airtight seals installed around shaft on drive side of single-width fans.

11. Weather Cover:  Enameled-steel sheet with ventilation slots, bolted to housing.

M. Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."  If different characteristics are required, add subparagraphs to suit Project.

Retain subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type:  Totally enclosed, fan cooled.

If Project has more than one type or configuration of centrifugal fan, delete paragraph and subparagraphs below and schedule fans on Drawings.

N. Capacities And Characteristics:

1. Housing Material:  [Reinforced steel] [Shaped fiberglass-reinforced plastic] [Aluminum] [Stainless steel].

2. Special Housing Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

3. Wheel Size (Diameter):  <Insert inches (mm).>

4. Wheel Material:  [Steel] [Aluminum] [One-piece fiberglass-reinforced plastic] [Stainless steel].

5. Special Wheel Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

6. Airflow:  <Insert cfm (L/s).>

7. Static Pressure:  <Insert inches wg (Pa).>

8. Class:  [I] [II] [III].

9. Brake Horsepower:  <Insert value.>

10. Drive Type:  [Belt] [Direct].

11. Fan Rpm:  <Insert value.>

12. Outlet Velocity:  <Insert fpm (m/s).>

13. Motor Size:  <Insert value> hp.

14. Motor Rpm:  <Insert value.>

15. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Minimum Circuit Ampacity:  <Insert value.>

e. Maximum Overcurrent Protection:  <Insert value.>

16. Discharge Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

17. Inlet Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

18. Vibration Isolators:  [Spring isolators] [Restrained spring isolators] <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

19. Spark Arrestance Class:  [A] [B] [C].

2.3 FORWARD-CURVED CENTRIFUGAL FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. ABB Fan Group North America.

2. Acme Engineering & Mfg. Corp.

3. Aerovent; a Twin City Fan Company.

4. Airmaster Fan Co.

5. Ammerman; General Resource Corp.

6. Bayley Fans; a division of Lau Industries, Inc.

7. Carrier Corporation.

8. Central Blower Corporation.

9. Chicago Blower Corporation.

10. Cincinnati Fan.

11. CML Northern Blower Inc.

12. Howden Fan Co.

13. Industrial Air; a division of Lau Industries, Inc.

14. Loren Cook Company.

15. Madison Manufacturing.

16. New Philadelphia Fan Co.

17. New York Blower Company (The).

18. Trane.

19. <Insert manufacturer's name.>

D. Description:  Factory-fabricated, -assembled, -tested, and -finished, belt-driven centrifugal fans consisting of housing, wheel, fan shaft, bearings, motor [and disconnect switch], drive assembly, and support structure.

E. Housings:  Formed panels to make curved-scroll housings with shaped cutoff; with doors or panels to allow access to internal parts and components.

1. Panel Bracing:  Steel angle- or channel-iron member supports for mounting and supporting fan scroll, wheel, motor, and accessories.

Split housings are an optional configuration.

2. Horizontally split, bolted-flange housing.

3. Spun inlet cone with flange.

4. Outlet flange.

F. Forward-Curved Wheels:  Black-enameled or galvanized steel construction with inlet flange, backplate, shallow blades with inlet and tip curved forward in direction of airflow, mechanically secured to flange and backplate; cast-steel hub swaged to backplate and fastened to shaft with set screws.

G. Shafts:  Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with final alignment and belt adjustment made after installation.

1. Turned, ground, and polished hot-rolled steel with keyway.  Ship with protective coating of lubricating oil.

2. Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

Retain one of first three paragraphs and associated subparagraphs below or retain all appropriate types and indicate types in equipment schedule.  Verify availability with manufacturers; other bearing types may be available.

H. Prelubricated and Sealed Shaft Bearings:  Self-aligning, pillow-block-type ball bearings.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

I. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, tapered roller bearings with double-locking collars and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

J. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, ball or roller bearings with adapter mount and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

K. Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  [1.5] [1.4] [1.3] [1.2].

2. Fan Pulleys:  Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is designer's choice.

3. Motor Pulleys:  Adjustable pitch for use with motors through [5] <Insert number> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

4. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

5. Belt Guards:  Fabricate to comply with OSHA and SMACNA requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated.  Secure to fan or fan supports without short circuiting vibration isolation.  Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

6. Motor Mount:  Adjustable for belt tensioning.

L. Accessories:

Retain applicable subparagraphs below.  Verify availability with manufacturers.

1. Scroll Access Doors:  Shaped to conform to scroll, with quick-opening latches and gaskets.

2. Cleanout Door:  [Bolted] [Quick-opening, latch-type] gasketed door allowing access to fan scroll, of same material as housing.

3. Scroll Drain Connection:  NPS 1 (DN 25) steel pipe coupling welded to low point of fan scroll.

4. Companion Flanges:  Rolled flanges for duct connections of same material as housing.

5. Variable Inlet Vanes:  With blades supported at both ends with two permanently lubricated bearings of same material as housing.  Variable mechanism terminating in single control lever with control shaft for double-width fans.

6. Discharge Dampers:  Assembly with [parallel] [opposed] blades constructed of two plates formed around and to shaft, channel frame, and sealed ball bearings; with blades linked outside of airstream to single control lever of same material as housing.

7. Inlet Screens:  Grid screen of same material as housing.

8. Shaft Cooler:  Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

9. Spark-Resistant Construction:  AMCA 99.

10. Shaft Seals:  Airtight seals installed around shaft on drive side of single-width fans.

11. Weather Cover:  Enameled-steel sheet with ventilation slots, bolted to housing.

M. Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."  If different characteristics are required, add subparagraphs to suit Project.

Retain subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type:  Totally enclosed, fan cooled.

If Project has more than one type or configuration of centrifugal fan, delete paragraph and subparagraphs below and schedule fans on Drawings.

N. Capacities And Characteristics:

1. Housing Material:  [Reinforced steel] [Shaped fiberglass-reinforced plastic] [Aluminum] [Stainless steel].

2. Special Housing Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

3. Wheel Size (Diameter):  <Insert inches (mm).>

4. Wheel Material:  [Steel] [Galvanized steel].

5. Special Wheel Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

6. Airflow:  <Insert cfm (L/s).>

7. Static Pressure:  <Insert inches wg (Pa).>

8. Class:  [I] [II] [III].

9. Brake Horsepower:  <Insert value.>

10. Drive Type:  [Belt] [Direct].

11. Fan Rpm:  <Insert value.>

12. Outlet Velocity:  <Insert fpm (m/s).>

13. Motor Size:  <Insert value> hp.

14. Motor Rpm:  <Insert value.>

15. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Minimum Circuit Ampacity:  <Insert value.>

e. Maximum Overcurrent Protection:  <Insert value.>

16. Discharge Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

17. Inlet Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

18. Vibration Isolators:  [Spring isolators] [Restrained spring isolators] <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

19. Spark Arrestance Class:  [A] [B] [C].

2.4 PLENUM FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. ABB Fan Group North America.

2. Acme Engineering & Mfg. Corp.

3. Aerovent; a Twin City Fan Company.

4. Airmaster Fan Co.

5. Ammerman; General Resource Corp.

6. Bayley Fans; a division of Lau Industries, Inc.

7. Carrier Corporation.

8. Central Blower Company.

9. Chicago Blower Corporation.

10. Cincinnati Fan.

11. CML Northern Blower Inc.

12. Howden Fan Co.

13. Industrial Air; a division of Lau Industries, Inc.

14. Loren Cook Company.

15. Madison Manufacturing.

16. New Philadelphia Fan Co.

17. New York Blower Company (The).

18. Trane.

19. <Insert manufacturer's name.>

D. Description:  Factory-fabricated, -assembled, -tested, and -finished, belt-driven centrifugal fans consisting of wheel, fan shaft, bearings, motor [and disconnect switch], drive assembly, and support structure.

E. Airfoil Wheels:  Single-width-single-inlet construction with smooth-curved inlet flange; heavy backplate; hollow die-formed, airfoil-shaped blades continuously welded at tip flange and backplate;[ and] cast-iron or cast-steel hub riveted to backplate and fastened to shaft with set screws[; and special coating].

F. Shafts:  Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with final alignment and belt adjustment made after installation.

1. Turned, ground, and polished hot-rolled steel with keyway.  Ship with protective coating of lubricating oil.

2. Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

Retain one of first three paragraphs and associated subparagraphs below or retain all appropriate types and indicate types in equipment schedule.  Verify availability with manufacturers; other bearing types may be available.

G. Prelubricated and Sealed Shaft Bearings:  Self-aligning, pillow-block-type ball bearings.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

H. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, tapered roller bearings with double-locking collars and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

I. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, ball or roller bearings with adapter mount and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

J. Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  [1.5] [1.4] [1.3] [1.2].

2. Fan Pulleys:  Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is designer's choice.

3. Motor Pulleys:  Adjustable pitch for use with motors through [5] <Insert number> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

4. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

5. Belt Guards:  Fabricate to comply with OSHA and SMACNA requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated.  Secure to fan or fan supports without short circuiting vibration isolation.  Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

6. Motor Mount:  Adjustable for belt tensioning.

K. Accessories:

Retain applicable subparagraphs below.  Verify availability with manufacturers.

1. Shaft Cooler:  Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

2. Spark-Resistant Construction:  AMCA 99.

3. Shaft Seals:  Airtight seals installed around shaft on drive side of single-width fans.

L. Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."  If different characteristics are required, add subparagraphs to suit Project.

Retain subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type:  Totally enclosed, fan cooled.

If Project has more than one type or configuration of plenum fan, delete paragraph and subparagraphs below and schedule fans on Drawings.

M. Capacities And Characteristics:

1. Wheel Size (Diameter):  <Insert inches (mm).>

2. Wheel Material:  [Steel] [Aluminum] [One-piece fiberglass-reinforced plastic] [Stainless steel].

3. Special Wheel Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

4. Airflow:  <Insert cfm (L/s).>

5. Static Pressure:  <Insert inches wg (Pa).>

6. Class:  [I] [II] [III].

7. Brake Horsepower:  <Insert value.>

8. Drive Type:  [Belt] [Direct].

9. Fan Rpm:  <Insert value.>

10. Outlet Velocity:  <Insert fpm (m/s).>

11. Motor Size:  <Insert value> hp.

12. Motor Rpm:  <Insert value.>

13. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Minimum Circuit Ampacity:  <Insert value.>

e. Maximum Overcurrent Protection:  <Insert value.>

14. Discharge Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

15. Inlet Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

16. Vibration Isolators:  [Spring isolators] [Restrained spring isolators] <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

17. Spark Arrestance Class:  [A] [B] [C].

2.5 PLUG FANS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. ABB Fan Group North America.

2. Acme Engineering & Mfg. Corp.

3. Aerovent; a Twin City Fan Company.

4. Airmaster Fan Co.

5. Ammerman; General Resource Corp.

6. Bayley Fans; a division of Lau Industries, Inc.

7. Carrier Corporation.

8. Central Blower Company.

9. Chicago Blower Corporation.

10. Cincinnati Fan.

11. CML Northern Blower Inc.

12. Howden Fan Co.

13. Industrial Air; a division of Lau Industries, Inc.

14. Loren Cook Company.

15. Madison Manufacturing.

16. New Philadelphia Fan Co.

17. New York Blower Company (The).

18. Trane.

19. <Insert manufacturer's name.>

D. Description:  Factory-fabricated, -assembled, -tested, and -finished, belt-driven centrifugal fans consisting of wheel, fan shaft, bearings, motor [and disconnect switch], drive assembly, and support structure.

E. Airfoil Wheels:  Single-width-single-inlet construction with smooth-curved inlet flange; heavy backplate; hollow die-formed, airfoil-shaped blades continuously welded at tip flange and backplate;[ and] cast-iron or cast-steel hub riveted to backplate and fastened to shaft with set screws[; and special coating].

F. Shafts:  Statically and dynamically balanced and selected for continuous operation at maximum rated fan speed and motor horsepower, with final alignment and belt adjustment made after installation.

1. Turned, ground, and polished hot-rolled steel with keyway.  Ship with protective coating of lubricating oil.

2. Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

Retain one of first three paragraphs and associated subparagraphs below or retain all appropriate types and indicate types in equipment schedule.  Verify availability with manufacturers; other bearing types may be available.

G. Prelubricated and Sealed Shaft Bearings:  Self-aligning, pillow-block-type ball bearings.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

H. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, tapered roller bearings with double-locking collars and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

I. Grease-Lubricated Shaft Bearings:  Self-aligning, pillow-block-type, ball or roller bearings with adapter mount and two-piece, cast-iron housing.

Retain and edit one of two subparagraphs below.  Common bearing life typically provided by manufacturers is either 50,000 or 120,000 hours.

1. Ball-Bearing Rating Life:  ABMA 9, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

2. Roller-Bearing Rating Life:  ABMA 11, Ll0 at [50,000 hours] [120,000 hours] <Insert hours>.

J. Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size:  [1.5] [1.4] [1.3] [1.2].

2. Fan Pulleys:  Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is designer's choice.

3. Motor Pulleys:  Adjustable pitch for use with motors through [5] <Insert number> hp; fixed pitch for use with larger motors.  Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

4. Belts:  Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

5. Belt Guards:  Fabricate to comply with OSHA and SMACNA requirements of diamond-mesh wire screen welded to steel angle frame or equivalent, prime coated.  Secure to fan or fan supports without short circuiting vibration isolation.  Include provisions for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

6. Motor Mount:  Adjustable for belt tensioning.

K. Accessories:

Retain applicable subparagraphs below.  Verify availability with manufacturers.

1. Shaft Cooler:  Metal disk between bearings and fan wheel, designed to dissipate heat from shaft.

2. Spark-Resistant Construction:  AMCA 99.

3. Shaft Seals:  Airtight seals installed around shaft on drive side of single-width fans.

L. Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."  If different characteristics are required, add subparagraphs to suit Project.

Retain subparagraph below if enclosure is not open-dripproof type.

1. Enclosure Type:  Totally enclosed, fan cooled.

If Project has more than one type or configuration of plug fan, delete paragraph and subparagraphs below and schedule fans on Drawings.

M. Capacities And Characteristics:

1. Wheel Size (Diameter):  <Insert inches (mm).>

2. Wheel Material:  [Steel] [Aluminum] [One-piece fiberglass-reinforced plastic] [Stainless steel].

3. Special Wheel Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

4. Airflow:  <Insert cfm (L/s).>

5. Static Pressure:  <Insert inches wg (Pa).>

6. Class:  [I] [II] [III].

7. Brake Horsepower:  <Insert value.>

8. Drive Type:  [Belt Drive] [Direct].

9. Fan Rpm:  <Insert value.>

10. Outlet Velocity:  <Insert fpm (m/s).>

11. Motor Size:  <Insert value> hp.

12. Motor Rpm:  <Insert value.>

13. Electrical Characteristics:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Minimum Circuit Ampacity:  <Insert value.>

e. Maximum Overcurrent Protection:  <Insert value.>

14. Discharge Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

15. Inlet Sound Power:

a. 1st Octave:  <Insert dB.>

b. 2nd Octave:  <Insert dB.>

c. 3rd Octave:  <Insert dB.>

d. 4th Octave:  <Insert dB.>

e. 5th Octave:  <Insert dB.>

f. 6th Octave:  <Insert dB.>

g. 7th Octave:  <Insert dB.>

h. 8th Octave:  <Insert dB.>

16. Vibration Isolators:  [Spring isolators] [Restrained spring isolators] <Insert type> having a static deflection of [1 inch (25 mm)] <Insert deflection>.

17. Spark Arrestance Class:  [A] [B] [C].

2.6 SOURCE QUALITY CONTROL

Sound-power rating information may only be available from manufacturers on request.  Refer to discussion on sound and vibration control in the Evaluations.

A. Sound-Power Level Ratings:  Comply with AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data."  Factory test fans according to AMCA 300, "Reverberant Room Method for Sound Testing of Fans."  Label fans with the AMCA-Certified Ratings Seal.

B. Fan Performance Ratings:  Establish flow rate, pressure, power, air density, speed of rotation, and efficiency by factory tests and ratings according to AMCA 210, "Laboratory Methods of Testing Fans for Rating."

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install centrifugal fans level and plumb.

Retain and edit three paragraphs and associated subparagraph below for floor-mounting units; delete if vibration and seismic controls are specified in Part 2 "Capacities and Characteristics" paragraphs or are indicated on Drawings.  If not scheduled, identify required vibration- and seismic-control device by using the titles of devices described in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" and identify its required static deflection.

B. Support floor-mounting units using [spring isolators] [restrained spring isolators] <Insert device> having a static deflection of [1 inch (25 mm)] <Insert deflection>.  Vibration- and seismic-control devices are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Secure vibration and seismic controls to concrete bases using anchor bolts cast in concrete base.

C. Install floor-mounting units on concrete bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03 Section "Cast-in-Place Concrete."

Retain paragraph above for projects not in seismic areas; retain paragraph below for projects in seismic areas.

D. Install floor-mounting units on concrete bases designed to withstand, without damage to equipment, the seismic force required by authorities having jurisdiction.  Concrete, reinforcement, and formwork requirements are specified in Division 03 Section "Cast-in-Place Concrete."

Retain and edit first paragraph below for suspended units; delete if vibration and seismic controls are specified in Part 2 "Capacities and Characteristics" paragraphs or are indicated on Drawings.  If not scheduled, identify required vibration- and seismic-control device by using the titles of devices described in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" and identify its required static deflection.

E. Support suspended units from structure using threaded steel rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stops] <Insert device> having a static deflection of [1 inch (25 mm)] <Insert deflection>.  Vibration-control devices are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

F. Install units with clearances for service and maintenance.

G. Label fans according to requirements specified in Division 23 Section "Identification for HVAC Piping and Equipment."

3.2 CONNECTIONS

Coordinate duct installations and specialty arrangements with schematics on Drawings and with requirements specified in duct systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Duct installation and connection requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of ducts and duct accessories.  Make final duct connections with flexible connectors.  Flexible connectors are specified in Division 23 Section "Air Duct Accessories."

B. Install ducts adjacent to fans to allow service and maintenance.

Retain first paragraph below if fans have scroll drains.

C. Install line-sized piping from scroll drain connection, with trap with seal equal to 1.5 times specified static pressure, to nearest floor drain.

D. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

E. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. Verify that shipping, blocking, and bracing are removed.

2. Verify that unit is secure on mountings and supporting devices and that connections to ducts and electrical components are complete.  Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

3. Verify that cleaning and adjusting are complete.

4. Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation.  Reconnect fan drive system, align and adjust belts, and install belt guards.

5. Adjust belt tension.

6. Adjust damper linkages for proper damper operation.

7. Verify lubrication for bearings and other moving parts.

8. Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in fully open position.

9. Refer to Division 23 Section "Testing, Adjusting, and Balancing for HVAC" for testing, adjusting, and balancing procedures.

10. Remove and replace malfunctioning units and retest as specified above.

B. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain centrifugal fans.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 233416

	CENTRIFUGAL HVAC FANS
	233416 - 1



