Copyright 2000 and 2005 AIA
MASTERSPEC Full Length
12/00 (R 06/06)

Copyright 2000 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233600 - AIR TERMINAL UNITS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Bypass single-duct air terminal units

2. Dual-duct air terminal units.

3. Fan-powered air terminal units.

4. Induction air terminal units.

5. Shutoff single-duct air terminal units.

6. Integral-diffuser air terminal units.

1.3 SUBMITTALS

A. Product Data:  For each type of product indicated, include rated capacities, furnished specialties, sound-power ratings, and accessories.

B. LEED Submittal:

1. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

C. Shop Drawings:  Detail equipment assemblies and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field connection.

1. Include a schedule showing unique model designation, room location, model number, size, and accessories furnished.

Retain subparagraph below if equipment includes wiring.

2. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Ceiling suspension assembly members.

2. Method of attaching hangers to building structure.

3. Size and location of initial access modules for acoustical tile.

4. Ceiling-mounted items including lighting fixtures, diffusers, grilles, speakers, sprinklers, access panels, and special moldings.

E. Operation and Maintenance Data:  For air terminal units to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

1. Instructions for resetting minimum and maximum air volumes.

2. Instructions for adjusting software set points.

1.4 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 01 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of air terminal units and are based on the specific system indicated.  Refer to Division 01 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate filtration, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

C. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

D. NFPA Compliance:  Install air terminal units according to NFPA 90A, "Standard for the Installation of Air Conditioning and Ventilating Systems."

1.5 COORDINATION

Edit this Article to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of air terminal units and suspension system with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, and partition assemblies.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 BYPASS SINGLE-DUCT AIR TERMINAL UNITS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Carnes.

2. Krueger.

3. METALAIRE, Inc.; Metal Industries Inc.

4. Nailor Industries of Texas Inc.

5. Price Industries.

6. Titus.

7. <Insert manufacturer's name.>

B. Configuration:  Diverting-damper assembly inside unit casing with control components located inside a protective metal shroud.

C. Casing:  0.034-inch (0.85-mm) steel.

1. Casing Lining:  1/2-inch- (13-mm-) thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.

2. Air Inlet:  Round stub connection for duct attachment.

3. Air Outlet:  S-slip and drive connections.

4. Access:  Removable panels for access to diverter and other parts requiring service, adjustment, or maintenance; with airtight gasket.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

5. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain paragraph below for units with mechanical volume regulators.

D. Diverter Assembly:  [Galvanized-steel gate, with polyethylene linear bearings] [Aluminum blade, with nylon-fitted pivot points].

Retain paragraph below for multioutlet section, or indicate number of outlets and outlet sizes on Drawings or in a schedule.

E. Multioutlet Attenuator Section:  With [two] [three] [four] <Insert number> [6-inch- (150-mm-)] [8-inch- (200-mm-)] [10-inch- (250-mm-)] diameter collars; each with locking butterfly balancing damper.

If heating coil is required, retain one of two paragraphs and associated subparagraphs below.

F. Hot-Water Heating Coil:  Copper tube, mechanically expanded into aluminum-plate fins; leak tested underwater to 200 psig (1380 kPa); and factory installed.

G. Electric Heating Coil:  Slip-in-type, open-coil design with integral control box factory wired and installed.  Include the following features:

1. Primary and secondary overtemperature protection.

Retain applicable subparagraphs below.

2. Nickel chrome 80/20 heating elements.

3. Airflow switch.

4. Noninterlocking disconnect switch.

5. Fuses (for coils more than 48 A).

6. Mercury contactors.

7. Pneumatic-electric switches and relays.

8. Magnetic contactor for each step of control (for three-phase coils).

Retain one of two paragraphs and associated subparagraphs below.

H. Electric Controls:  Damper actuator and thermostat.

1. Damper Actuator:  24 V, powered closed, powered open[ with microswitch to energize heating control circuit].

2. Thermostat:  Wall-mounting electric type with temperature display in Fahrenheit and Celsius, and space temperature set point.

Retain subparagraph below for heating-cooling changeover.

3. Changeover Thermostat:  Duct-mounting, electric type reverses action of controls when duct temperature rises 70 deg F (21 deg C).

I. Electronic Controls:  Bidirectional damper operator and microprocessor-based thermostat.

1. Damper Actuator:  24 V, powered closed, powered open.

2. Thermostat:  Wall-mounting electronic type with the following features:

Retain applicable subparagraphs below.

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Temperature set-point display in Fahrenheit and Celsius.

d. Auxiliary switch shall energize heating control circuit.

e. Changeover thermistor shall reverse action.

2.3 DUAL-DUCT AIR TERMINAL UNITS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Anemostat; a Mestek Company.

2. Carnes.

3. Krueger.

4. METALAIRE, Inc.; Metal Industries Inc.

5. Nailor Industries of Texas Inc.

6. Price Industries.

7. Titus.

8. Trane Co. (The); Worldwide Applied Systems Group.

9. Tuttle & Bailey.

10. <Insert manufacturer's name.>

B. Configuration:  Two volume dampers inside unit casing with mixing attenuator section and control components located inside a protective metal shroud.

C. Casing:  [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum].

Retain one of two optional sentences in subparagraph below or delete both.

1. Casing Lining:  [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.[ Cover liner with nonporous foil.][ Cover liner with nonporous foil and perforated metal.]

Retain standard lining in subparagraph above or alternative lining in first subparagraph below; below is for medical-facility and clean-room applications.

2. Casing Lining:  Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

3. Air Inlets:  Round stub connections or S-slip and drive connections for duct attachment.

4. Air Outlet:  S-slip and drive connections.

5. Access:  Removable panels for access to dampers and other parts requiring service, adjustment, or maintenance; with airtight gasket.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

6. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

D. Volume Damper:  Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates vary among manufacturers and with pressure rating.  Edit subparagraph below to suit Project.

1. Maximum Damper Leakage:  ARI 880 rated, 3 percent of nominal airflow at [3-inch wg (750-Pa)] [6-inch wg (1500-Pa)] inlet static pressure.

Select one of two subparagraphs below.

2. Damper Position, Hot Deck:  Normally [open] [closed].

3. Damper Position, Cold Deck:  Normally [closed] [open].

E. Attenuator Section:  [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum] sheet metal.

Retain one of two optional sentences in subparagraph below or delete both.

1. Lining: [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.[ Cover liner with nonporous foil.][ Cover liner with nonporous foil and perforated metal.]

Retain standard lining in subparagraph above or alternative lining in subparagraph below; below is for medical-facility and clean-room applications.

2. Lining:  Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain paragraph below for multioutlet section, or indicate number of outlets and outlet sizes on Drawings or in a schedule.

F. Multioutlet Attenuator Section:  With [two] [three] [four] <Insert number> [6-inch- (150-mm-)] [8-inch- (200-mm-)] [10-inch- (250-mm-)] [12-inch- (300-mm-)] diameter collars; each with locking butterfly balancing damper.

Retain one of first four paragraphs and associated subparagraphs below.

G. Pneumatic Controls:  Damper operator, velocity controllers, and thermostat shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC."

1. Pneumatic Damper Operator:  [8- to 13-psig (55- to 90-kPa)] [3- to 13-psig (21- to 90-kPa)] spring range.

2. Velocity Controllers:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor.  Locate velocity sensors in cold-deck air inlet and air outlet.

3. Thermostat:  Wall-mounting pneumatic type with appropriate mounting hardware.

H. Electronic Controls:  Bidirectional damper operator and microprocessor-based thermostat with integral airflow transducer and room sensor shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC." and shall have the following features:

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Velocity Controller:  Factory calibrated to minimum and maximum air volumes, field adjustable at thermostat; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor.  Locate velocity sensors in cold-deck air inlet and air outlet.

3. Thermostat:  Wall-mounting electronic type with the following features:

Retain applicable subparagraphs below.

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Temperature set-point display in Fahrenheit and Celsius.

I. DDC Controls:  Single-package unitary controller and actuator specified in Division 23 Section "Instrumentation and Control for HVAC."

Select paragraph above when control components are specified with the control system; select first paragraph and subparagraphs below when control components are packaged with the equipment.

J. DDC Controls:  Bidirectional damper operators and microprocessor-based controller and room sensor shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC." and shall have the following features:

1. Damper Actuators:  24 V, powered closed, [spring return open] [powered open].

2. Velocity Sensors:  Multipoint array with velocity sensors in cold- and hot-deck air inlet and air outlet.

3. Terminal Unit Controller:  Pressure independent, [variable-air] [constant]-volume controller with electronic airflow transducers factory calibrated to minimum and maximum air volumes, and having the following features:

Retain applicable subparagraphs below.

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Occupied and unoccupied operating mode.

d. Remote reset of airflow or temperature set points.

e. Adjusting and monitoring with portable terminal.

f. Communication with temperature-control system specified in Division 23 Section "Instrumentation and Control for HVAC."

4. Room Sensor:  Wall mounting, with temperature set-point adjustment and access for connection of portable operator terminal.

K. Control Sequence:

1. Modulate cold-air damper to maintain room temperature.

2. Modulate warm-air damper to maintain constant airflow.

2.4 FAN-POWERED AIR TERMINAL UNITS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Anemostat; a Mestek Company.

2. Carnes.

3. Environmental Technologies, Inc.; Enviro-Air Div.

4. Krueger.

5. METALAIRE, Inc.; Metal Industries Inc.

6. Nailor Industries of Texas Inc.

7. Price Industries.

8. Titus.

9. Trane Co. (The); Worldwide Applied Systems Group.

10. Tuttle & Bailey.

11. <Insert manufacturer's name.>

B. Configuration:  Volume-damper assembly and fan in series or in parallel arrangement, as indicated on Drawings, inside unit casing with control components inside a protective metal shroud.

C. Casing:  [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum].

Retain one of two optional sentences in subparagraph below or delete both.

1. Casing Lining:  [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.[ Cover liner with nonporous foil.][ Cover liner with nonporous foil and perforated metal.]

Retain standard lining in subparagraph above or alternative lining in first subparagraph below; below is for medical-facility and clean-room applications.

2. Casing Lining:  Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

3. Air Inlets:  Round stub connections or S-slip and drive connections for duct attachment.

4. Air Outlet:  S-slip and drive connections.

5. Access:  Removable panels for access to dampers and other parts requiring service, adjustment, or maintenance; with airtight gasket and quarter-turn latches.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

6. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

D. Volume Damper:  Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates vary among manufacturers and with pressure rating.  Edit first subparagraph below to suit Project.

1. Maximum Damper Leakage:  ARI 880 rated, [2] [3] percent of nominal airflow at [3-inch wg (750-Pa)] [6-inch wg (1500-Pa)] inlet static pressure.

2. Damper Position:  Normally [open] [closed].

E. Fan Section:  Galvanized-steel plenum, with direct-drive, forward-curved fan with air filter and backdraft damper.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motor:  [Multispeed] <Insert other type>.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

a. Speed Control:  Infinitely adjustable with pneumatic-electric and electronic controls.

b. Fan-Motor Assembly Isolation:  Rubber isolators.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

2. Air Filter:  [2-inch- (50-mm-)] [1-inch- (25-mm-)] thick, [fiberglass throwaway,] MERV [6] [7] according to ASHRAE 52.2.

F. Attenuator Section:  [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum] sheet metal.

Retain one of two optional sentences in subparagraph below or delete both.

1. Lining:  [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.[ Cover liner with nonporous foil.][ Cover liner with nonporous foil and perforated metal.]

Retain standard lining in subparagraph above or alternative lining in subparagraph below; below is for medical-facility and clean-room applications.

2. Lining:  Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

If heating coil is required, retain one of two paragraphs and associated subparagraphs below.

G. Hot-Water Heating Coil:  Copper tube, mechanically expanded into aluminum-plate fins; leak tested underwater to 200 psig (1380 kPa); and factory installed.

H. Electric Heating Coil:  Slip-in-type, open-coil design with integral control box factory wired and installed.  Include the following features:

1. Primary and secondary overtemperature protection.

Retain applicable subparagraphs below.

2. Nickel chrome 80/20 heating elements.

3. Fan interlock contacts.

4. Noninterlocking disconnect switch.

5. Fuses (for coils more than 48 A).

6. Mercury contactors.

7. Pneumatic-electric switches and relays.

8. Magnetic contactor for each step of control (for three-phase coils).

I. Factory-Mounted and -Wired Controls:  Electrical components shall be mounted in control box with removable cover.  Incorporate single-point electrical connection to power source.

1. Control Transformer:  Factory mounted for control voltage on electric and electronic control units with terminal strip in control box for field wiring of thermostat and power source.

2. Wiring Terminations:  Fan and controls to terminal strip, and terminal lugs shall match quantities, sizes, and materials of branch-circuit conductors.  Enclose terminal lugs in terminal box that is sized according to NFPA 70.

3. Disconnect Switch:  Factory-mounted, fused type.

J. Control Panel Enclosure:  NEMA 250, Type 1, with access panel sealed from airflow and mounted on side of unit.

Retain one of first three paragraphs and associated subparagraphs below.

K. Electric Controls:  24-V damper actuator with wall-mounting electric thermostat and appropriate mounting hardware.

L. Pneumatic Controls:  Damper operator, velocity controller, and thermostat shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC."

1. Pneumatic Damper Operator:  [8- to 13-psig (55- to 90-kPa)] [3- to 13-psig (21- to 90-kPa)] spring range.

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat:  Wall-mounting pneumatic type with appropriate mounting hardware.

M. Electronic Controls:  Bidirectional damper operator and microprocessor-based controller with integral airflow transducer and room sensor shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC" and shall have the following features:

Retain applicable subparagraphs below.

1. Proportional, plus integral control of room temperature.

2. Time-proportional reheat-coil control.

3. Occupied and unoccupied operating mode.

4. Remote reset of airflow or temperature set points.

5. Adjusting and monitoring with portable terminal.

6. Communication with temperature-control system specified in Division 23 Section "Instrumentation and Control for HVAC."

N. Control Sequence:

Retain first two subparagraphs and associated subparagraphs below for electronic controls.  Retain third and fourth subparagraphs and associated subparagraphs for pneumatic-electric controls.

1. With central system fan operating in occupied mode, sequence the controls as follows:

a. When primary duct is pressurized, modulate volume damper to maintain room temperature.

b. On reduced-cooling demand, close volume damper.  At a field-adjustable point, air terminal fan is energized.

c. As cooling demand increases, increase air terminal fan speed.

d. If central duct system pressure varies, modulate volume damper to maintain constant primary airflow.

e. If no cooling or heating demand, control enters field-adjustable, no-load band.

f. On heating demand, energize heating coil.

2. With central system fan operating in unoccupied mode, sequence the controls as follows:

a. On heating demand, energize air terminal unit fan and heating coil.

b. Maintain field-adjustable setback temperature.

c. Close volume damper.

3. With central system fan operating in occupied mode, sequence the controls as follows:

a. On cooling demand, modulate volume damper to proportion airflow from central system.

b. On reduced-cooling demand, close volume damper.  Pneumatic-electric or damper-position switch energizes fan.

c. Speed control adjusts air terminal fan speed to match downstream resistance.

d. On heating demand, energize heating coil.

4. With central system fan operating in unoccupied mode, sequence the controls as follows:

a. Cycle air terminal fan to maintain room temperature.

2.5 INDUCTION AIR TERMINAL UNITS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Price Industries.

2. Tuttle & Bailey.

3. <Insert manufacturer's name.>

B. Configuration:  Volume-damper assembly inside unit casing with mechanical induction damper mounted on casing and control components located inside a protective metal shroud.

C. Casing:  [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum].

1. Casing Lining:  [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.

2. Air Inlet:  Round stub connection for duct attachment.

3. Air Outlet:  S-slip and drive connections[, size matching inlet size].

4. Access:  Removable panels for access to dampers and other parts requiring service, adjustment, or maintenance; with airtight gasket.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

5. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

D. Volume Damper:  Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates vary among manufacturers and with pressure rating.  Edit first subparagraph below to suit Project.

1. Maximum Damper Leakage:  ARI 880 rated, [2] [3] percent of nominal airflow at [3-inch wg (750-Pa)] [6-inch wg (1500-Pa)] inlet static pressure.

2. Damper Position:  Normally [open] [closed].

E. Induction Damper:  Galvanized-steel, multiblade assembly with self-lubricating bearings.

If heating coil is required, retain one of two paragraphs and associated subparagraphs below.

F. Hot-Water Heating Coil:  Copper tube, mechanically expanded into aluminum-plate fins; leak tested underwater to 200 psig (1380 kPa); and factory installed.

G. Electric Heating Coil:  Slip-in-type, open-coil design with integral control box factory wired and installed.  Include the following features:

1. Primary and secondary overtemperature protection.

Retain applicable subparagraphs below.

2. Nickel chrome 80/20 heating elements.

3. Airflow switch.

4. Noninterlocking disconnect switch.

5. Fuses (for coils more than 48 A).

6. Mercury contactors.

7. Pneumatic-electric switches and relays.

8. Magnetic contactor for each step of control (for three-phase coils).

Retain one of two paragraphs and associated subparagraphs below.

H. Pneumatic Controls:  Damper operator, velocity controller, induction damper operator, and thermostat shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC."

1. Damper Operator:  Pneumatic, 5- to 10-psig (35- to 70-kPa) spring range.

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Induction Damper Operator:  Pneumatic, spring range matching reset range of controller.

4. Thermostat:  Wall-mounting pneumatic type with appropriate mounting hardware.

I. Electronic Controls:  Pneumatic damper operators, electronic controller integral airflow transducer, and electronic thermostat with the following features:

1. Damper Actuator:  Pneumatic, 5- to 10-psig (35- to 70-kPa) spring range.

2. Velocity Controller:  Factory calibrated and field adjustable at thermostat to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Induction Damper Operator:  Pneumatic, spring range matching reset range of controller.

4. Thermostat:  Wall-mounting electronic type with the following features:

Retain applicable subparagraphs below.

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Temperature set-point display in Fahrenheit and Celsius.

2.6 SHUTOFF SINGLE-DUCT AIR TERMINAL UNITS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Anemostat; a Mestek Company.

2. Carnes.

3. Environmental Technologies, Inc.; Enviro-Air Div.

4. Krueger.

5. METALAIRE, Inc.; Metal Industries Inc.

6. Nailor Industries of Texas Inc.

7. Phoenix Controls Corporation.

8. Price Industries.

9. Titus.

10. Trane Co. (The); Worldwide Applied Systems Group.

11. Trox USA, Inc.

12. Tuttle & Bailey.

13. Warren Technology.

14. <Insert manufacturer's name.>

B. Configuration:  Volume-damper assembly inside unit casing with control components located inside a protective metal shroud.

C. Casing:  [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum].

Retain one of two optional sentences in subparagraph below or delete both.

1. Casing Lining:  [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.[ Cover liner with nonporous foil.][ Cover liner with nonporous foil and perforated metal.]

Retain standard lining in subparagraph above or alternative lining in first subparagraph below; below is for medical-facility and clean-room applications.

2. Casing Lining:  Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

3. Air Inlet:  Round stub connection or S-slip and drive connections for duct attachment.

4. Air Outlet:  S-slip and drive connections[, size matching inlet size].

5. Access:  Removable panels for access to dampers and other parts requiring service, adjustment, or maintenance; with airtight gasket.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

6. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain one of first two paragraphs and associated subparagraphs below; retain first for units with mechanical volume regulators.

D. Regulator Assembly:  Extruded-aluminum or galvanized-steel components; key damper blades onto shaft with nylon-fitted pivot points located inside unit casing.

1. Automatic Flow-Control Assembly:  Combined spring rates shall be matched for each volume-regulator size with machined dashpot for stable operation.

2. Factory-calibrated and field-adjustable assembly with shaft extension for connection to externally mounted control actuator.

Retain first paragraph below for units with system-air-powered volume regulators.

E. Regulator Assembly:  System-air-powered bellows section incorporating polypropylene bellows for volume regulation and thermostatic control.  Bellows shall operate at temperatures from 0 to 140 deg F (minus 18 to plus 60 deg C); shall be impervious to moisture and fungus; shall be suitable for 10-inch wg (2500-Pa) static pressure; and shall be factory tested for leaks.

F. Volume Damper:  Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates vary among manufacturers and with pressure rating.  Edit first subparagraph below to suit Project.

1. Maximum Damper Leakage:  ARI 880 rated, [2] [3] percent of nominal airflow at [3-inch wg (750-Pa)] [6-inch wg (1500-Pa)] inlet static pressure.

2. Damper Position:  Normally [open] [closed].

G. Attenuator Section:  [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum] sheet metal.

Retain one of two optional sentences in subparagraph below or delete both.

1. Lining:  [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.[ Cover liner with nonporous foil.][ Cover liner with nonporous foil and perforated metal.]

Retain standard lining in subparagraph above or alternative lining in subparagraph below; below is for medical-facility and clean-room applications.

2. Lining:  Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

H. Multioutlet Attenuator Section:  With [two] [three] [four] <Insert number> [6-inch- (150-mm-)] [8-inch- (200-mm-)] [10-inch- (250-mm-)] diameter collars; each with locking butterfly balancing damper.

If heating coil is required, retain one of two paragraphs and associated subparagraphs below.

I. Hot-Water Heating Coil:  Copper tube, mechanically expanded into aluminum-plate fins; leak tested underwater to 200 psig (1380 kPa); and factory installed.

J. Electric Heating Coil:  Slip-in-type, open-coil design with integral control box factory wired and installed.  Include the following features:

1. Primary and secondary overtemperature protection.

Retain applicable subparagraphs below.

2. Nickel chrome 80/20 heating elements.

3. Airflow switch.

4. Noninterlocking disconnect switch.

5. Fuses (for coils more than 48 A).

6. Mercury contactors.

7. Pneumatic-electric switches and relays.

8. Magnetic contactor for each step of control (for three-phase coils).

Retain one of five paragraphs and associated subparagraphs below.

K. Electric Controls:  Damper actuator and thermostat.

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Thermostat:  Wall-mounting electronic type with clock display, temperature display in Fahrenheit and Celsius, and space temperature set point.

L. Pneumatic Controls:  Damper operator, velocity controller, and thermostat shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC."

1. Pneumatic Damper Operator:  [8- to 13-psig (55- to 90-kPa)] [3- to 13-psig (21- to 90-kPa)] spring range.

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat:  Wall-mounting pneumatic type with appropriate mounting hardware.

M. Electronic Controls:  Bidirectional damper operator and microprocessor-based thermostat with integral airflow transducer and room sensor shall be compatible with temperature controls specified in other Division 23 Sections and shall have the following features:

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat:  Wall-mounting electronic type with the following features:

Retain applicable subparagraphs below.

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Temperature set-point display in Fahrenheit and Celsius.

N. DDC Controls:  Single-package unitary controller and actuator specified in Division 23 Section "Instrumentation and Control for HVAC."

Select paragraph above when control components are specified with the control system; select paragraph and subparagraphs below when control components are packaged with the equipment.

O. DDC Controls:  Bidirectional damper operators and microprocessor-based controller and room sensor shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC" and shall have the following features:

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Terminal Unit Controller:  Pressure-independent, variable-air-volume controller with electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes, and having the following features:

Retain applicable subparagraphs below.

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Occupied and unoccupied operating mode.

d. Remote reset of airflow or temperature set points.

e. Adjusting and monitoring with portable terminal.

f. Communication with temperature-control system specified in Division 23 Section "Instrumentation and Control for HVAC."

3. Room Sensor:  Wall mounting, with temperature set-point adjustment and access for connection of portable operator terminal.

Retain below for units with system-powered controls.

P. Control Sequence:

1. Suitable for operation with duct pressures between 0.25- and 3.0-inch wg (60- and 750-Pa) inlet static pressure.

2. Factory-mounted and -piped, 5-micron filter; velocity-resetting, adjustable, high-limit control; and amplifying relay.

3. System-powered, wall-mounting thermostat.

2.7 INTEGRAL-DIFFUSER AIR TERMINAL UNITS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Acutherm.

2. Warren Technology.

3. <Insert manufacturer's name.>

B. Configuration:  Volume-damper assembly inside unit casing with [integral] [attached] [linear-slot] [square-ceiling] [louver-face] [perforated] diffuser.

Retain casing below if appropriate to unit.

C. Casing:  [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum].

1. Casing Lining:  [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071; secured with adhesive.

2. Air Inlet:  Round stub connections for duct attachment.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

3. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

D. Volume Damper:  Galvanized steel with peripheral gasket and self-lubricating bearings.

1. Damper Position:  Normally [open] [closed].

E. Diffuser:  Galvanized-steel insulated plenum with extruded-aluminum or sheet-steel diffuser, having fixed or variable geometry designed to operate from 100 percent to minimum airflow, manual adjustment of airflow direction, and white baked-enamel finish.

Retain one of three paragraphs and associated subparagraphs below.

F. Electric Controls:  Damper actuator and thermostat.

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Thermostat:  Wall-mounting electronic type with clock display, temperature display in Fahrenheit and Celsius, and space temperature set point.

G. Pneumatic Controls:  Damper operator[, velocity controller,] and thermostat shall be compatible with temperature controls specified in Division 23 Section "Instrumentation and Control for HVAC."

1. Pneumatic Damper Operator:  [8- to 13-psig (55- to 90-kPa)] [3- to 13-psig (21- to 90-kPa)] spring range.

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat:  Wall-mounting pneumatic type with appropriate mounting hardware.

H. Electronic Controls:  Bidirectional damper operator and microprocessor-based thermostat with integral airflow transducer and room sensor shall be compatible with temperature controls specified in other Division 23 Sections and shall have the following features:

1. Damper Actuator:  24 V, powered closed, [spring return open] [powered open].

2. Velocity Controller:  Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat:  Wall-mounting electronic type with the following features:

Retain applicable subparagraphs below.

a. Proportional, plus integral control of room temperature.

b. Time-proportional reheat-coil control.

c. Temperature set-point display in Fahrenheit and Celsius.

Retain paragraph and subparagraphs below for units with system-powered controls.

I. Control Sequence:

1. Suitable for operation with duct pressures between 0.25- and 3.0-inch wg (60- and 750-Pa) inlet static pressure.

2. Factory-mounted and -piped, 5-micron filter; velocity-resetting, adjustable, high-limit control; and amplifying relay.

3. System-powered, wall-mounting thermostat.

Retain below for units with self-contained controls.

J. Integral thermally powered actuators, sensing duct and room temperature, control diffusion dampers.

2.8 SOURCE QUALITY CONTROL

A. Identification:  Label each air terminal unit with plan number, nominal airflow, maximum and minimum factory-set airflows, coil type, and ARI certification seal.

B. Verification of Performance:  Rate air terminal units according to ARI 880.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install air terminal units level and plumb.  Maintain sufficient clearance for normal service and maintenance.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to air terminal units to allow service and maintenance.

C. Hot-Water Piping:  In addition to requirements in Division 23 Section "Hydronic Piping," connect heating coils to supply with shutoff valve, strainer, control valve, and union or flange; and to return with balancing valve and union or flange.

D. Connect ducts to air terminal units according to Division 23 Section "[Metal Ducts] [Nonmetal Ducts]."

E. Ground units with electric heating coils according to Division 26 Section "Grounding and Bonding for Electrical Systems."

F. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

G. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. After installing air terminal units and after electrical circuitry has been energized, test for compliance with requirements.

Retain first subparagraph below for air terminal units with hot-water coils.

2. Leak Test:  After installation, fill water coils and test for leaks.  Repair leaks and retest until no leaks exist.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace malfunctioning units and retest as specified above.

3.4 STARTUP SERVICE

Delete this Article if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

1. Complete installation and startup checks according to manufacturer's written instructions and do the following:

a. Verify that inlet duct connections are as recommended by air terminal unit manufacturer to achieve proper performance.

b. Verify that controls and control enclosure are accessible.

c. Verify that control connections are complete.

d. Verify that nameplate and identification tag are visible.

e. Verify that controls respond to inputs as specified.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain air terminal units.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 233600

AIR TERMINAL UNITS
233600 - 1

