Copyright 2001 and 2005 AIA
MASTERSPEC Full Length
09/01 (R 06/06)

Copyright 2001 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233723 - HVAC GRAVITY VENTILATORS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following types of roof-mounting intake and relief ventilators:

Adjust list below to suit Project.

1. Louver penthouses.

2. Roof hoods.

3. Goosenecks.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 08 Section "Louvers and Vents" for ventilator assemblies provided as part of the general construction.

2. Division 23 Section "HVAC Power Ventilators" for roof-mounting exhaust fans.

1.3 PERFORMANCE REQUIREMENTS

A. Structural Performance:  Intake and relief ventilators shall be capable of withstanding the effects of gravity loads, wind loads,[ seismic loads,] and thermal movements without permanent deformation of components, noise or metal fatigue, or permanent damage to fasteners and anchors.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.  ASHRAE 62.1-2004, Section 5.6.2 - "Rain Entrainment," limits amount of water penetration through intake.

B. Water Entrainment:  Limit water penetration through unit to comply with ASHRAE 62.1-2004.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.[ For louvers specified to bear AMCA seal, include printed catalog pages showing specified models with appropriate AMCA Certified Ratings Seals.]

B. LEED Submittal:

1. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

C. Shop Drawings:  For intake and relief ventilators.  Include plans, elevations, sections, details, and ventilator attachments to curbs and curb attachments to roof structure.

D. Coordination Drawings:  Roof framing plans and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

1. Structural members to which roof curbs and ventilators will be attached.

2. Sizes and locations of roof openings.

E. Samples for Verification:  For each type of exposed finish required for intake and relief ventilators.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

F. Welding certificates.

1.5 QUALITY ASSURANCE

A. Source Limitations:  Obtain ventilators through one source from a single manufacturer where indicated to be of same type, design, or factory-applied color finish.

B. Product Options:  Information on Drawings and in Specifications establishes requirements for system's aesthetic effects and performance characteristics.  Aesthetic effects are indicated by dimensions, arrangements, alignment, and profiles of components and assemblies as they relate to sightlines, to one another, and to adjoining construction.  Performance characteristics are indicated by criteria subject to verification by one or more methods including preconstruction testing, field testing, and in-service performance.

Retain paragraph above or below.  Retain below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 01 requirements.

C. Product Options:  Drawings indicate size, profiles, and dimensional requirements of intake and relief ventilators and are based on the specific equipment indicated.  Refer to Division 01 Section "Product Requirements."

Retain subparagraph below with either "Product Options" Paragraph above or revise to suit Project.

1. Do not modify intended aesthetic effects, as judged solely by Architect, except with Architect's approval.  If modifications are proposed, submit comprehensive explanatory data to Architect for review.

Delete paragraph and subparagraphs below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

D. Welding:  Qualify procedures and personnel according to the following:

Retain applicable standards below.

1. AWS D1.2, "Structural Welding Code--Aluminum."

2. AWS D1.3, "Structural Welding Code--Sheet Steel."

1.6 COORDINATION

A. Coordinate installation of roof curbs and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 MATERIALS

Retain materials in this Article required for intake and relief ventilators specified in succeeding articles.

A. Aluminum Extrusions:  ASTM B 221 (ASTM B 221M), Alloy 6063-T5 or T-52.

B. Aluminum Sheet:  ASTM B 209 (ASTM B 209M), Alloy 3003 or 5005 with temper as required for forming or as otherwise recommended by metal producer for required finish.

C. Galvanized-Steel Sheet:  ASTM A 653/A 653M, G90 (Z275) zinc coating, mill phosphatized.

D. Stainless-Steel Sheet:  ASTM A 666, Type 304, with No. [4] [6] finish.

E. Fasteners:  Same basic metal and alloy as fastened metal or 300 Series stainless steel, unless otherwise indicated.  Do not use metals that are incompatible with joined materials.

1. Use types and sizes to suit unit installation conditions.

2. Use [Phillips flat] [hex-head or Phillips pan]-head screws for exposed fasteners, unless otherwise indicated.

F. Post-Installed Fasteners for Concrete and Masonry:  Torque-controlled expansion anchors, made from stainless-steel components, with capability to sustain, without failure, a load equal to 4 times the loads imposed, for concrete, or 6 times the load imposed, for masonry, as determined by testing per ASTM E 488, conducted by a qualified independent testing agency.

G. Bituminous Paint:  Cold-applied asphalt emulsion complying with ASTM D 1187.

2.3 FABRICATION, GENERAL

A. Factory or shop fabricate intake and relief ventilators to minimize field splicing and assembly.  Disassemble units to the minimum extent as necessary for shipping and handling.  Clearly mark units for reassembly and coordinated installation.

B. Fabricate frames, including integral bases, to fit in openings of sizes indicated, with allowances made for fabrication and installation tolerances, adjoining material tolerances, and perimeter sealant joints.

C. Fabricate units with closely fitted joints and exposed connections accurately located and secured.

D. Fabricate supports, anchorages, and accessories required for complete assembly.

E. Perform shop welding by AWS-certified procedures and personnel.

2.4 LOUVER PENTHOUSES

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan company.

3. Carnes.

4. Greenheck.

5. JencoFan.

6. Loren Cook Company.

7. Penn Ventilation.

8. <Insert manufacturer's name.>

Retain roof material option in first paragraph below to match retained frame and blade materials.

B. Construction:  All-welded assembly with [4-inch (100-mm)] [6-inch (150-mm)]-deep louvers, mitered corners, and [aluminum] [galvanized-steel] [stainless-steel] sheet roof.

C. Frame and Blade Material and Nominal Thickness:  Extruded aluminum, of thickness required to comply with structural performance requirements, but not less than 0.080 inch (2.0 mm) for frames and [0.080 inch (2.0 mm)] [0.060 inch (1.5 mm)] for blades.

D. Frame and Blade Material and Nominal Thickness:  Galvanized-steel sheet, of thickness required to comply with structural performance requirements, but not less than 0.052 inch (1.3 mm) for frames and [0.040 inch (1.0 mm)] [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] for blades.

E. Frame and Blade Material and Nominal Thickness:  Stainless-steel sheet, of thickness required to comply with structural performance requirements, but not less than [0.050 inch (1.27 mm)] [0.062 inch (1.57 mm)], with grain running [parallel] [perpendicular] to length of blades and frame members.

Retain and edit five subparagraphs below with any of last three paragraphs retained above.

Retain first two subparagraphs below unless indicated on Drawings.  Verify that louvers are available that comply with requirements below and with performance requirements selected.

1. Blade Spacing:  <Insert dimensions in inches (mm)>.

2. Blade Angle:  <Insert angle in degrees>.

3. Air Performance:  Not more than [0.10-inch wg (25-Pa)] <Insert pressure> static pressure drop at [700-fpm (3.6-m/s)] [750-fpm (3.8-m/s)] [800-fpm (4.1-m/s)] [850-fpm (4.3-m/s)] <Insert velocity> free-area velocity.

Verify availability of seal in subparagraph below for louvers indicated.  See Editing Instruction No. 2 in the Evaluations about certified ratings.  Coordinate with product data requirement in Part 1 "Submittals" Article.

4. AMCA Seal:  Mark units with the AMCA Certified Ratings Seal.

Retain subparagraph below for exterior mitered corners.  If retaining, verify available corner construction with manufacturers selected.

5. Exterior Corners:  Prefabricated corner units with [mitered and welded blades] [mitered blades with concealed close-fitting splices] and with [fully recessed] [semirecessed] mullions at corners.

Retain paragraph and subparagraphs below for roof curbs furnished by penthouse manufacturer for field installation.  Delete if roof curbs are specified in Division 07 Section "Roof Accessories."

F. Roof Curbs:  Galvanized-steel sheet; with mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer.  Size as required to fit roof opening and ventilator base.

1. Configuration:  [Self-flashing without a cant strip, with] [Built-in cant and] [Built-in raised cant and] mounting flange.

Coordinate curb height with roof deck construction; other heights are available.

2. Overall Height:  [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Retain one or both of first two paragraphs below.  If both bird screening and insect screening are required, indicate location of each on Drawings.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.  ASHRAE 62.1-2004, Section 5.6.5 - "Bird Screens" requires that outdoor intakes be equipped with a screening device designed to limit penetration of a 1/2-inch (13-mm) probe.

G. Bird Screening:  [Galvanized-steel, 1/2-inch- (12.7-mm-) square mesh, 0.041-inch (1.04-mm) wire] [Aluminum, 1/2-inch- (12.7-mm-) square mesh, 0.063-inch (1.6-mm) wire] [Flattened, expanded aluminum, 3/4 by 0.050 inch (19 by 1.27 mm) thick] [Stainless-steel, 1/2-inch- (12.7-mm-) square mesh, 0.047-inch (1.19-mm) wire].

H. Insect Screening:  [Aluminum, 18-by-16 (1.4-by-1.6-mm) mesh, 0.012-inch (0.30-mm)] [Stainless-steel, 18-by-18 (1.4-by-1.4-mm) mesh, 0.009-inch (0.23-mm)] wire.

I. Galvanized-Steel Sheet Finish:

1. Surface Preparation:  Clean surfaces of dirt, grease, and other contaminants.  Clean welds, mechanical connections, and abraded areas and repair galvanizing according to ASTM A 780.  Apply a conversion coating suited to the organic coating to be applied over it.

Revise subparagraph below if a specific type of primer or a baked-on application is required.  Coordinate with Division 09 painting Sections.

2. Factory Priming for Field-Painted Finish:  Where field painting after installation is indicated, apply an air-dried primer immediately after cleaning and pretreating.

Subparagraph and associated subparagraph below are examples only.  Revise to suit Project or paint systems available from manufacturers specified.

3. Baked-Enamel Finish:  Immediately after cleaning and pretreating, apply manufacturer's standard finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 1 mil (0.025 mm) for topcoat and an overall minimum dry film thickness of 2 mils (0.05 mm).

a. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

2.5 ROOF HOODS

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan company.

3. Carnes.

4. Greenheck.

5. JencoFan.

6. Loren Cook Company.

7. Penn Ventilation.

8. <Insert manufacturer's name.>

B. Factory or shop fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figures 5-6 and 5-7.

C. Materials:  [Galvanized-steel sheet, minimum 0.064-inch- (1.62-mm-) thick base and 0.040-inch- (1.0-mm-) thick hood] [Aluminum sheet, minimum 0.063-inch- (1.6-mm-) thick base and 0.050-inch- (1.27-mm-) thick hood]; suitably reinforced.

Retain paragraph and subparagraphs below for roof curbs that are shop fabricated for field installation.  Delete if roof curbs are specified in Division 07 Section "Roof Accessories."

D. Roof Curbs:  Galvanized-steel sheet; with mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer.  Size as required to fit roof opening and ventilator base.

1. Configuration:  [Self-flashing without a cant strip, with] [Built-in cant and] [Built-in raised cant and] mounting flange.

Coordinate curb height with roof deck construction; other heights are available.

2. Overall Height:  [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Retain one or both of first two paragraphs below.  If both bird screening and insect screening are required, indicate location of each on Drawings.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.  ASHRAE 62.1-2004, Section 5.6.5 - "Bird Screens" requires that outdoor intakes be equipped with a screening device designed to limit penetration of a 1/2-inch (13-mm) probe.

E. Bird Screening:  [Galvanized-steel, 1/2-inch- (12.7-mm-) square mesh, 0.041-inch (1.04-mm) wire] [Aluminum, 1/2-inch- (12.7-mm-) square mesh, 0.063-inch (1.6-mm) wire] [Flattened, expanded aluminum, 3/4 by 0.050 inch (19 by 1.27 mm) thick] [Stainless-steel, 1/2-inch- (12.7-mm-) square mesh, 0.047-inch (1.19-mm) wire].

F. Insect Screening:  [Aluminum, 18-by-16 (1.4-by-1.6-mm) mesh, 0.012-inch (0.30-mm)] [Stainless-steel, 18-by-18 (1.4-by-1.4-mm) mesh, 0.009-inch (0.23-mm)] wire.

G. Galvanized-Steel Sheet Finish:

1. Surface Preparation:  Clean surfaces of dirt, grease, and other contaminants.  Clean welds, mechanical connections, and abraded areas and repair galvanizing according to ASTM A 780.  Apply a conversion coating suited to the organic coating to be applied over it.

Revise subparagraph below if a specific type of primer or a baked-on application is required.  Coordinate with Division 09 painting Sections.

2. Factory Priming for Field-Painted Finish:  Where field painting after installation is indicated, apply an air-dried primer immediately after cleaning and pretreating.

Subparagraph and associated subparagraph below are examples only.  Revise to suit Project or paint systems available from manufacturers specified.

3. Baked-Enamel Finish:  Immediately after cleaning and pretreating, apply manufacturer's standard finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 1 mil (0.025 mm) for topcoat and an overall minimum dry film thickness of 2 mils (0.05 mm).

a. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

2.6 GOOSENECKS

A. Factory or shop fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 5-5; with a minimum of 0.052-inch- (1.3-mm-) thick, galvanized-steel sheet.

Retain paragraph and subparagraphs below for roof curbs that are shop fabricated for field installation.  Delete if roof curbs are specified in Division 07 Section "Roof Accessories."

B. Roof Curbs:  Galvanized-steel sheet; with mitered and welded corners; 1-1/2-inch- (40-mm-) thick, rigid fiberglass insulation adhered to inside walls; and 1-1/2-inch (40-mm) wood nailer.  Size as required to fit roof opening and ventilator base.

1. Configuration:  [Self-flashing without a cant strip, with] [Built-in cant and] [Built-in raised cant and] mounting flange.

Coordinate curb height with roof deck construction; other heights are available.

2. Overall Height:  [8 inches (200 mm)] [9-1/2 inches (240 mm)] [12 inches (300 mm)] [16 inches (400 mm)] [18 inches (450 mm)].

Retain one or both of first two paragraphs below.  If both bird screening and insect screening are required, indicate location of each on Drawings.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.  ASHRAE 62.1-2004, Section 5.6.5 - "Bird Screens" requires that outdoor intakes be equipped with a screening device designed to limit penetration of a 1/2-inch (13-mm) probe.

C. Bird Screening:  [Galvanized-steel, 1/2-inch- (12.7-mm-) square mesh, 0.041-inch (1.04-mm) wire] [Aluminum, 1/2-inch- (12.7-mm-) square mesh, 0.063-inch (1.6-mm) wire] [Flattened, expanded aluminum, 3/4 by 0.050 inch (19 by 1.27 mm) thick] [Stainless-steel, 1/2-inch- (12.7-mm-) square mesh, 0.047-inch (1.19-mm) wire].

D. Insect Screening:  [Aluminum, 18-by-16 (1.4-by-1.6-mm) mesh, 0.012-inch (0.30-mm)] [Stainless-steel, 18-by-18 (1.4-by-1.4-mm) mesh, 0.009-inch (0.23-mm)] wire.

E. Galvanized-Steel Sheet Finish:

1. Surface Preparation:  Clean surfaces of dirt, grease, and other contaminants.  Clean welds, mechanical connections, and abraded areas and repair galvanizing according to ASTM A 780.  Apply a conversion coating suited to the organic coating to be applied over it.

Revise subparagraph below if a specific type of primer or a baked-on application is required.  Coordinate with Division 09 painting Sections.

2. Factory Priming for Field-Painted Finish:  Where field painting after installation is indicated, apply an air-dried primer immediately after cleaning and pretreating.

Subparagraph and associated subparagraph below are examples only.  Revise to suit Project or paint systems available from manufacturers specified.

3. Baked-Enamel Finish:  Immediately after cleaning and pretreating, apply manufacturer's standard finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 1 mil (0.025 mm) for topcoat and an overall minimum dry film thickness of 2 mils (0.05 mm).

a. Color and Gloss:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install intake and relief ventilators level, plumb, and at indicated alignment with adjacent work.

Retain option in first paragraph below if curbs are not provided by ventilator manufacturer.

B. Secure intake and relief ventilators to roof curbs with cadmium-plated hardware.  Use concealed anchorages where possible.[ Refer to Division 07 Section "Roof Accessories" for installation of roof curbs.]

C. Install goosenecks on curb base where throat size exceeds [9 by 9 inches (230 by 230 mm)] <Insert measurement>.

D. Install intake and relief ventilators with clearances for service and maintenance.

E. Install perimeter reveals and openings of uniform width for sealants and joint fillers, as indicated.

F. Install concealed gaskets, flashings, joint fillers, and insulation as installation progresses.  Comply with Division 07 Section "Joint Sealants" for sealants applied during installation.

G. Label intake and relief ventilators according to requirements specified in Division 23 Section "Identification for HVAC Piping and Equipment."

H. Protect galvanized and nonferrous-metal surfaces from corrosion or galvanic action by applying a heavy coating of bituminous paint on surfaces that will be in contact with concrete, masonry, or dissimilar metals.

I. Repair finishes damaged by cutting, welding, soldering, and grinding.  Restore finishes so no evidence remains of corrective work.  Return items that cannot be refinished in the field to the factory, make required alterations, and refinish entire unit or provide new units.

3.2 CONNECTIONS

Coordinate duct installation and specialty arrangements with schematics on Drawings and with requirements specified in duct systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Duct installation and connection requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of ducts and duct accessories.

3.3 ADJUSTING

A. Adjust damper linkages for proper damper operation.

END OF SECTION 233723

HVAC GRAVITY VENTILATORS
233723 - 1

