Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
09/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235100 - BREECHINGS, CHIMNEYS, AND STACKS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Listed chimney liners.

2. Listed [single] [double]-wall [vents] [chimneys].

3. Listed, refractory-lined[ breechings and] stacks.

4. Field-fabricated metal breechings[ and chimneys].

5. Listed [grease] [dishwasher] [grease and dishwasher] ducts.

B. Related Sections include the following:

List below only products and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 23 Section "Draft Control Devices" for induced-draft and mechanical fans and for motorized and barometric dampers.

1.3 SUBMITTALS

A. Product Data:  For the following:

1. Chimney liners.

2. Type B and BW vents.

3. Type L vents.

4. Special gas vents.

5. Building-heating-appliance chimneys.

6. Grease ducts.

7. Refractory-lined metal breechings and chimneys.

8. Guy wires and connectors.

B. Shop Drawings:  For vents, breechings, chimneys, and stacks.  Include plans, elevations, sections, details, and attachments to other work.

1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, methods of field assembly, components, hangers and seismic restraints, and location and size of each field connection.

Retain subparagraph below if products are required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify products' compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

2. For installed products indicated to comply with design loads, include calculations required for selecting seismic restraints and structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

C. Welding certificates.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

D. Manufacturer Seismic Qualification Certification:  Submit certification that factory-fabricated breeching, chimneys, and stacks; accessories; and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Breeching, Chimneys, and Stacks:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of anchorage devices on which the certification is based and their installation requirements.

E. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Source Limitations:  Obtain listed system components through one source from a single manufacturer.

Delete first paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

B. Welding:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code--Steel," for hangers and supports and AWS D9.1/D9.1M, "Sheet Metal Welding Code," for shop and field welding of joints and seams in vents, breechings, and stacks.

C. Certified Sizing Calculations:  Manufacturer shall certify venting system sizing calculations.

1.5 COORDINATION

Retain first paragraph below for chimneys and stacks supported on concrete bases.

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

B. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

1.6 WARRANTY

Retain this Article for breechings, chimneys, and stacks containing refractory.

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of venting system that fail in materials or workmanship within specified warranty period.  Failures include, but are not limited to, structural failures caused by expansion and contraction.

Verify available warranties for units and components and insert number in subparagraph below.

1. Warranty Period:  [10] [15] [25] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 LISTED CHIMNEY LINERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. American Metal Products; MASCO Corporation.

2. Deflect-O Corp.

3. Heat-Fab, Inc.

4. Industrial Chimney Company.

5. Metal-Fab, Inc.

6. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

7. Shook Manufactured Products, Inc.

8. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

9. Tru-Flex Metal Hose Corp.

10. <Insert manufacturer's name.>

Straight, stainless-steel chimney liners can be used for dishwasher exhaust ducts and Type II, commercial kitchen hood exhaust ducts.

D. Description:  [Straight] [Corrugated], single-wall chimney liner tested according to UL 1777 and rated for 1000 deg F (538 deg C) continuously, or 2100 deg F (1150 deg C) for 10 minutes; with negative or positive flue pressure complying with NFPA 211.

E. Straight Liner Materials:  ASTM A 666, [Type 304] [Type 316] stainless steel.

F. Corrugated Liner Materials:  [ASTM A 240/A 240M, Type 321] [ASTM A 240/A 240M, Type 430] [ASTM A 959, Type 29-4C] stainless steel.

G. Accessories:

1. Fittings:  Tees, elbows, increasers, draft-hood connectors, metal caps with bird barriers, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar or compatible materials and designs.

Retain first subparagraph below for positive-pressure applications.

2. Sealant:  Manufacturer's standard high-temperature sealant.

3. Insulating Fill:  Manufacturer's standard high-temperature insulation fill material in annular space surrounding chimney liner including high-temperature, ceramic-fiber insulation required to seal chimney at top and bottom.

2.2 LISTED TYPE B AND BW VENTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. American Metal Products; MASCO Corporation.

2. Cleaver-Brooks; Div. of Aqua-Chem Inc.

3. FAMCO.

4. Hart & Cooley, Inc.

5. Heat-Fab, Inc.

6. Industrial Chimney Company.

7. LSP Products Group, Inc.

8. Metal-Fab, Inc.

9. Schebler Co. (The).

10. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

11. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

12. Tru-Flex Metal Hose Corp.

13. Van-Packer Company, Inc.

14. <Insert manufacturer's name.>

D. Description:  Double-wall metal vents tested according to UL 441 and rated for 480 deg F (248 deg C) continuously for Type B, or 550 deg F (288 deg C) continuously for Type BW; with neutral or negative flue pressure complying with NFPA 211.

E. Construction:  Inner shell and outer jacket separated by at least a 1/4-inch (6-mm) airspace.

F. Inner Shell:  [ASTM B 209 (ASTM B 209M), Type 1100 aluminum] [ASTM B 209 (ASTM B 209M), Type 3003 aluminum] [ASTM B 209 (ASTM B 209M), Type 3105 aluminum] [ASTM A 666, Type 430 stainless steel].

G. Outer Jacket:  [Galvanized] [Aluminized] steel.

H. Accessories:  Tees, elbows, increasers, draft-hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.

Retain one of first four "Termination" subparagraphs below or insert type to suit Project.  Use caution because many systems are tested with specific terminations.

1. Termination:  Stack cap designed to exclude minimum 90 percent of rainfall.

2. Termination:  Round chimney top designed to exclude minimum 98 percent of rainfall.

3. Termination:  Exit cone with drain section incorporated into riser.

4. Termination:  Antibackdraft.

5. Termination:  <Insert termination.>

2.3 LISTED TYPE L VENTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. American Metal Products; MASCO Corporation.

2. FAMCO.

3. Heat-Fab, Inc.

4. Industrial Chimney Company.

5. LSP Products Group, Inc.

6. Metal-Fab, Inc.

7. Schebler Co. (The).

8. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

9. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

10. Tru-Flex Metal Hose Corp.

11. Van-Packer Company, Inc.

12. <Insert manufacturer's name.>

D. Description:  Double-wall metal vents tested according to UL 641 and rated for 570 deg F (300 deg C) continuously, or 1700 deg F (926 deg C) for 10 minutes; with neutral or negative flue pressure complying with NFPA 211.

E. Construction:  Inner shell and outer jacket separated by at least a [1/4-inch (6-mm)] [1-inch (25-mm)] [2-inch (50-mm)] [4-inch (100-mm)] airspace filled with high-temperature, [ceramic-fiber] [mineral-wool] insulation.

F. Inner Shell:  ASTM A 666, [Type 304] [Type 316] stainless steel.

G. Outer Jacket:  [Galvanized] [Aluminized] [Stainless] steel.

H. Accessories:  Tees, elbows, increasers, draft-hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.

Retain one of first three "Termination" subparagraphs below or insert type to suit Project.  Use caution because many systems are tested with specific terminations.

1. Termination:  Stack cap designed to exclude 90 percent of rainfall.

2. Termination:  Round chimney top designed to exclude 98 percent of rainfall.

3. Termination:  Exit cone with drain section incorporated into riser.

4. Termination:  <Insert termination.>

2.4 LISTED SPECIAL GAS VENTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Heat-Fab, Inc.

2. Metal-Fab, Inc.

3. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

4. Z-Flex; Flexmaster Canada Limited.

5. <Insert manufacturer's name.>

D. Description:  Double-wall metal vents tested according to UL 1738 and rated for 480 deg F (248 deg C) continuously, with positive or negative flue pressure complying with NFPA 211.

E. Construction:  Inner shell and outer jacket separated by at least a 1/2-inch (13-mm) airspace.

F. Inner Shell:  ASTM A 959, Type 29-4C stainless steel.

G. Outer Jacket:  [Aluminized] [Stainless] steel.

H. Accessories:  Tees, elbows, increasers, draft-hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.

Retain one of first three "Termination" subparagraphs below or insert type to suit Project.  Use caution because many systems are tested with specific terminations.

1. Termination:  Stack cap designed to exclude minimum 90 percent of rainfall.

2. Termination:  Round chimney top designed to exclude minimum 98 percent of rainfall.

3. Termination:  Exit cone with drain section incorporated into riser.

4. Termination:  <Insert termination.>

2.5 LISTED BUILDING-HEATING-APPLIANCE CHIMNEYS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. American Metal Products; MASCO Corporation.

2. Cleaver-Brooks; Div. of Aqua-Chem Inc.

3. FAMCO.

4. Hart & Cooley, Inc.

5. Heat-Fab, Inc.

6. Industrial Chimney Company.

7. LSP Products Group, Inc.

8. Metal-Fab, Inc.

9. Schebler Co. (The).

10. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

11. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

12. Tru-Flex Metal Hose Corp.

13. Van-Packer Company, Inc.

14. <Insert manufacturer's name.>

Retain three paragraphs below for building-heating-appliance chimneys suitable for dual-fuel boilers, oven vents, water heaters, or exhaust for engines.

D. Description:  Double-wall metal vents tested according to UL 103 and rated for 1000 deg F (538 deg C) continuously, or 1700 deg F (926 deg C) for 10 minutes; with neutral or negative flue pressure complying with NFPA 211.

E. Construction:  Inner shell and outer jacket separated by at least a [1/2-inch (25-mm)] [1-inch (50-mm)] [2-inch (50-mm)] [3-inch (75-mm)] [4-inch (100-mm)] annular space[ filled with high-temperature, ceramic-fiber insulation].

F. Inner Shell:  ASTM A 666, [Type 304] [Type 316] stainless steel.

Retain three paragraphs below for 1400 deg F (760 deg C) chimneys suitable for dual-fuel boilers, oven vents, water heaters, or exhaust for engines.

G. Description:  Double-wall metal vents tested according to UL 103 and UL 959 and rated for 1400 deg F (760 deg C) continuously, or 1800 deg F (982 deg C) for 10 minutes; with positive or negative flue pressure complying with NFPA 211.

H. Construction:  Inner shell and outer jacket separated by at least a [1-inch (25-mm)] [2-inch (50-mm)] [3-inch (75-mm)] [4-inch (100-mm)] annular space filled with high-temperature, ceramic-fiber insulation.

I. Inner Shell:  ASTM A 666, [Type 304] [Type 316] stainless steel.

Retain first three paragraphs below for Type HT chimneys suitable for fireplaces and other solid-fuel-burning appliances.

J. Description:  Double-wall metal vents tested according to UL 103 and rated for 1000 deg F (538 deg C) continuously, or 2100 deg F (1150 deg C) for 10 minutes; with neutral or negative flue pressure complying with NFPA 211.

K. Construction:  Inner shell and outer jacket separated by at least a [1-inch (25-mm)] [1-1/2-inch (38-mm)] [2-inch (50-mm)] [4-inch (100-mm)] annular space filled with high-temperature, ceramic-fiber insulation.

L. Inner Shell:  [ASTM A 666, Type 304] [ASTM A 666, Type 316] [ASTM A 240/A 240M, Type 430] stainless steel.

M. Outer Jacket:  [Galvanized] [Aluminized] [Stainless] steel.

N. Accessories:  Tees, elbows, increasers, draft-hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.

Retain one of first three "Termination" subparagraphs below or insert type to suit Project.  Use caution because many systems are tested with specific terminations.

1. Termination:  Stack cap designed to exclude minimum 90 percent of rainfall.

2. Termination:  Round chimney top designed to exclude minimum 98 percent of rainfall.

3. Termination:  Exit cone with drain section incorporated into riser.

4. Termination:  <Insert termination.>

2.6 LISTED GREASE DUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. American Metal Products; MASCO Corporation.

2. FAMCO.

3. Heat-Fab, Inc.

4. Industrial Chimney Company.

5. LSP Products Group, Inc.

6. Metal-Fab, Inc.

7. Schebler Co. (The).

8. Selkirk Inc.; Selkirk Metalbestos and Air Mate.

9. Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

10. Tru-Flex Metal Hose Corp.

11. Van-Packer Company, Inc.

12. <Insert manufacturer's name.>

D. Description:  Double-wall metal vents tested according to UL 1978 and rated for 500 deg F (260 deg C) continuously, or 2000 deg F (1093 deg C) for 30 minutes; with positive or negative duct pressure and complying with NFPA 211.

E. Construction:  Inner shell and outer jacket separated by at least a [1-inch (25-mm)] [2-inch (50-mm)] [3-inch (75-mm)] [4-inch (100-mm)] annular space filled with high-temperature, ceramic-fiber insulation.

F. Inner Shell:  ASTM A 666, [Type 304] [Type 316] stainless steel.

G. Outer Jacket:  [Aluminized] [Stainless] steel where concealed.  Stainless steel where exposed.

H. Accessories:  Tees, elbows, increasers, hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.  Include unique components required to comply with NFPA 96 including cleanouts, transitions, adapters and drain fittings.

2.7 LISTED, REFRACTORY-LINED METAL BREECHINGS AND CHIMNEYS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Van-Packer Company, Inc.

2. Warren Environment, Inc.

3. <Insert manufacturer's name.>

D. Comply with ASME STS-1.

Retain and revise first two paragraphs below to suit Project conditions for freestanding stacks.

E. Design Wind Loads:  [150 mph (241 km/h)] <Insert wind speed>.

F. Design for seismic conditions at Project site.

G. Chimney Outer Jacket:  [Aluminized] [Galvanized] steel with [riveted] [welded] seams.

H. Refractory Lining:  Tested according to UL 959 for temperature and acid resistance, and bearing the testing laboratory label.

1. Temperature Rating:  1800 deg F (982 deg C) continuously, and 2000 deg F (1093 deg C) intermittently.

2. Acid Extraction:  Maximum of 0.2 percent.

3. Cold Crushing Strength:  Minimum of 3200 psig (22 MPa).

4. Thickness:  Minimum of 2 inches (50 mm).

Paint materials and applications are specified in Division 09 Section "High-Performance Coatings."

I. Finish:  Factory-applied, high-heat-resistant paint; color as selected by Architect.

Components and accessories in remaining paragraphs are typically used for prefabricated chimneys and stacks.  Revise to suit Project.  First two paragraphs must be revised for freestanding stacks.

J. Base Section:  Acid-resistant-coated, cast-iron anchor lugs for securing stack to foundation[ with anchorage designed by manufacturer].

K. Reinforced Cleanout Section:  Smoke-tight connection, with gasketed and bolt-tightened inspection plate; neck shall be welded to stack section.

L. T or Y Sections:  Smoke-tight connection, with welded joints and refractory lining; finished with smooth transition and with no exposed metal on inside.

M. Spark Screen:  ASTM A 666, Type 316 stainless steel, 0.0625 inch (1.6 mm) thick, maximum 1/2-by-1/2-inch (13-by-13-mm) mesh, with ASTM A 666, Type 304 stainless-steel rolled angle and drawband.

N. Guy Bands:  8-inch- (200-mm-) wide bands of same material as jacket, with bolted fasteners.

O. Roof Penetration:  Factory-fabricated thimbles, flashings, and counterflashings.

P. Fabricate sections, fittings, and accessories as individual pieces or in combination lengths for field handling.

Q. Fabricate components with centrifugally cast refractory lining in lengths suitable for connection with drawbands.

R. Bond refractory to steel jacket with calcium aluminate cement to prevent separation in finished product during shipping, handling, and installation.

S. Fabricate stacks with anchor lugs; cleanout; T sections; flashings and counterflashings; and provisions for support, expansion, and contraction.

2.8 FIELD-FABRICATED METAL BREECHINGS AND CHIMNEYS

Retain paragraph below for freestanding stacks.  Insert dimensions unless they are indicated on Drawings.

A. Fabricate freestanding chimneys according to SMACNA's "Guide for Steel Stack Design and Construction."  Design for minimum <Insert feet (meters)> high and <Insert inches (mm)> in diameter.

Retain paragraph and subparagraphs below for low-heat appliances.

B. Fabricate breechings and chimneys from ASTM A 1011/A 1011M hot-rolled steel with continuously welded joints, complying with NFPA 211 for minimum metal thickness.

1. Equal to or Less Than 1.069 Sq. Ft. (0.099 Sq. m.) or 14 Inches (356 mm) in Diameter:  0.053 inch (1.35 mm).

2. Up to 1.396 Sq. Ft. (0.129 Sq. m) or 16 Inches (406 mm) in Diameter:  0.067 inch (1.7 mm).

3. Up to 1.764 Sq. Ft. (0.164 Sq. m.) or 18 Inches (457 mm) in Diameter:  0.093 inch (2.36 mm).

4. Larger Than Above:  0.123 inch (3.12 mm).

Retain paragraph and subparagraphs below for oil-fired appliances, solid-fuel-burning appliances, or appliances listed for venting with Type L vents.

C. Fabricate chimneys and vent connectors from galvanized steel, complying with NFPA 211 for minimum metal thickness.

1. Equal to or Less Than 6 Inches (152 mm) in Diameter:  0.019 inch (0.48 mm).

2. Up to 10 Inches (254 mm) in Diameter:  0.024 inch (0.61 mm).

3. Up to 16 Inches (406 mm) in Diameter:  0.029 inch (0.74 mm).

4. Larger Than Above:  0.056 inch (1.42 mm).

Retain two paragraphs and subparagraphs below for appliances not installed in attics that are listed to be vented by Type B or L vents.

D. Fabricate chimneys and vent connectors from ASTM B 209 (ASTM B 209M), Type 1100 or 3003, aluminum or stainless steel, complying with NFPA 211 for the following minimum metal thicknesses:

1. Aluminum:  0.027 inch (0.69 mm).

2. Stainless Steel:  0.012 inch (0.31 mm).

E. Fabricate cleanout doors from compatible material, same thickness as breeching, bolted and gasketed.

Retain paragraph and subparagraphs below for engine exhaust applications that use steel pipe.

F. Fabricate engine exhaust from ASTM A 53/A 53M, Type E (electric-resistance welded), Grade B; or ASTM A 106, Type S, Grade B, [Schedule 40] [Schedule 80] pipe; with welded joints and carbon-steel fittings and flanges.

1. Wrought-Steel Fittings:  ASME B16.9, wall thickness to match adjoining pipe.

2. Wrought Cast- and Forged-Steel Flanges and Flanged Fittings:  ASME B16.5, Class 150, including bolts, nuts, and gaskets.

2.9 GUYING AND BRACING MATERIALS

This Article contains materials recommended by one manufacturer that also advises that a professional engineer design components and connections to adjacent structures.

A. Cable:  [Three] [Four] <Insert number> galvanized, stranded wires of the following thickness:

Retain appropriate size in subparagraphs below.

1. Minimum Size:  1/4 inch (6 mm) in diameter.

2. For ID Sizes 4 to 15 Inches (100 to 381 mm):  5/16 inch (8 mm).

3. For ID Sizes 18 to 24 Inches (457 to 610 mm):  3/8 inch (9.5 mm).

4. For ID Sizes 27 to 30 Inches (685 to 762 mm):  7/16 inch (11 mm).

5. For ID Sizes 33 to 36 Inches (838 to 915 mm):  1/2 inch (13 mm).

6. For ID Sizes 39 to 48 Inches (990 to 1220 mm):  9/16 inch (14.3 mm).

7. For ID Sizes 51 to 60 Inches (1295 to 1524 mm):  5/8 inch (16 mm).

B. Pipe:  [Two] [Three] <Insert number> galvanized steel, NPS 1-1/4 (DN 32).

C. Angle Iron:  [Two] [Three] <Insert number> galvanized steel, 2 by 2 by 0.25 inch (50 by 50 by 6 mm).

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of work.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATION

Revise this Article to include breechings, chimneys, and stacks included on Project.

A. Listed Chimney Liners:  High-efficiency boiler or furnace vents in masonry chimney, dishwasher exhaust, or Type II commercial kitchen hood.

B. Listed Type B and BW Vents:  Vents for certified gas appliances.

C. Listed Type L Vent:  Vents for low-heat appliances.

D. Listed Special Gas Vent:  Condensing gas appliances.

E. Listed Building-Heating-Appliance Chimneys:  Dual-fuel boilers, oven vents, water heaters, and exhaust for engines.  Fireplaces and other solid-fuel-burning appliances.

F. Listed Grease Ducts:  Type I commercial kitchen grease duct.

G. Listed, Refractory-Lined Metal Breechings and Chimneys:  Freestanding dual-fuel boiler vents, oven vents, water heaters, exhaust for engines, fireplaces, and other solid-fuel-burning appliances.

H. Field-Fabricated Metal Breechings and Chimneys:  Dual-fuel boilers, oven vents, water heaters, exhaust for engines, fireplaces, and other solid-fuel-burning appliances.

Retain paragraph below if steel pipe is required for engine exhaust.

I. Field-Fabricated Metal Breechings and Chimneys:  Steel pipe for use with engine exhaust.

3.3 INSTALLATION OF LISTED VENTS AND CHIMNEYS

A. Locate to comply with minimum clearances from combustibles and minimum termination heights according to product listing or NFPA 211, whichever is most stringent.

Retain first paragraph below if specifying positive-pressure vents.

B. Seal between sections of positive-pressure vents and grease exhaust ducts according to manufacturer's written installation instructions, using sealants recommended by manufacturer.

C. Support vents at intervals recommended by manufacturer to support weight of vents and all accessories, without exceeding appliance loading.

Retain first paragraph below for appliances more than 83 percent efficient.

D. Slope breechings down in direction of appliance, with condensate drain connection at lowest point piped to nearest drain.

E. Lap joints in direction of flow.

Retain three paragraphs below for refractory-lined chimneys.

F. Connect base section to foundation using anchor lugs of size and number recommended by manufacturer.

G. Join sections with acid-resistant joint cement to provide continuous joint and smooth interior finish.

H. Erect stacks plumb to finished tolerance of no more than 1 inch (25 mm) out of plumb from top to bottom.

3.4 INSTALLATION OF UNLISTED, FIELD-FABRICATED BREECHINGS AND CHIMNEYS

A. Suspend breechings and chimneys independent of their appliance connections.

Retain first paragraph below for Projects in seismic areas.

B. Install, support, and restrain according to seismic requirements.

C. Align breechings at connections, with smooth internal surface and a maximum 1/8-inch (3-mm) misalignment tolerance.

Retain first paragraph below for appliances more than 83 percent efficient.

D. Slope breechings down in direction of appliance, with condensate drain connection at lowest point piped to nearest drain.

E. Lap joints in direction of flow.

F. Support breechings and chimneys from building structure with bolts, concrete inserts, steel expansion anchors, welded studs, C-clamps, or beam clamps according to manufacturer's written instructions.

3.5 CLEANING

A. After completing system installation, including outlet fittings and devices, inspect exposed finish.  Remove burrs, dirt, and construction debris and repair damaged finishes.

B. Clean breechings internally, during and after installation, to remove dust and debris.  Clean external surfaces to remove welding slag and mill film.  Grind welds smooth and apply touchup finish to match factory or shop finish.

C. Provide temporary closures at ends of breechings, chimneys, and stacks that are not completed or connected to equipment.

END OF SECTION 235100

	BREECHINGS, CHIMNEYS, AND STACKS
	235100 - 1



