Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
03/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235213 - ELECTRIC BOILERS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged, factory-fabricated and -assembled electric boilers, trim, and accessories for generating [hot water] [steam].

1.3 SUBMITTALS

A. Product Data:  Include performance data, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:  For boilers, boiler trim, and accessories.  Include plans, elevations, sections, details, and attachments to other work.

Retain first subparagraph and associated subparagraph below if boilers are required to withstand specific design loads and Architect has either delegated design responsibility to Contractor or wants to review structural data as another way to verify boiler's compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

1. Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

a. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

2. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

C. Manufacturer Seismic Qualification Certification:  Submit certification that boiler, accessories, and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Source quality-control test reports.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For boilers, components, and accessories to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

H. Other Informational Submittals:

Retain first subparagraph below for steam boilers operating at more than 15 psig (104 kPa) or hot-water boilers operating at more than 160 psig (1100 kPa) or 250 deg F (120 deg C).

1. ASME Stamp Certification and Report:  Submit "A," "S," or "PP" stamp certificate of authorization, as required by authorities having jurisdiction, and document hydrostatic testing of piping external to boiler.

2. Startup service reports.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASME Compliance:  Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

C. NFPA Compliance:  Design and fabricate boilers to comply with NFPA 70, "National Electrical Code," Article 424, Paragraphs G and H.

D. UL Compliance:  Test boilers for compliance with UL 834, "Heating, Water Supply, and Power Boilers--Electric."  Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."  See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 23 Section "Heating Boilers."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace pressure vessels of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations in Division 23 Section "Heating Boilers" for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers in this Article.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Acme Engineering Prod. Inc.

2. Bryan Steam, LLC.

3. Cleaver-Brooks; div. of Aqua-Chem, Inc.

4. Fulton Boiler Works, Inc.

5. Lattner Boiler Manufacturing.

6. Lochinvar Corporation.

7. Patterson-Kelley.

8. Precision Boilers.

9. PVI Industries, LLC.

10. RECO USA.

11. Reimers Electra Steam, Inc.

12. <Insert manufacturer's name.>

2.2 MANUFACTURED UNITS

A. Description:  Factory-fabricated, -assembled, and -tested electric boilers with trim and controls necessary to generate [hot water] [steam].

B. Pressure Vessel:  [Carbon-steel] [Cast-iron] pressure vessel mounted on structural-steel base.

C. Nozzles:  Flanges for [water inlet and] [steam] outlet and heating element inserts; threaded connections for trim and controls.

D. Insulation:  [One layer] [Two layers] of minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick, glass-fiber insulation.

E. Jacket:  [Galvanized ]sheet metal casing with [baked-enamel] [powder-coated] protective finish and removable panels with snap-in or interlocking closures for access to pressure vessel.

F. Lifting Lugs:  Welded to pressure vessel, extending above jacket.

G. Heating Elements:  [Copper] [Incoloy]-sheathed, replaceable electric-resistance element, rated 20 kW maximum, with maximum [50 W/sq. in. (7.7 W/sq. cm)] [75 W/sq. in. (11.5 W/sq. cm)] over heat-transfer length.

H. Mounting base to secure boiler to concrete base.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

1. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when mounting base is anchored to building structure.

Retain one of two "Trim" articles below.

2.3 TRIM

Retain this Article for hot-water boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 160 psig (1100 kPa) or boiler temperature exceeds 250 deg F (120 deg C).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, Building Services Piping]."

Retain first paragraph below if using modulating sequence of elements.

B. Aquastat Controllers:  Operating auto-reset high limit.

C. Safety Relief Valve:  ASME rated.

D. Pressure and Temperature Gage:  Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage.  Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

E. Boiler Air Vent:  [Automatic] [Manual].

F. Dip-tube in water outlet.

G. Drain Valve:  Minimum NPS 3/4 (DN 20) hose-end ball valve sized per requirements of authorities having jurisdiction.

Coordinate paragraph and subparagraphs below with other Division 22 Sections for domestic water heaters.  A tankless heater is not available from all manufacturers listed.

H. Tankless Heater:  Carbon-steel header with copper-tube heat exchanger, mounted in an upper port of pressure vessel and sealed with fiber gasket.

1. Tappings NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

2. Tappings NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

2.4 TRIM

Retain this Article for steam boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 15 psig (104 kPa).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, " Building Services Piping]."

Retain paragraph below if using modulating sequence of elements.

B. Pressure Controllers:  Operating auto-reset high limit.

Retain first paragraph and subparagraphs below if safety valve is a component of boiler.  Coordinate with Division 23 Section "Steam and Condensate Heating Piping."

C. Safety Relief Valve:

1. Size and Capacity:  As required for equipment according to ASME Boiler and Pressure Vessel Code.

2. Description:  Fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

a. Drip-Pan Elbow:  Cast iron and having threaded inlet and outlet with threads complying with ASME B1.20.1.

D. Pressure Gage:  Minimum 3-1/2-inch (89-mm) diameter.  Gage shall have normal operating pressure about 50 percent of full range.

E. Water Column:  Minimum 12-inch (300-mm) glass gage with shutoff cocks.

F. Drain Valves:  Minimum NPS 3/4 (DN 20) or nozzle size with hose-end connection.

In first paragraph below, retain option if boiler operating pressure exceeds 100 psig (690 kPa).

G. Blowdown Valves:  Factory-installed bottom and surface, slow-acting blowdown valves same size as boiler nozzle.[  Blowdown valves shall be combination of slow and quick acting as required by ANSI B31.1.]

H. Stop Valves:  Boiler inlets and outlets, except safety relief valves or preheater inlet and outlet, shall be equipped with stop valve in an accessible location as near as practical to boiler nozzle and same size or larger than nozzle.  Valves larger than NPS 2 (DN 50) shall have rising stem.

Retain paragraph below for boilers equipped with manhole openings that operate at more than 15 psig (104 kPa) and supply steam to a common steam header with other boilers.

I. Stop-Check Valves:  Factory-installed, stop-check valve and stop valve at boiler outlet with free-blow drain valve factory installed between the two valves and visible when operating stop-check valve.

Coordinate paragraph and subparagraphs below with other Division 22 Sections for domestic water heaters.  A tankless heater is not available from all manufacturers listed.

J. Tankless Heater:  Carbon-steel header with copper-tube heat exchanger, mounted in an upper port of pressure vessel and sealed with fiber gasket.

1. Tappings NPS 2 (DN 50) and Smaller:  Threaded ends according to ASME B1.20.1 for pipe threads.

2. Tappings NPS 2-1/2 (DN 65) and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

2.5 CONTROLS

Retain paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC."

A. Refer to Division 23 Section "Instrumentation and Control for HVAC."

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers.  Coordinate with Division 23 Section "Instrumentation and Control for HVAC."

B. Boiler operating controls shall include the following devices and features:

1. Control transformer.

2. Step controller.

3. Recycling relay returns controller to off position after power failure.

4. Multistage thermostat.

5. Control circuit switch.

6. Visual indication for each step.

7. Supply-voltage indicator.

8. Set-Point Adjust:  Set points shall be adjustable.

Retain subparagraph below for steam boilers.

9. Operating Level Control:  Factory wired and mounted to cycle feedwater pump(s) for makeup water control.

Retain one of three subparagraphs below for operating control sequences.  Retain one of first two subparagraphs for hot-water boilers; second or third, for steam boilers.

10. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control element sequence controller to maintain space temperature in response to thermostat with heat anticipator located in heated space.

11. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control element sequence controller to reset supply-water temperature inversely with outside-air temperature.  At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

12. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control element sequence controller to maintain a constant steam pressure.  Maintain pressure set point plus or minus 10 percent.

Retain subparagraph below with any of three "Sequence of Operation" subparagraphs above.

a. Include automatic, alternating-operation sequence for multiple boilers to provide equal runtime for boilers.

C. Safety Controls:  To maintain safe operating conditions, safety controls limit boiler operation.

In subparagraph below, retain "temperature" option for hot-water boiler and "pressure" option for steam boiler.

1. High Cutoff:  [Manual] [Automatic] reset stops boiler if operating conditions rise above set point or maximum boiler design [temperature] [pressure].

In first subparagraph below, retain first option for hot-water boilers and second option for steam boilers.

2. Low-Water Cutoff Switch:  [Electronic] [Float and electronic] probe shall prevent boiler operation on low water.  Cutoff switch shall be [manual] [automatic]-reset type.

3. Audible Alarm:  Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain paragraph and subparagraphs below if boiler controls interface with building management system.

D. Building Management System Interface:  Factory install hardware and software to enable building management system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building management system is through hardwired points and minimal interface is required.  If extensive interface is required, delete below and retain second subparagraph below.

1. Hardwired Points:

a. Monitoring:  On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control:  On/off operation, [hot water supply temperature set-point adjustment] [steam pressure adjustment] <Insert control>.

Retain subparagraph below if extensive interface with building management system is required and is beyond that than can be provided by hardwired points.  Requirement may exclude some manufacturers listed.

2. A communication interface with building management system shall enable building management system operator to remotely control and monitor the boiler from an operator workstation.  Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building management system.

2.6 ELECTRICAL POWER

A. Single-Point Field Power Connection:  Factory-installed and -wired switches, transformers, and electrical devices necessary shall provide a single-point field power connection to boiler.

1. Field power interface shall be to [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

Subparagraph below describes an optional, but recommended, safety feature.  Edit to suit Project.

2. Interlock with door to de-energize power with door open.

B. Electrical Enclosures:  NEMA 250, Type [1] <Insert type> enclosure with hinged door and key-locking handle.

C. Install factory wiring outside of an enclosure in a [metal ]raceway.

D. Comply with NFPA 70.

1. Electrical Circuits:  48 A, maximum.

E. Connectors:  Mechanical lugs bolted to copper bus bars or distribution blocks with pressure connectors.

F. Fuses:  NEMA FU 1, Class J or K5; 60 A, maximum.

G. Contactors:  3-pole magnetic contactors, listed for 500,000 cycles at full load.

H. Factory-wired internal control devices and heating elements.

1. Wiring shall be numbered and color coded to match the wiring diagram.

2.7 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of boiler, delete this Article and schedule boilers on Drawings.

A. Heating Medium:  [Hot water] [Steam].

Retain one of first two paragraphs below.  Retain first for hot-water boilers and second for steam boilers.

B. Design Pressure Rating:  [160 psig (1100 kPa)] <Insert value>.

C. Design Pressure Rating:  [15 psig (104 kPa)] [60 psig (420 kPa)] [125 psig (860 kPa)] <Insert value>.

D. Safety Relief Valve Setting:  <Insert psig (kPa).>

Retain four paragraphs below for hot-water boilers.

E. Entering-Water Temperature:  <Insert deg F (deg C).>

F. Leaving-Water Temperature:  <Insert deg F (deg C).>

G. Design Water Flow Rate:  <Insert gpm (L/s).>

H. Design Pressure Drop:  <Insert psig (kPa).>

Retain two paragraphs below for steam boilers.

I. Steam Operating Pressure:  <Insert psig (kPa).>

J. Steam Flow Rate:  <Insert lb/h (kg/s).>

Retain one of two paragraphs below for rating methods.

K. Output Capacity:  <Insert MBh (kW).>

L. Equivalent Direct Radiation:  <Insert EDR (W).>

Retain first paragraph and subparagraphs below if boiler is equipped with tankless water heater.

M. Tankless Water Heater:

1. Design Water Flow:  <Insert gpm (L/s).>

2. Design Pressure Drop:  <Insert psig (kPa).>

3. Entering-Water Temperature:  <Insert deg F (deg C).>

4. Leaving-Water Temperature:  <Insert deg F (deg C).>

N. Electrical Characteristics:

1. kilowatts:  <Insert value.>

2. Volts:  [208] [480] <Insert value> V.

3. Phase:  Three.

4. Hertz:  [50] [60].

5. Full-Load Amperes:  <Insert value.>

6. Minimum Circuit Ampacity:  <Insert value.>

7. Maximum Overcurrent Protection:  <Insert amperage.>

2.8 SOURCE QUALITY CONTROL

A. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

B. Hydrostatic Test:  Factory test assembled boiler including hydrostatic test.

Retain paragraph below if Owner wants to witness source quality-control testing.

C. Allow Owner access to source quality-control testing of boilers.  Notify Architect 14 days in advance of testing.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before boiler installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations, and piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

1. Final boiler locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

B. Examine mechanical spaces, including required space for element removal, for suitable conditions where boilers will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 BOILER INSTALLATION

A. Install boilers level on concrete base.  Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

Coordinate selection of device and deflection in first paragraph below with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."  Vibration isolation of electric boilers is not common except under extreme circumstances.  Review Project requirements and edit to suit.

B. Vibration Isolation:  Elastomeric [isolator pads] [mounts] with a minimum static deflection of [0.25 inch (6.35 mm)] <Insert deflection>.  Vibration isolation devices and installation requirements are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

C. Install electrical devices furnished with boiler but not specified to be factory mounted.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to boiler to allow service and maintenance.

C. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.

D. Connect steam and condensate piping to supply-, return-, and blowdown-boiler tappings with shutoff valve and union or flange at each connection.

E. Install piping from safety relief valves to nearest floor drain.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.  Delete both if safety valves are specified in Division 23 Section "Steam and Condensate Heating Piping" or "Hydronic Piping."

F. Install piping from safety valves to drip-pan elbow and to nearest floor drain.

G. Install piping from equipment drain connection to nearest floor drain.  Piping shall be at least full size of connection.  Provide an isolation valve if required.

H. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

I. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

3. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

a. Check and adjust initial operating set points and high- and low-limit safety set points of water level and [water temperature] [steam pressure].

b. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Remove and replace malfunctioning units and retest as specified above.

D. Occupancy Adjustments:  When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

Retain paragraph and subparagraphs below if performance tests are required.  Performance verification based on field tests is not typically required because of the associated cost.  Consult Owner.

E. Performance Tests:

1. Engage a factory-authorized service representative to inspect component assemblies and equipment installations, including connections, and to conduct performance testing.

2. Boilers shall comply with performance requirements indicated, as determined by field performance tests.  Adjust, modify, or replace equipment in order to comply.

3. Perform field performance tests to determine the capacity of boilers.

4. Repeat tests until results comply with requirements indicated.

5. Provide analysis equipment required to determine performance.

6. Provide temporary equipment and system modifications necessary to dissipate the heat produced during tests if building systems are not adequate.

7. Notify Architect in advance of test dates.

8. Document test results in a report and submit to Architect.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[  Video training sessions.] Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 235213

	ELECTRIC BOILERS
	235213 - 1



