Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
03/04 (R 06/06)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235216 - CONDENSING BOILERS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged, factory-fabricated and -assembled, gas-fired, [pulse-combustion] [fire-tube] [water-tube] [water-jacketed] condensing boilers, trim, and accessories for generating [hot water] [steam].

1.3 SUBMITTALS

A. Product Data:  Include performance data, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings:  For boilers, boiler trim, and accessories.  Include plans, elevations, sections, details, and attachments to other work.

Retain subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify equipment's compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

1. Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

a. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

b. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails and equipment mounting frames.

Retain subparagraph below if equipment includes wiring.

2. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

C. Manufacturer Seismic Qualification Certification:  Submit certification that boiler, accessories, and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

D. Source quality-control test reports.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For boilers to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

H. Other Informational Submittals:

Retain subparagraph below for steam boilers operating at more than 15 psig (104 kPa) or hot-water boilers operating at more than 160 psig (1100 kPa) or 250 deg F (121 deg C).

1. ASME Stamp Certification and Report:  Submit "A," "S," or "PP" stamp certificate of authorization, as required by authorities having jurisdiction, and document hydrostatic testing of piping external to boiler.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASME Compliance:  Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

C. ASHRAE/IESNA 90.1 Compliance:  Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

Delete first paragraph below if boiler rating exceeds 300,000 Btu/h (87.9 kW).

D. DOE Compliance:  Minimum efficiency shall comply with 10 CFR 430, Subpart B, Appendix N, "Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers."

E. UL Compliance:  Test boilers for compliance with UL 795, "Commercial-Industrial Gas Heating Equipment." Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 23 Section "Heating Boilers."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period for Pulse-Combustion Boilers:

a. Heat Exchanger Damaged by Thermal Shock:  [10] <Insert number> years from date of Substantial Completion.

b. Heat-Exchanger Corrosion:  [Prorated] [Nonprorated] for [five] <Insert number> years from date of Substantial Completion.

2. Warranty Period for Fire-Tube Condensing Boilers:

a. Leakage and Materials:  [10] <Insert number> years from date of Substantial Completion.

b. Heat Exchanger Damaged by Thermal Stress and Corrosion:  [Prorated] [Nonprorated] for [five] <Insert number> years from date of Substantial Completion.

3. Warranty Period for Water-Tube Condensing Boilers:  [20] <Insert number> years from date of Substantial Completion.

4. Warranty Period for Water-Jacketed Condensing Boilers:

a. Leakage and Materials:  [Eight] <Insert number> years from date of Substantial Completion.

b. Heat Exchanger Damaged by Thermal Stress and Corrosion:  [Prorated] [Nonprorated] for [five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations in Division 23 Section "Heating Boilers" for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers in this Article.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Retain one of four lists below.

Retain list below for pulse-combustion condensing boilers.

1. Fulton Boiler Works, Inc.

2. Gasmaster Industries Incorporated.

3. Hydrotherm, Inc.; a division of Mestek, Inc.

4. <Insert manufacturer's name.>

Retain list below for fire-tube condensing boilers.

5. AERCO International.

6. Heat Transfer Products, Inc.

7. <Insert manufacturer's name.>

Retain list below for water-tube condensing boilers.

8. Laars Heating Systems; a division of Waterpik Technologies, Inc.

9. Lochinvar Corporation.

10. <Insert manufacturer's name.>

Retain list below for water-jacketed condensing boilers.

11. Viessmann Manufacturing Co. (US) Inc.

12. <Insert manufacturer's name.>

Retain one of four "Manufactured Units" articles below.

2.2 MANUFACTURED UNITS

Retain this Article for pulse-combustion condensing boilers.

A. Description:  Factory-fabricated, -assembled, and -tested, pulse-combustion condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; combustion-air intake connections; water supply, return, and condensate drain connections; and controls.

Retain first option in first paragraph below if boiler operates at less than 140-degree return-water temperature.

B. Heat Exchanger:  [Type 316L, stainless-steel] [Carbon-steel] primary and secondary combustion chamber.

C. Pressure Vessel:  Carbon steel with welded heads and tube connections.

D. Exhaust Decoupler:  Fiberglass composite material in a corrosion-resistant steel box.

E. Burner:  [Natural] [Propane] gas, self-aspirating and self-venting after initial start.

F. Blower:  Centrifugal fan to operate only during start of each burner sequence.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

G. Gas Train:  Combination gas valve with manual shutoff and pressure regulator.

H. Ignition:  Spark ignition with 100 percent main-valve shutoff with electronic flame supervision.

I. Casing:

1. Jacket:  Sheet metal, with snap-in or interlocking closures.

2. Control Compartment Enclosure:  NEMA 250, Type 1A.

3. Finish:  [Baked-enamel] [Powder-coated] protective finish.

4. Insulation:  Minimum 2-inch- (50-mm-) thick, mineral-fiber insulation surrounding the heat exchanger.

5. Draft Hood:  [Integral] [External].

6. Combustion-Air Connection:  Inlet duct collar and sheet metal closure over burner compartment.

7. Mounting base to secure boiler to concrete base.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

a. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when mounting base is anchored to building structure.

J. Mufflers:  Carbon-steel intake muffler and stainless-steel exhaust.

K. Condensate Trap:  Cast-iron body with stainless-steel internal parts.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

L. Characteristics and Capacities:

1. Heating Medium:  [Hot water] [Steam].

Retain one of first two subparagraphs below.  Retain first for hot-water boilers and second for steam boilers.

2. Design Water Pressure Rating:  [15 psig (104 kPa)] [150 psig (1035 kPa)] <Insert pressure rating>.

3. Design Steam Pressure Rating:  [60 psig (415 kPa)] [100 psig (690 kPa)] [160 psig (1100 kPa)] <Insert pressure rating>.

4. Safety Relief Valve Setting:  <Insert psig (kPa).>

Retain five subparagraphs below for hot-water boilers.

5. Entering-Water Temperature:  <Insert deg F (deg C).>

6. Leaving-Water Temperature:  <Insert deg F (deg C).>

7. Design Water Flow Rate:  <Insert gpm (L/s).>

8. Minimum Water Flow Rate:  <Insert gpm (L/s).>

9. Design Pressure Drop:  <Insert psig (kPa).>

Retain two subparagraphs below for steam boilers.

10. Steam Operating Pressure:  <Insert psig (kPa).>

11. Steam Flow Rate:  <Insert lb/h (kg/s).>

Retain one of three subparagraphs below.  Specify standing or intermittent pilot with minimum AFUE.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1-2004, Table 6.8.1F, "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

12. Minimum Efficiency AFUE:  <Insert value> percent.

13. Minimum Thermal Efficiency:  <Insert value> percent.

14. Minimum Combustion Efficiency:  <Insert value> percent.

Retain one of first two subparagraphs below.

15. AGA Input:  <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining subparagraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

16. Gas Input:  <Insert cfh (mL/s).>

Retain one of three subparagraphs below for rating methods.

17. AGA Output Capacity:  <Insert MBh (kW).>

18. DOE Output Capacity:  <Insert MBh (kW).>

19. Equivalent Direct Radiation:  <Insert EDR (W).>

Consider impact of site altitude on fan and motor.

20. Blower:

a. Motor Horsepower:  <Insert value.>

b. RPM:  <Insert value.>

21. Electrical Characteristics:

a. Volts:  [115] [208] [230] [460] <Insert value> V.

b. Phase:  [Single] [Three].

c. Hertz:  [50] [60].

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.3 MANUFACTURED UNITS

Retain this Article for fire-tube condensing boilers.

A. Description:  Factory-fabricated, -assembled, and -tested, fire-tube condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; combustion-air intake connections; water supply, return, and condensate drain connections; and controls.  Water heating service only.

B. Heat Exchanger:  Nonferrous, corrosion-resistant combustion chamber.

C. Pressure Vessel:  Carbon steel with welded heads and tube connections.

D. Burner:  [Natural] [Propane] gas, forced draft.

E. Blower:  Centrifugal fan to operate during each burner firing sequence and to prepurge and postpurge the combustion chamber.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

F. Gas Train:  Combination gas valve with manual shutoff and pressure regulator.

G. Ignition:  Spark ignition with 100 percent main-valve shutoff with electronic flame supervision.

H. Casing:

1. Jacket:  [Sheet metal] [Plastic], with snap-in or interlocking closures.

2. Control Compartment Enclosures:  NEMA 250, Type 1A.

If retaining second option in "Jacket" Subparagraph above, delete first subparagraph below.

3. Finish:  [Baked-enamel] [Powder-coated] protective finish.

4. Insulation:  Minimum 2-inch- (50-mm-) thick, [mineral-fiber] [polyurethane-foam] insulation surrounding the heat exchanger.

5. Combustion-Air Connections:  Inlet and vent duct collars.

6. Mounting base to secure boiler.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

a. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when mounting base is anchored to building structure.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

I. Characteristics and Capacities:

1. Heating Medium:  Hot water.

2. Design Water Pressure Rating:  [160 psig (1100 kPa)] <Insert value>.

3. Safety Relief Valve Setting:  <Insert psig (kPa).>

4. Entering-Water Temperature:  <Insert deg F (deg C).>

5. Leaving-Water Temperature:  <Insert deg F (deg C).>

6. Design Water Flow Rate:  <Insert gpm (L/s).>

7. Minimum Water Flow Rate:  <Insert gpm (L/s).>

8. Design Pressure Drop:  <Insert psig (kPa).>

Retain one of three subparagraphs below.  Specify standing or intermittent pilot with minimum AFUE.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1-2004, Table 6.8.1F, "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

9. Minimum Efficiency AFUE:  <Insert value> percent.

10. Minimum Thermal Efficiency:  <Insert value> percent.

11. Minimum Combustion Efficiency:  <Insert value> percent.

Retain one of first two subparagraphs below.

12. AGA Input:  <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining subparagraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

13. Gas Input:  <Insert cfh (mL/s).>

Retain one of three subparagraphs below for rating methods.

14. AGA Output Capacity:  <Insert MBh (kW).>

15. DOE Output Capacity:  <Insert MBh (kW).>

16. Equivalent Direct Radiation:  <Insert EDR (W).>

Consider impact of site altitude on fan and motor.

17. Blower:

a. Motor Horsepower:  <Insert value.>

b. RPM:  <Insert value.>

18. Electrical Characteristics:

a. Volts:  [115] [208] [230] [460] <Insert value> V.

b. Phase:  [Single] [Three].

c. Hertz:  [50] [60].

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.4 MANUFACTURED UNITS

Retain this Article for water-tube condensing boilers.

A. Description:  Factory-fabricated, -assembled, and -tested, water-tube condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; combustion-air intake connections; water supply, return, and condensate drain connections; and controls.  Water heating service only.

B. Heat Exchanger:  Finned-copper primary and stainless-steel secondary heat exchangers.

C. Combustion Chamber:  Stainless steel, sealed.

D. Burner:  [Natural] [Propane] gas, forced draft drawing from gas premixing valve.

E. Blower:  Centrifugal fan to operate during each burner firing sequence and to prepurge and postpurge the combustion chamber.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

F. Gas Train:  Combination gas valve with manual shutoff and pressure regulator.

G. Ignition:  Silicone carbide hot-surface ignition that includes flame safety supervision and 100 percent main-valve shutoff.

H. Integral Circulator:  Cast-iron body and stainless-steel impeller sized for minimum flow required in heat exchanger.

I. Casing:

1. Jacket:  Sheet metal, with snap-in or interlocking closures.

2. Control Compartment Enclosures:  NEMA 250, Type 1A.

3. Finish:  Textured epoxy.

4. Insulation:  Minimum [1-inch- (25-mm-)] [2-inch- (50-mm-)] thick, mineral-fiber insulation surrounding the heat exchanger.

5. Combustion-Air Connections:  Inlet and vent duct collars.

6. Mounting base to secure boiler.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

a. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when mounting base is anchored to building structure.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

J. Characteristics and Capacities:

1. Heating Medium:  Hot water.

2. Design Water Pressure Rating:  [160 psig (1100 kPa)] <Insert value>.

3. Safety Relief Valve Setting:  <Insert psig (kPa).>

4. Entering-Water Temperature:  <Insert deg F (deg C).>

5. Leaving-Water Temperature:  <Insert deg F (deg C).>

6. Design Water Flow Rate:  <Insert gpm (L/s).>

7. Minimum Water Flow Rate:  <Insert gpm (L/s).>

8. Design Pressure Drop:  <Insert psig (kPa).>

Retain one of three subparagraphs below.  Specify standing or intermittent pilot with minimum AFUE.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1-2004, Table 6.8.1F, "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

9. Minimum Efficiency AFUE:  <Insert value> percent.

10. Minimum Thermal Efficiency:  <Insert value> percent.

11. Minimum Combustion Efficiency:  <Insert value> percent.

Retain one of first two subparagraphs below.

12. AGA Input:  <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining subparagraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

13. Gas Input:  <Insert cfh (mL/s).>

Retain one of two subparagraphs below for rating methods.

14. AGA Output Capacity:  <Insert MBh (kW).>

15. DOE Output Capacity:  <Insert MBh (kW).>

Consider impact of site altitude on fan and motor.

16. Blower:

a. Motor Horsepower:  <Insert value.>

b. RPM:  <Insert value.>

17. Electrical Characteristics:

a. Volts:  [115] [208] [230] [460] <Insert value> V.

b. Phase:  [Single] [Three].

c. Hertz:  [50] [60].

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.5 MANUFACTURED UNITS

Retain this Article for water-jacketed condensing boilers.

A. Description:  Factory-fabricated, -assembled, and -tested, water-jacketed condensing boiler with heat exchanger sealed pressure tight, built on a steel base; including insulated jacket; flue-gas vent; water supply, return, and condensate drain connections; and controls.  Water heating service only.

B. Heat Exchanger:  Stainless-steel primary and secondary combustion chamber.

C. Pressure Vessel:  Carbon steel with welded heads and tube connections where not in contact with combustion or flue gases.

D. Burner:  [Natural] [Propane] gas, forced draft; swing-open front and burner observation port.

E. Blower:  Centrifugal fan, forced draft.  Include prepurge and postpurge of the combustion chamber.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If characteristics other than those in "Motors" Section are required, add subparagraphs below to suit Project.

1. Motors:  Comply with requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

a. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

F. Gas Train:  Combination gas valve with manual shutoff and pressure regulator.  Include 100 percent safety shutoff with electronic flame supervision.

G. Ignition:  Electric-spark ignition with 100 percent main-valve shutoff with electronic flame supervision.

H. Casing:

1. Jacket:  Sheet metal, with snap-in or interlocking closures.

2. Control Compartment Enclosures:  NEMA 250, Type 1A.

3. Finish:  Powder-coated protective finish.

4. Insulation:  Minimum 4-inch- (100-mm-) thick, mineral-fiber insulation surrounding the heat exchanger.

5. Combustion-Air Connections:  Inlet and vent duct collars.

6. Mounting base to secure boiler.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Manufacturer Seismic Qualification Certification" Paragraph in Part 1 "Submittals" Article.

a. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when mounting base is anchored to building structure.

If Project has more than one type or configuration of boiler, delete paragraph and subparagraphs below and schedule boilers on Drawings.

I. Characteristics and Capacities:

1. Heating Medium:  Hot water.

2. Design Water Pressure Rating:  [30 psig (207 kPa)] <Insert value>.

3. Safety Relief Valve Setting:  <Insert psig (kPa).>

4. Maximum Design Temperature:  210 deg F (99 deg C).

5. Entering-Water Temperature:  <Insert deg F (deg C).>

6. Leaving-Water Temperature:  <Insert deg F (deg C).>

7. Design Water Flow Rate:  <Insert gpm (L/s).>

8. Design Pressure Drop:  <Insert psig (kPa).>

Retain one of three subparagraphs below.  Specify standing or intermittent pilot with minimum AFUE.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1, Table 6.8.1F, "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

9. Minimum Efficiency AFUE:  <Insert value> percent.

10. Minimum Thermal Efficiency:  <Insert value> percent.

11. Minimum Combustion Efficiency:  <Insert value> percent.

Retain one of first two subparagraphs below.

12. AGA Input:  <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining subparagraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

13. Gas Input:  <Insert cfh (mL/s).>

Retain one of three subparagraphs below for rating methods.

14. AGA Output Capacity:  <Insert MBh (kW).>

15. DOE Output Capacity:  <Insert MBh (kW).>

16. Equivalent Direct Radiation:  <Insert EDR (W).>

Consider impact of site altitude on fan and motor.

17. Blower:

a. Motor Horsepower:  <Insert value.>

b. RPM:  <Insert value.>

18. Electrical Characteristics:

a. Volts:  [115] [208] [230] [460] <Insert value> V.

b. Phase:  [Single] [Three].

c. Hertz:  [50] [60].

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

Retain one of two "Trim" articles below.

2.6 TRIM

Retain this Article for hot-water boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 160 psig (1100 kPa) or boiler temperature exceeds 250 deg F (121 deg C).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain option in first paragraph below if using modulating or low-high-low firing sequence.

B. Aquastat Controllers:  Operating[, firing rate,] and high limit.

C. Safety Relief Valve:  ASME rated.

D. Pressure and Temperature Gage:  Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage.  Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

E. Boiler Air Vent:  [Automatic] [Manual].

F. Drain Valve:  Minimum NPS 3/4 (DN 20) hose-end gate valve.

Retain paragraph below if pump is a component of boiler.  Coordinate with Division 23 Section "Hydronic Pumps."

G. Circulation Pump:  Non-overloading, in-line pump with split-capacitor motor having thermal-overload protection and lubricated bearings; designed to operate at specified boiler pressures and temperatures.

2.7 TRIM

Retain this Article for steam boilers.

In paragraph below, retain first option if boiler operating pressure exceeds 15 psig (104 kPa).

A. Include devices sized to comply with [ANSI B31.1, "Power Piping] [ANSI B31.9, "Building Services Piping]."

Retain option in paragraph below if using modulating or low-high-low firing sequence.

B. Pressure Controllers:  Operating[, firing rate,] and high limit.

Retain first paragraph and subparagraphs below if safety valve is a component of boiler.  Coordinate with Division 23 Section "Steam and Condensate Heating Piping."

C. Safety Relief Valve:

1. Size and Capacity:  As required for equipment according to ASME Boiler and Pressure Vessel Code.

2. Description:  Fully enclosed steel spring with adjustable pressure range and positive shutoff; factory set and sealed.

a. Drip-Pan Elbow:  Cast iron and having threaded inlet and outlet with threads complying with ASME B1.20.1.

D. Pressure Gage:  Minimum 3-1/2-inch (89-mm) diameter.  Gage shall have normal operating pressure about 50 percent of full range.

E. Water Column:  Minimum 12-inch (300-mm) glass gage with shutoff cocks.

F. Drain Valves:  Minimum NPS 3/4 (DN 20) or nozzle size with hose-end connection.

In first paragraph below, retain option if boiler operating pressure exceeds 100 psig (690 kPa).

G. Blowdown Valves:  Factory-installed bottom and surface, slow-acting blowdown valves same size as boiler nozzle.[  Blowdown valves shall be combination of slow and quick acting as required by ANSI B31.1.]

H. Stop Valves:  Boiler inlets and outlets, except safety relief valves or preheater inlet and outlet, shall be equipped with stop valve in an accessible location as near as practical to boiler nozzle and same size or larger than nozzle.  Valves larger than NPS 2 (DN 50) shall have rising stem.

Retain paragraph below for boilers equipped with manhole openings that operate at more than 15 psig (104 kPa) and supply steam to a common steam header with other boilers.

I. Stop-Check Valves:  Factory-installed, stop-check valve and stop valve at boiler outlet with free-blow drain valve factory installed between the two valves and visible when operating stop-check valve.

2.8 CONTROLS

Retain paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC."

A. Refer to Division 23 Section "Instrumentation and Control for HVAC."

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers.  Coordinate with Division 23 Section "Instrumentation and Control for HVAC."

B. Boiler operating controls shall include the following devices and features:

1. Control transformer.

2. Set-Point Adjust:  Set points shall be adjustable.

Retain two subparagraphs below for steam boilers.

3. Operating Pressure Control:  Factory wired and mounted to cycle burner.

4. Low-Water Cutoff and Pump Control:  Cycle feedwater pump(s) for makeup water control.

Retain one of three subparagraphs below for operating control sequences.  Retain one of first two subparagraphs for hot-water boilers; or third, for steam boilers.

5. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

6. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature.  At [0 deg F (minus 17 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [200 deg F (93 deg C)] <Insert temperature>; at [60 deg F (15 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [140 deg F (60 deg C)] <Insert temperature>.

7. Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain a constant steam pressure.  Maintain pressure set point plus or minus 10 percent.

Retain subparagraph below with any of three "Sequence of Operation" subparagraphs above.

a. Include automatic, alternating-firing sequence for multiple boilers to ensure maximum system efficiency throughout the load range and to provide equal runtime for boilers.

C. Burner Operating Controls:  To maintain safe operating conditions, burner safety controls limit burner operation.

In subparagraph below, retain "temperature" option for hot-water boiler and "pressure" option for steam boiler.

1. High Cutoff:  [Manual] [Automatic] reset stops burner if operating conditions rise above maximum boiler design [temperature] [pressure].

In first subparagraph below, retain first option for hot-water boilers and second option for steam boilers.

2. Low-Water Cutoff Switch:  [Electronic] [Float and electronic] probe shall prevent burner operation on low water.  Cutoff switch shall be [manual] [automatic]-reset type.

3. Blocked Inlet Safety Switch:  Manual-reset pressure switch field mounted on boiler combustion-air inlet.

4. Audible Alarm:  Factory mounted on control panel with silence switch; shall sound alarm for above conditions.

Retain paragraph and subparagraphs below if boiler controls interface with building automation system.

D. Building Automation System Interface:  Factory install hardware and software to enable building automation system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required.  If extensive interface is required, delete below and retain second subparagraph below.

1. Hardwired Points:

a. Monitoring:  On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

b. Control:  On/off operation, [hot water supply temperature set-point adjustment] [steam pressure adjustment] <Insert control>.

Retain subparagraph below if extensive interface with building automation system is required and is beyond that than can be provided by hardwired points.  Requirement may exclude some manufacturers listed.

2. A communication interface with building automation system shall enable building automation system operator to remotely control and monitor the boiler from an operator workstation.  Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building automation system.

2.9 ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this Article.  Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

A. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 26 Sections.

B. Single-Point Field Power Connection:  Factory-installed and -wired switches, motor controllers, transformers, and other electrical devices necessary shall provide a single-point field power connection to boiler.

1. House in NEMA 250, Type [1] <Insert type> enclosure.

2. Wiring shall be numbered and color-coded to match wiring diagram.

3. Install factory wiring outside of an enclosure in a [metal ]raceway.

4. Field power interface shall be to [wire lugs] [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

5. Provide branch power circuit to each motor and to controls[ with a disconnect switch or circuit breaker].

6. Provide each motor with overcurrent protection.

2.10 VENTING KITS

Some boiler manufacturers offer venting kits that can be included with boiler.  Retain this Article if venting kit is included with boiler; otherwise, specify kit in Division 23 Section "Breechings, Chimneys, and Stacks."

A. Kit:  Complete system, ASTM A 959, Type 29-4C stainless steel, pipe, vent terminal, thimble, indoor plate, vent adapter, condensate trap and dilution tank, and sealant.

B. Combustion-Air Intake:  Complete system, stainless steel, pipe, vent terminal with screen, inlet air coupling, and sealant.

2.11 SOURCE QUALITY CONTROL

A. Burner and Hydrostatic Test:  Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency; perform hydrostatic test.

B. Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

Retain paragraph below if Owner wants to witness source quality-control testing.

C. Allow Owner access to source quality-control testing of boilers.  Notify Architect 14 days in advance of testing.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before boiler installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations, and piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

1. Final boiler locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

B. Examine mechanical spaces for suitable conditions where boilers will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 BOILER INSTALLATION

A. Install boilers level on concrete base.  Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

Retain first paragraph below for equipment supported on slabs-on-grade.  Coordinate selection of device and deflection below with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

B. Vibration Isolation:  Elastomeric [isolation pads] [mounts] with a minimum static deflection of [0.25 inch (6.35 mm)] <Insert deflection>.  Vibration isolation devices and installation requirements are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

C. Install gas-fired boilers according to NFPA 54.

D. Assemble and install boiler trim.

E. Install electrical devices furnished with boiler but not specified to be factory mounted.

F. Install control wiring to field-mounted electrical devices.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to boiler to allow service and maintenance.

C. Install piping from equipment drain connection to nearest floor drain.  Piping shall be at least full size of connection.  Provide an isolation valve if required.

D. Connect piping to boilers, except safety relief valve connections, with flexible connectors of materials suitable for service.  Flexible connectors and their installation are specified in Division 23 Section "Common Work Results for HVAC,"

E. Connect gas piping to boiler gas-train inlet with union.  Piping shall be at least full size of gas train connection.  Provide a reducer if required.

F. Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.

G. Connect steam and condensate piping to supply-, return-, and blowdown-boiler tappings with shutoff valve and union or flange at each connection.

H. Install piping from safety relief valves to nearest floor drain.

Retain paragraph above for hot-water boilers and first paragraph below for steam boilers.  Delete both if safety valves are specified in Division 23 Section "Steam and Condensate Heating Piping" or "Hydronic Piping."

I. Install piping from safety valves to drip-pan elbow and to nearest floor drain.

J. Boiler Venting:

1. Install flue venting kit and combustion-air intake.

Delete option in subparagraph below if vent kit is specified in this Section.

2. Connect full size to boiler connections.[  Comply with requirements in Division 23 Section "Breechings, Chimneys, and Stacks."]

K. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

L. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

1. Perform installation and startup checks according to manufacturer's written instructions.

2. Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

3. Operational Test:  Start units to confirm proper motor rotation and unit operation.  Adjust air-fuel ratio and combustion.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

a. Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level and [water temperature] [steam pressure].

b. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Remove and replace malfunctioning units and retest as specified above.

D. Occupancy Adjustments:  When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

Retain paragraph and subparagraphs below if performance tests are required.  Performance verification based on field tests is not typically required because of the associated cost.  Consult Owner.

E. Performance Tests:

1. Engage a factory-authorized service representative to inspect component assemblies and equipment installations, including connections, and to conduct performance testing.

2. Boilers shall comply with performance requirements indicated, as determined by field performance tests.  Adjust, modify, or replace equipment to comply.

3. Perform field performance tests to determine capacity and efficiency of boilers.

a. Test for full capacity.

b. Test for boiler efficiency at [low fire 20, 40, 60, 80, 100, 80, 60, 40, and 20] <Insert range> percent of full capacity.  Determine efficiency at each test point.

4. Repeat tests until results comply with requirements indicated.

5. Provide analysis equipment required to determine performance.

6. Provide temporary equipment and system modifications necessary to dissipate the heat produced during tests if building systems are not adequate.

7. Notify Architect in advance of test dates.

8. Document test results in a report and submit to Architect.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[  Video training sessions.] Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 235216

CONDENSING BOILERS
235216 - 1

