Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
06/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235313 - BOILER FEEDWATER PUMPS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Feedwater pumps and receivers.

2. Vacuum-type feedwater pumps and receivers.

1.3 DEFINITION

Retain this Article if abbreviation in paragraph below remains after this Section has been edited.

A. NPSH:  Net-positive suction head.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.  Include rated capacity, temperature and NPSH required, pump performance curves with selection points clearly indicated, and furnished specialties and accessories.

B. Shop Drawings:  Include plans, elevations, sections, details, dimensions, weights, loadings, required clearances, method of field assembly, and attachments to other work.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

C. Manufacturer Seismic Qualification Certification:  Submit certification that feedwater equipment, accessories, and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."  Include the following:

1. Basis of Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of internal and external parts during a seismic event."

b. The term "withstand" means "the unit will remain in place without separation of internal and external parts during a seismic event and the unit will be fully operational after the event."

2. Dimensioned Outline Drawings of Equipment:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which certification is based and their installation requirements.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For feedwater equipment to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Regulatory Requirements:  Fabricate and test unit according to ASME PTC 12.1, "Closed Feedwater Heaters."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. ASME Compliance:  [ASME B31.1, "Power Piping," for systems more than 15 psig (104 kPa)] [ASME B31.9, "Building Services Piping," for systems equal to or less than 15 psig (104 kPa)].  Safety valves and pressure vessels shall bear the appropriate ASME label.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Preparation for Shipping:  Clean flanges and exposed-metal surfaces and treat with anticorrosion compound after assembly and testing.  Protect flanges, pipe openings, and nozzles with wooden flange covers or with screwed-in plugs.

B. Store units in dry location.

C. Retain protective flange covers and machined-surface protective coatings during storage.

D. Protect bearings and couplings against damage from sand, grit, and other foreign matter.

E. Comply with manufacturer's written rigging instructions.

1.7 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

PART 2 -  PRODUCTS

2.1 FEEDWATER UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

If retaining first paragraph below, also retain "Capacities and Characteristics" Paragraph at the end of this Article.

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. AESYS Technologies, LLC; Boiler Div.

2. Alyan Pump.

3. Aurora Pump; Pentair Pump Group.

4. BFS Industries, LLC.

5. Bryan Boilers; Bryan Steam, LLC.

6. Cleaver-Brooks; Div. of Aqua-Chem, Inc.

7. Deaerating Designs; a division of Precision Boilers, Inc.

8. Domestic Pump; a unit of ITT Fluid Technology.

9. Eastern Industrial Products, Inc.; Smith-Koch, Inc. Div.

10. Flotronics, Inc.

11. Gerow Equipment Co.; Pump & Hydraulic Division.

12. Hurst Boiler & Welding Company, Inc.

13. Industrial Steam.

14. Lattner Boiler Manufacturing.

15. Lockwood Products, Inc.; Sub. of John L. Underwood Co., Inc.

16. MEPCO (Marshall Engineered Products Co.).

17. Parker Boiler Co.

18. PVI Industries, LLC.

19. Roth Pump Company; a subsidiary of Roy E. Roth Co.

20. Sellers Engineering Co.

21. Shippensburg Pump Co., Inc.

22. Skidmore.

23. Stickle Steam Specialties Co., Inc.

24. Superior Boiler Works, Inc.

25. U.S. Deaerator Co.

26. US Filter.

27. <Insert manufacturer's name.>

D. Description:  Factory-assembled and -tested unit consisting of a receiver, [simplex] [duplex] feedwater pumps, controls, and the following features and accessories:

1. [Liquid-filled industrial][Bimetal dial-type] thermometer graduated in [Fahrenheit] [Celsius] [both Fahrenheit and Celsius].

2. Level gage glass[, reflex flat type,] with stops at top and bottom.

3. Lifting eyes.

4. Companion flanges.

5. Pump, suction and discharge isolation valve, inlet strainer, discharge check valve, and liquid-filled pressure gage.

Coordinate first subparagraph below with sequence of operation.

6. Makeup Water Assembly:  [Float operated with integral valve] [Electric level controller and valve]; with inlet strainer and three-valve bypass.

7. Feedwater Heater:  Sparge tube, thermostat, and control valve.

8. Factory-Installed Pipe, NPS 2-1/2 (DN 65) and Smaller:  ASTM A 53/A 53M, Type S (seamless), Grade B; or ASTM A 106, Type S, Grade B, Schedule [40] [80]; with threaded joints and fittings.

Retain one or more of first five subparagraphs below.

a. Cast-Iron Threaded Fittings:  ASME B16.4; Class [125] [250].

b. Malleable-Iron Threaded Fittings:  ASME B16.3, Class [150] [300].

c. Forged-Steel Fittings:  ASME B16.11, Class 3000.

d. Malleable-Iron Unions:  ASME B16.39; Class [150] [300].

e. Forged-Steel Unions:  MSS SP-83, Class 3000.

9. Factory-Installed Pipe, NPS 3 (DN 80) and Larger:  ASTM A 53/A 53M, Type E (electric-resistance welded), Grade B; or ASTM A 106, Type S, Grade B, Schedule [40] [80]; with welded joints and carbon-steel fittings and flanges.

a. Wrought-Steel Fittings:  ASME B16.9, wall thickness to match adjoining pipe.

b. Wrought Cast- and Forged-Steel Flanges and Flanged Fittings:  ASME B16.5, Class [150] [300], including bolts, nuts, and gaskets.

E. Receiver:

If more than one feedwater unit is required, delete subparagraph below and indicate material in a schedule on Drawings.

1. Material:  [Close-grain cast iron] [Welded carbon steel] [Welded carbon steel galvanized after fabrication] [Stainless steel].

Retain subparagraph and associated subparagraphs below for carbon-steel tanks only.

2. Additional corrosion protection:

Retain one or both subparagraphs below.

a. [0.07-inch (1.8-mm)] [0.13-inch (3.3-mm)] [0.19-inch (4.8-mm)] <Insert thickness> thickness allowance.

b. Electrolytic corrosion-inhibitor anode.

Retain subparagraph below for cast-iron and carbon-steel receivers only.  First option is most common.

3. Finish:  [Primer] [Primer under enamel topcoat] [Primer under epoxy topcoat].

Factory-applied insulation is not available from all manufacturers listed.  Consult manufacturer.

4. Factory-Applied Insulation and Jacket:  Minimum thickness of [2 inches (50 mm)] <Insert thickness> for mineral-fiber pipe and tank insulation.  Cover insulation with [painted steel] [stucco-embossed aluminum] [stainless-steel] jacket.

If more than one feedwater unit is required, delete first subparagraph below and indicate mounting arrangement in a schedule on Drawings.

5. Mounting Arrangement:  [Recessed below floor] [Floor mounted].

6. Mounting Frame:  Structural-steel stand to support receiver and pumps.[  Fabricate stand with bracing adequate for seismic forces according to authorities having jurisdiction and to allow anchoring mounting frame to floor.]

Retain one of first two paragraphs and associated subparagraphs below and edit for desired pump construction.

F. Vertical Feedwater Pump:  Flange-mounted, close-coupled, [single-stage,] [multistage,] radially split-case-design centrifugal pump; rated for [175-psig (1205-kPa)] <Insert pressure> minimum working pressure and a continuous water temperature of at least [225 deg F (107 deg C)] <Insert temperature>; with the following features:

1. Impeller:  [Bronze] [Stainless steel].

2. Seals:  Mechanical.

Confirm availability of third option in subparagraph below with manufacturer for pump size and configuration selected.  Some pump configurations may exclude the third option and necessitate the second.

3. Motor:  [Open dripproof] [Totally enclosed] [Totally enclosed fan-cooled] enclosure.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

G. Horizontal Feedwater Pump:  Base-mounted, [single-stage,] [multistage,] radially split-case-design centrifugal pump; rated for [175-psig (1205-kPa)] <Insert pressure> minimum working pressure and a continuous water temperature of at least [225 deg F (107 deg C)] <Insert temperature>; with the following features:

1. Impeller:  [Bronze] [Stainless steel].

2. Coupling:  [Close] [Flexible].

3. Seals:  Mechanical.

Confirm availability of third option in subparagraph below with manufacturer for pump size and configuration selected.  Some pump configurations may exclude the third option and necessitate the second.

4. Motor:  [Open dripproof] [Totally enclosed] [Totally enclosed fan-cooled] enclosure.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

H. Control panel shall be unit mounted and factory wired and include the following:

Type 1 in subparagraph below is most common and a standard product offering.  Type 12 is second most common.  Type 4X is used primarily in corrosive environments.

1. NEMA 250, Type [1] [4] [4X] [12] <Insert type> enclosure.

Retain first subparagraph and associated subparagraph below for single-point field power connection to unit.

2. Single-point field power interface to [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

a. Branch power circuit to each motor and to controls[ with a disconnect switch or circuit breaker].

3. NEMA-rated motor controller for each motor, and include a hand-off-auto switch and overcurrent protection.

a. Alternating controls for duplex units with intermittent operation as indicated by control sequence.

4. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

5. Wiring outside of an enclosure in a [metal ]raceway.  Make connections to motor with liquidtight conduit.

6. Removable control mounting plate.

7. Visual indication of status and alarm[ with momentary test push button].

Retain first subparagraph below for audible alarm.  Coordinate with control sequence.

8. Audible alarm and silence switch.

9. Visual indication of elapsed run time, graduated in hours.

10. Fused control-circuit transformer.

Retain subparagraph below for nonstandard requirement.

11. Microprocessor-based controller.

Retain one of first three paragraphs and associated subparagraphs below.  Retain first for simplex feedwater system with single feedwater pump.  Retain second for duplex-pump units with operating and standby pump.  Retain third for duplex-pump units with continuous pump operation and modulating control valve.  Coordinate with boiler operation and controls.  See Evaluations for further discussion.

I. Feedwater Simplex-Pump Control Sequence:

1. Boiler water-level controller starts and stops pump to maintain boiler water-level set point.

2. Visual indication of pump on[ and off] status.

3. Visual[ and audible] alarm indication of pump failure.

J. Feedwater Duplex-Pump Control Sequence:

1. Boiler water-level controller starts and stops lead pump to maintain boiler water-level set point.

2. Lead and lag pumps alternate [after each start] [to equalize run time].

3. Lead pump failure, lag pump [automatically starts if lead pump cannot maintain set point] [ is started manually].

4. Visual indication of pump on[ and off] status.

5. Visual indication of pump lead/lag status.

6. Visual[ and audible] alarm indication of pump failure.

K. Feedwater Duplex-Pump Control Sequence:

1. Pump runs continuously while boiler operates.  Electric interlock with boiler control starts lead pump when boiler starts.

2. Boiler water-level controller modulates feedwater control valve to maintain boiler water-level set point.  Valve closes when boiler is off.

3. Lead and lag pumps alternate [after each start] [to equalize run time].

Retain one of first two subparagraphs below.

4. Lead pump failure automatically starts lag pump.

5. Feedwater pressure controller starts and stops lag pump to maintain feedwater pressure set point.

6. Visual indication of pump on[ and off] status.

7. Visual indication of pump lead/lag status.

8. Visual[ and audible] alarm indication of pump failure.

L. Receiver Makeup Water Control Sequence:

Retain one of first two subparagraphs below.

1. Electric level controller operates electric control valve to maintain receiver water-level set point.

2. Mechanical float operates integral valve to maintain water-level set point.

3. Visual[ and audible] alarm indication of low[ and high] receiver-water level.

Retain paragraph and subparagraph below if unit controls interface with building management system.

M. Building Management System Interface:  Factory install hardware to enable building management system to monitor and display points.

1. Hardwired Monitoring Points:  On/off status for each pump[, failure alarm for each pump] [, receiver low-water-level alarm] [, receiver high-water-level alarm] [, feedwater temperature] <Insert monitoring>.

If Project has more than one type or configuration of feedwater unit, delete paragraph and subparagraphs below and schedule feedwater units on Drawings.  If retaining below, retain "Basis-of-Design Product" Paragraph at the beginning of this Article and insert manufacturer's name and product name or designation there.

N. Capacities and Characteristics:

1. Condensate Receiver:

a. Volume:  <Insert gal. (L).>

Retain subparagraph above or first two subparagraphs below.

b. Diameter:  <Insert inches (mm).>

c. Length:  <Insert inches (mm).>

d. Height to Condensate Inlet:  <Insert inches (mm).>

e. Condensate Return Minimum Inlet Size:  <Insert NPS (DN).>

f. Makeup Water Minimum Inlet Size:  <Insert NPS (DN).>

g. Sparge-Tube Steam Supply:  <Insert lb/h (kW).>

2. Feedwater Pumps:

a. No. of Pumps:  [Simplex] [Duplex] <Insert number>.

b. Flow Rate:  <Insert gpm (L/s).>

c. NPSH Required:  <Insert psig (kPa).>

d. Rated Operating Temperature:  <Insert deg F (deg C).>

e. Head Pressure:  <Insert psig (kPa).>

f. Horsepower:  <Insert horsepower.>

g. Speed:  <Insert value> RPM.

h. Volts:  [115] [208] [230] [460] <Insert value> V.

i. Phase:  [Single] [Three].

j. Hertz:  60.

See Evaluations for discussion of feedwater unit with an integral vacuum producer.

2.2 FEEDWATER UNIT WITH VACUUM PRODUCER

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

If retaining first paragraph below, also retain "Capacities and Characteristics" Paragraph at the end of this Article.

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Alyan Pump.

2. Domestic Pump; a unit of ITT Fluid Technology.

3. Flotronics, Inc.

4. Lockwood Products, Inc.; Sub. of John L. Underwood Co., Inc.

5. MEPCO (Marshall Engineered Products Co.).

6. Shippensburg Pump Co., Inc.

7. Skidmore.

8. U.S. Deaerator Co.

9. <Insert manufacturer's name.>

D. Description:  Receiver mounted, consisting of multijet vacuum producer, centrifugal pump and motor assembly mounted on separation chamber, and automatic pressure and water temperature controls.  Include the following accessories:

1. [Liquid-filled industrial] [Bimetal dial-type] thermometer graduated in [Fahrenheit] [Celsius] [both Fahrenheit and Celsius].

2. Vacuum Gage:  Dial-type register in inches of mercury (kPa).

3. Level Gage Glass:  Stops top and bottom.

4. Air-suction check valve.

5. Lifting eyes.

6. Companion flanges.

7. Low-water cutoff switch.

8. Cooling-Water Control:  Aquastat, inlet strainer, and electric valve.

9. Air vent.

10. Overflow drain from vacuum-producer receiver.

11. Factory-Installed Pipe, NPS 2-1/2 (DN 65) and Smaller:  ASTM A 53/A 53M, Type S (seamless), Grade B; or ASTM A 106, Type S, Grade B, Schedule [40] [80]; with threaded joints and fittings.

Retain one or more of first five subparagraphs below.

a. Cast-Iron Threaded Fittings:  ASME B16.4; Class [125] [250].

b. Malleable-Iron Threaded Fittings:  ASME B16.3, Class [150] [300].

c. Forged-Steel Fittings:  ASME B16.11, Class 3000.

d. Malleable-Iron Unions:  ASME B16.39; Class [150] [300].

e. Forged-Steel Unions:  MSS SP-83, Class 3000.

12. Factory-Installed Pipe, NPS 3 (DN 80) and Larger:  ASTM A 53/A 53M, Type E (electric-resistance welded), Grade B; or ASTM A 106, Type S, Grade B, Schedule [40] [80]; with welded joints and carbon-steel fittings and flanges.

a. Wrought-Steel Fittings:  ASME B16.9, wall thickness to match adjoining pipe.

b. Wrought Cast- and Forged-Steel Flanges and Flanged Fittings:  ASME B16.5, Class [150] [300], including bolts, nuts, and gaskets.

E. Vacuum-Producer Reservoir and Vacuum Receiver:

If more than one feedwater unit is required, delete subparagraph below and indicate material in a schedule on Drawings.

1. Material:  [Close-grain cast iron] [Welded carbon steel] [Welded carbon steel galvanized after fabrication] [Stainless steel].

Retain subparagraph and associated subparagraphs below for carbon-steel tanks only.

2. Additional corrosion protection:

Retain one or both subparagraphs below.

a. [0.07-inch (1.8-mm)] [0.13-inch (3.3-mm)] [0.19-inch (4.8-mm)] <Insert thickness> thickness allowance.

b. Electrolytic corrosion-inhibitor anode.

Retain subparagraph below for cast-iron and carbon-steel receivers only.  First option is most common.

3. Finish:  [Primer] [Primer under enamel topcoat] [Primer under epoxy topcoat].

Factory-applied insulation is not available from all manufacturers listed.  Consult manufacturer.

4. Factory-Applied Insulation and Jacket:  Minimum thickness of [2 inches (50 mm)] <Insert thickness> for mineral-fiber pipe and tank insulation.  Cover insulation with [painted steel] [stucco-embossed aluminum] [stainless-steel] jacket.

If more than one feedwater unit is required, delete first subparagraph below and indicate mounting arrangement in a schedule on Drawings.

5. Mounting Arrangement:  [Recessed below floor] [Floor mounted].

6. Mounting Frame:  Structural-steel stand to support receiver and pumps.[ Fabricate stand with bracing adequate for seismic forces according to authorities having jurisdiction and to allow anchoring mounting frame to floor.]

Retain one of two paragraphs and associated subparagraphs below and edit for desired pump construction.

F. Vertical Vacuum-Producer Pump:  Flange-mounted, close-coupled, single-stage, radially split-case-design centrifugal pump; rated for [175-psig (1205-kPa)] <Insert pressure> minimum working pressure and a continuous water temperature of at least [225 deg F (107 deg C)] <Insert temperature>; with the following features:

1. Impeller:  Bronze.

2. Shaft:  Stainless steel.

3. Seals:  Mechanical.

Confirm availability of third option in subparagraph below with manufacturer for pump size and configuration selected.  Some pump configurations may exclude the third option and necessitate the second.

4. Motor:  [Open dripproof] [Totally enclosed] [Totally enclosed fan-cooled] enclosure.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

G. Horizontal Vacuum-Producer Pump:  Base-mounted, single-stage, radially split-case-design centrifugal pump; rated for [175-psig (1205-kPa)] <Insert pressure> minimum working pressure and a continuous water temperature of at least [225 deg F (107 deg C)] <Insert temperature>; with the following features:

1. Impeller:  Bronze.

2. Shaft:  Stainless steel.

3. Coupling:  [Close] [Flexible].

4. Seals:  Mechanical.

Confirm availability of third option in subparagraph below with manufacturer for pump size and configuration selected.  Some pump configurations may exclude the third option and necessitate the second.

5. Motor:  [Open dripproof] [Totally enclosed] [Totally enclosed fan-cooled] enclosure.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Retain one of first two paragraphs and associated subparagraphs below and edit for desired pump construction.

H. Vertical Feedwater Pump:  Flange-mounted, close-coupled, [single-stage,] [multistage,] radially split-case-design centrifugal pump; rated for [175-psig (1205-kPa)] <Insert pressure> minimum working pressure and a continuous water temperature of at least [225 deg F (107 deg C)] <Insert temperature>; with the following features:

1. Impeller:  [Bronze] [Stainless steel].

2. Seals:  Mechanical.

Confirm availability of third option in subparagraph below with manufacturer for pump size and configuration selected.  Some pump configurations may exclude the third option and necessitate the second.

3. Motor:  [Open dripproof] [Totally enclosed] [Totally enclosed fan-cooled] enclosure.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

I. Horizontal Feedwater Pump:  Base-mounted, [single-stage,] [multistage,] radially split-case-design centrifugal pump; rated for [175-psig (1205-kPa)] <Insert pressure> minimum working pressure and a continuous water temperature of at least [225 deg F (107 deg C)] <Insert temperature>; with the following features:

1. Impeller:  [Bronze] [Stainless steel].

2. Coupling:  [Close] [Flexible].

3. Seals:  Mechanical.

Confirm availability of third option in subparagraph below with manufacturer for pump size and configuration selected.  Some pump configurations may exclude the third option and necessitate the second.

4. Motor:  [Open dripproof] [Totally enclosed] [Totally enclosed fan-cooled] enclosure.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

J. Control panel shall be unit mounted and factory wired and include the following:

Retain one of two subparagraphs below.

1. Vacuum Switches for Simplex Vacuum-Producer Pumps:  Include pressure adjustment, and test push button.  Factory set to operate pump between 3 and 6 inches of mercury (10.1 and 20.2 kPa).

2. Vacuum Switches for Duplex Vacuum-Producer Pumps:  Include pressure adjustment, and test push button.  Factory set so one pump operates for 3 to 5 inches of mercury (10.1 to 16.9 kPa) and both pumps operate for 4 to 6 inches of mercury (13.5 to 20.2 kPa).

Type 1 in subparagraph below is most common and a standard product offering.  Type 12 is second most common.  Type 4X is used primarily in corrosive environments.

3. NEMA 250, Type [1] [4] [4X] [12] <Insert type> enclosure.

Retain first subparagraph and associated subparagraph below for single-point field power connection to unit.

4. Single-point field power interface to [fused disconnect switch] [nonfused disconnect switch] [circuit breaker].

a. Branch power circuit to each motor and to controls[ with a disconnect switch or circuit breaker].

5. NEMA-rated motor controller for each motor and include a hand-off-auto switch and overcurrent protection.

a. Alternating control for units with intermittent operation as indicated by control sequence.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Wiring outside of an enclosure in a [metal ]raceway.  Make connections to motor with liquidtight conduit.

8. Removable control mounting plate.

9. Visual indication of status and alarm[ with momentary test push button].

Retain first subparagraph below for audible alarm.  Coordinate with control sequence.

10. Audible alarm and silence switch.

11. Visual indication of elapsed run time, graduated in hours.

12. Fused control-circuit transformer.

K. Vacuum-Producer Control Sequence:

1. Cycle pumps to maintain vacuum-pressure set point.

2. Visual indication of pump on[ and off] status.

3. Visual[ and audible] alarm indication of pump failure.

Retain one of first three paragraphs and associated subparagraphs below.  Retain first for simplex feedwater system with single feedwater pump.  Retain second for duplex-pump units with operating and standby pump.  Retain third for duplex-pump units with continuous pump operation and modulating control valve.  Coordinate with boiler operation and controls.  See Evaluations for further discussion.

L. Feedwater Simplex-Pump Control Sequence:

1. Boiler water-level controller starts and stops pump to maintain boiler water-level set point.

2. Visual indication of pump on[ and off] status.

3. Visual[ and audible] alarm indication of pump failure.

M. Feedwater Duplex-Pump Control Sequence:

1. Boiler water-level controller starts and stops lead pump to maintain boiler water-level set point.

2. Lead and lag pumps alternate [after each start] [to equalize run time].

3. Lead pump failure, lag pump [automatically starts if lead pump cannot maintain set point] [ is started manually].

4. Visual indication of pump on[ and off] status.

5. Visual indication of pump lead/lag status.

6. Visual[ and audible] alarm indication of pump failure.

N. Feedwater Duplex-Pump Control Sequence:

1. Pump runs continuously while boiler operates.  Electric interlock with boiler control starts lead pump when boiler starts.

2. Boiler water-level controller modulates feedwater control valve to maintain boiler water-level set point.  Valve closes when boiler is off.

3. Lead and lag pumps alternate [after each start] [to equalize run time].

Retain one of first two subparagraphs below.

4. Lead pump failure automatically starts lag pump.

5. Feedwater pressure controller starts and stops lag pump to maintain feedwater pressure set point.

6. Visual indication of pump on[ and off] status.

7. Visual indication of pump lead/lag status.

8. Visual[ and audible] alarm indication of pump failure.

O. Makeup Water Control Sequence:

1. Electric level controller operates electric control valve to maintain water temperature set point.

2. Visual[ and audible] alarm indication of low[ and high] water level.

Retain paragraph and subparagraph below if unit controls interface with building management system.

P. Building Management System Interface:  Factory install hardware to enable building management system to monitor and display points.

1. Hardwired Monitoring Points:  On/off status for each pump[, failure alarm for each pump] [, receiver low-water-level alarm] [, receiver high-water-level alarm] [, feedwater temperature] <Insert monitoring>.

If Project has more than one type or configuration of unit, delete paragraph and subparagraphs below and schedule units on Drawings.  If retaining below, retain the "Basis-of-Design Product" Paragraph at the beginning of this Article and insert manufacturer's name and product name or designation there.

Q. Capacities and Characteristics:

1. Vacuum-Producer Reservoir:

a. Volume:  <Insert gal. (L).>

Retain subparagraph above or first two subparagraphs below.

b. Diameter:  <Insert inches (mm).>

c. Length:  <Insert inches (mm).>

d. Cooling Makeup Water Supply:  <Insert NPS (DN).>

e. Overflow Drain:  <Insert NPS (DN).>

2. Vacuum-Producer Pumps:

a. No. of Pumps:  [Simplex] [Duplex] <Insert number>.

b. Air Capacity:  <Insert cfm (L/s).>

c. Head Pressure:  <Insert inches of mercury (kPa).>

d. Horsepower:  <Insert horsepower.>

e. Speed:  <Insert value> RPM.

f. Volts:  [115] [208] [230] [460] <Insert value> V.

g. Phase:  [Single] [Three].

h. Hertz:  60.

3. Vacuum Receiver:

a. Volume:  <Insert gal. (L).>

Retain subparagraph above or first two subparagraphs below.

b. Diameter:  <Insert inches (mm).>

c. Length:  <Insert inches (mm).>

d. Height to Condensate Inlet:  <Insert inches (mm).>

e. Condensate Return Minimum Inlet Size:  <Insert NPS (DN).>

4. Feedwater Pumps:

a. No. of Pumps:  [Simplex] [Duplex] <Insert number>.

b. Flow Rate:  <Insert gpm (L/s).>

c. NPSH Required:  <Insert psig (kPa).>

d. Rated Operating Temperature:  <Insert deg F (deg C).>

e. Head Pressure:  <Insert psig (kPa).>

f. Horsepower:  <Insert horsepower.>

g. Speed:  <Insert value> RPM.

h. Volts:  [115] [208] [230] [460] <Insert value> V.

i. Phase:  [Single] [Three].

j. Hertz:  60.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before feedwater unit installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations, and piping and electrical connections to verify actual locations, sizes, and other conditions affecting feedwater unit performance, maintenance, and operations.

1. Final feedwater unit locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

2. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install feedwater unit level on concrete base.  Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

Coordinate selection of device and deflection in first paragraph below with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

B. Vibration Isolation:  Elastomeric [isolator pads] [mounts] with a minimum static deflection of [0.25 inch (6.35 mm)] <Insert deflection>.  Vibration isolation devices and installation requirements are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

C. Install unit to permit access for maintenance.

D. Support piping independent of pumps.

E. Install base-mounted pumps on concrete bases with grouted base frames.

F. Install parts and accessories shipped loose.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Connect makeup water piping and cooling-water piping with reduced-pressure backflow preventers.

D. Install overflow drain piping to nearest floor drain.

E. Install vents and extend to outdoors; terminate with elbow turned down and an insect screen.

3.4 FIELD QUALITY CONTROL

Retain one of two paragraphs below.  Retain first paragraph to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

C. Tests and Inspections:

1. Inspect field-assembled components, equipment installation, and piping and electrical connections for compliance with manufacturer's written instructions.

2. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

3. Check bearing lubrication.

4. Verify proper motor rotation.

5. Start up service.

6. Report results in writing.

D. Remove and replace malfunctioning units and retest as specified above.

3.5 ADJUSTING

A. Adjust boiler water-level controls to properly stage unit.

B. Set field-adjustable, makeup water and cooling-water controls.

3.6 CLEANING

A. Clean equipment internally; remove coatings applied for protection during shipping and storage, foreign material, and oily residue according to manufacturer's written instructions.

B. Clean strainers.

3.7 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain feedwater units.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 235313

	BOILER FEEDWATER PUMPS
	235313 - 1



