Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
06/04 (R 06/06)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 235523 - GAS-FIRED RADIANT HEATERS
If applying for LEED certification, LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.  ASHRAE/IESNA 90.1-2004, Section 6.5.8 - "Radiant Heating Systems," requires that radiant heat be used to heat unenclosed spaces except loading docks equipped with air curtains.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes gas-fired, [tubular infrared] [and] [high-intensity infrared] radiant heaters.

1.3 SUBMITTALS

A. Product Data:  For each type of gas-fired radiant heater indicated.  Include rated capacities, operating characteristics, and accessories.

In paragraph below, retain first option if equipment is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify equipment's compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

B. Shop Drawings:  [For gas-fired radiant heaters; signed and sealed by a qualified professional engineer.  Include] [For gas-fired radiant heaters.  Include] plans, elevations, sections, details, and attachments to other work.

1. Prepared by or under the supervision of a qualified professional engineer detailing fabrication and assembly of gas-fired radiant heaters, as well as procedures and diagrams.

2. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

3. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain option in subparagraph below if thermostat is specified in this Section; delete if thermostats for these units are specified in Division 23 Section "Instrumentation and Control for HVAC."

4. Wiring Diagrams:  Power[, signal, and control] wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Plans, elevations, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Structural members to which equipment will be attached.

2. Items penetrating roof and the following:

a. Vent and gas piping rough-ins and connections.

b. <Insert item.>

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

D. Manufacturer Seismic Qualification Certification:  Submit certification that gas-fired radiant heaters, accessories, and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For gas-fired radiant heaters to include in emergency, operation, and maintenance manuals.

G. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of gas-fired radiant heater that fails in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number in subparagraph below.

1. Warranty Period:  [Three] [Five] [10] <Insert number> years from date of Substantial Completion.

1.6 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraph below to suit Project.

1. Burner Igniters:  [One] <Insert number> hot-surface burner igniter(s) for each style of gas-fired radiant heater furnished.

PART 2 -  PRODUCTS

2.1 TUBULAR INFRARED HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Calcana Industries Ltd.

2. Combustion Research Corporation.

3. Gas-Fired Products Inc.; Space-Ray Div.

4. Reznor/Thomas & Betts Corporation.

5. Roberts-Gordon, Inc.

6. Schwank Inc.

7. Solaronics, Inc.

8. Sterling HVAC Products; Div. of Mestek Technology Inc.

9. <Insert manufacturer's name.>

D. Description:  Factory assembled, piped, and wired, and complying with ANSI Z83.20/CSA 2.34.

E. Fuel Type:  Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

Retain first paragraph below unless more than one type of tubing is required; in which case, delete below and indicate type of tubing in a schedule on Drawings.  See the sample schedule in the Evaluations.

F. Combustion Tubing:  4-inch- (100-mm-) diameter [stainless] [aluminized] steel with high-emissivity, high-temperature, corrosion-resistant external finish.

G. Tubing Connections:  Stainless-steel couplings or flared joints with stainless-steel draw bolts.

H. Reflector:  Polished aluminum, 97 percent minimum reflectivity, with end caps.  Shape to control radiation from tubing for uniform intensity at floor level with 100 percent cutoff above centerline of tubing.  Provide for rotating reflector or heater around a horizontal axis for minimum 30-degree (0.52-radian) tilt from vertical.

1. Reflector Extension Shields:  Same material as reflectors, arranged for fixed connection to lower reflector lip and rigid support to provide 100 percent cutoff of direct radiation from tubing at angles greater than 30 degrees (0.52 radians) from vertical.

2. Include hanger kit.

I. Burner Safety Controls:

1. Gas Control Valve:  Single-stage, regulated redundant 24-V ac gas valve containing pilot solenoid valve, electric gas valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff all in one body.

2. Blocked Vent Safety:  Differential pressure switch in burner safety circuit to stop burner operation with high discharge or suction pressure.

3. Control Panel Interlock:  Stops burner if panel is open.

4. Indicator Lights:  Burner-on indicator light.

Retain one of first three paragraphs and associated subparagraphs below, or revise to suit selected equipment.

J. Burner and Emitter Type:  Gravity-vented power burner, with the following features:

1. Emitter Tube:  4-inch- (100-mm-) diameter, [aluminized] [hot-rolled]-steel tubing with sight glass for burner and pilot flame observation.

2. Venting:  [Unvented] [Connector at exit end of emitter tubing for vent-pipe connection] [Concentric vent for combustion air and flue gas with rain cap for both].

a. Vent Terminal:  [Vertical] [Horizontal].

Retain one of two subparagraphs below or revise to suit selected equipment.

3. Burner/Ignition:  Power gas burner with electronic spark and electronic flame safety.

4. Burner/Ignition:  Stainless-steel burner cup and head with balanced-rotor draft fan and [direct-sensing, hot-surface ignition] [spark ignition with electronic flame supervision].

Subparagraph below is an optional feature.

5. Combustion-Air Connection:  Duct connection for combustion air to be drawn directly from outdoors by burner fan.

K. Burner and Emitter Type:  Vacuum-vented burner, with the following features:

1. Emitter Tube:  4-inch- (100-mm-) diameter, [aluminized] [hot-rolled]-steel tubing with sight glass for burner and pilot flame observation.

2. Burner/Ignition:  Electronic spark and electronic flame safety.

Retain one of first two subparagraphs below or revise to suit selected equipment.

a. Venting:  Burner exhaust tubing connected at exit end to vacuum-fan inlet.

b. Venting:  Balancing damper at exit end of burner exhaust tubing and at connection to manifold tube.

3. Vacuum Fan:  Dynamically balanced, direct-driven, [cast-aluminum-alloy] [stainless-steel] impeller in an aluminized-steel housing, isolated from system by flexible connector with a minimum temperature rating of 450 deg F (232 deg C).

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

a. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1) Motor:  Resilient-mounted, capacitor-start-capacitor-run type with sealed ball bearings; totally enclosed, nonventilated type with internal thermal protection.

2) Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

3) Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 26 Sections.

Retain one or more of four optional accessories below.

4. Balancing Dampers:  Plate type, mounted in cast, double-flange fitting with vacuum test plug.

5. Filter:  Cartridge type for mounting on burner housing.

6. Combustion-Air Connection:  Duct connection to burner for combustion air to be drawn directly from outside.

7. Outdoor-Air Connection:  Dynamically balanced, direct-driven, forward-curved fan with duct connection to each burner.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

a. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1) Motor:  Resilient-mounted, capacitor-start-capacitor-run type, thermally protected with sealed ball bearings.

2) Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

3) Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 26 Sections.

L. Burner and Emitter Type:  Vacuum vented, condensing, with multiple atmospheric burners and provision for condensation of combustion products in venting manifold tubing.

1. Emitter Tube:  4-inch- (100-mm-) diameter, [aluminized] [hot-rolled] [porcelain-lined]-steel tubing with sight glass for burner and pilot flame observation.

2. Burner/Ignition:  Electronic spark and electronic flame safety.

3. Vacuum Fan:  Dynamically balanced, direct-driven, [cast-aluminum-alloy] [stainless-steel] impeller in an aluminized-steel housing, isolated from system by flexible connector with a minimum temperature rating of 450 deg F (232 deg C).

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

a. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1) Motor:  Resilient-mounted, capacitor-start-capacitor-run type, thermally protected with sealed ball bearings.

2) Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

3) Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 26 Sections.

Retain one or more of three optional accessories below.

4. Balancing Dampers:  Plate type, mounted in cast, double-flange fitting with vacuum test plug.

5. Filter:  Cartridge type for mounting on burner housing.

6. Outdoor-Air Connection:  Dynamically balanced, direct-driven, forward-curved fan with duct connection to each burner.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

a. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1) Motor:  Resilient-mounted, capacitor-start-capacitor-run type, thermally protected with sealed ball bearings.

2) Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

3) Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 26 Sections.

M. Capacities and Characteristics:

1. Gas Input:  <Insert Btu/h (kW).>

2. Gas Output:  <Insert Btu/h (kW).>

3. Fuel Supply Connection:  <Insert inches (mm).>

4. Vacuum Motor Size:  <Insert horsepower.>

a. Volts:  [120] [208] [230] <Insert value> V.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

5. Outdoor-Air Motor Size:  <Insert horsepower.>

a. Volts:  [120] [208] [230] <Insert value> V.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert amperage.>

2.2 HIGH-INTENSITY INFRARED HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Combustion Research Corporation.

2. Gas-Fired Products Inc.; Space-Ray Div.

3. Panelbloc, Inc.

4. Reznor/Thomas & Betts Corporation.

5. Roberts-Gordon, Inc.

6. Schwank Inc.

7. Solaronics, Inc.

8. Sterling HVAC Products; Div. of Mestek Technology Inc.

9. <Insert manufacturer's name.>

D. Description:  Factory assembled, piped, and wired, and complying with ANSI Z83.19A/CSA 2.35A, "Gas-Fired, High-Intensity Infrared Heaters."

E. Fuel Type:  Design burner for [natural] [propane] gas having characteristics same as those of gas available at Project site.

F. Burner:  Aluminized-steel plenum chamber with stainless-steel retainers and direct spark ignition.

G. Emitter:  Ceramic combustion surface.

H. Reflector:  Polished aluminum.

I. Accessories:

1. Parabolic reflector.

2. Wire grid for increased efficiency.

3. Protective screen.

4. Heat-deflector shield.

5. Stainless-steel flexible connector with manual valve.

6. Hanger chain with "S" hooks.

7. Preassembled chain suspension kit.

J. Capacities and Characteristics:

1. Gas Input:  <Insert Btu/h (kW).>

2. Gas Output:  <Insert Btu/h (kW).>

3. Fuel Supply Connection:  <Insert inches (mm).>

2.3 CONTROLS

A. Thermostat:  Devices and wiring are specified in Division 23 Section "Instrumentation and Control for HVAC."

Retain one of two paragraphs below or revise to suit selected equipment.  Delete if thermostat is specified in Division 23 Section "Instrumentation and Control for HVAC."

B. Thermostat:  Single-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

C. Thermostat:  2-stage, wall-mounting type with 50 to 90 deg F (10 to 32 deg C) operating range and fan on switch.

Retain subparagraph below with either paragraph above.

1. Control Transformer:  Integrally mounted.

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain first option in first paragraph below for projects in the U.S.; retain second option for projects in Canada.

A. Install and connect gas-fired radiant heaters and associated fuel and vent features and systems according to [NFPA 54] [CAN/CSA B149.1], applicable local codes and regulations, and manufacturer's written installation instructions.

B. Suspended Units:  Suspend from substrate using chain hanger kits and building attachments.

1. Spring hangers[ and seismic restraints] are specified in Division 23 Section "Hangers and Supports for HVAC Piping and Equipment[."] [" and "Vibration and Seismic Controls for HVAC Piping and Equipment."]

Delete subparagraph below if Project site is aseismic.

2. Restrain the unit to resist code-required horizontal acceleration.  Seismic restraints are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

C. Maintain manufacturers' recommended clearances to combustibles.

3.2 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to gas-fired radiant heaters to allow service and maintenance.

C. Gas Piping:  Comply with Division 23 Section "[Facility Natural-Gas Piping] [Facility Liquefied-Petroleum Gas Piping]." Connect gas piping to gas train inlet; provide union with enough clearance for burner removal and service.

D. Vent Connections:  Comply with Division 23 Section "Breechings, Chimneys, and Stacks."

E. Electrical Connections:  Comply with applicable requirements in Division 26 Sections.

1. Install electrical devices furnished with heaters but not specified to be factory mounted.

3.3 FIELD QUALITY CONTROL

Retain one of first two paragraphs below.  Retain first to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph and subparagraphs below to describe tests and inspections to be performed by either entity in two paragraphs above.

C. Tests and Inspections:

1. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

2. Verify bearing lubrication.

3. Verify proper motor rotation.

4. Test Reports:  Prepare a written report to record the following:

a. Test procedures used.

b. Test results that comply with requirements.

c. Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

D. Remove and replace malfunctioning units and retest as specified above.

3.4 ADJUSTING

A. Adjust initial temperature set points.

B. Adjust burner and other unit components for optimum heating performance and efficiency.

3.5 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain gas-fired radiant heaters.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 235523

GAS-FIRED RADIANT HEATERS
235523 - 1

