Copyright 2002 and 2005 AIA
MASTERSPEC Full Length
03/02 (R 06/06)

Copyright 2002 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 236313 - AIR-COOLED REFRIGERANT CONDENSERS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes packaged, air-cooled condensers for [outdoor] [indoor] installation.

1.3 SUBMITTALS

A. Product Data:  For each air-cooled condenser, include rated capacities, operating characteristics, furnished specialties, and accessories.  Include equipment dimensions, weights and structural loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain paragraph and subparagraphs below if air-cooled condensers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify air-cooled condensers' compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

B. Shop Drawings:  Signed and sealed by a qualified professional engineer.

1. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

2. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails and equipment mounting frames.

3. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Schematic drawing, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Structural members to which air-cooled condensers will be attached.

2. Liquid and vapor pipe sizes.

3. Refrigerant specialties.

4. Piping including connections, oil traps, and double risers.

5. Compressors.

6. Evaporators.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

D. Manufacturer Seismic Qualification Certification:  Submit certification that air-cooled condensers, accessories, and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

E. Field quality-control test reports.

F. Operation and Maintenance Data:  For air-cooled condensers to include in emergency, operation, and maintenance manuals.

G. LEED Submittal:

Retain subparagraph below for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

1. Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment and refrigerants comply.

1.4 QUALITY ASSURANCE

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 01 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of air-cooled condensers and are based on the specific system indicated.  Refer to Division 01 Section "Product Requirements."

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Fabricate and label refrigeration system according to ASHRAE 15, "Safety Code for Mechanical Refrigeration."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

D. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

B. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

C. Coordinate location of refrigerant piping and electrical roughins.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Bohn Refrigeration Products; Heatcraft, Inc.

2. Carrier Corporation; Carrier Air Conditioning Div.

3. Colmac Coil Manufacturing, Inc.

4. Coolenheat Inc.

5. Dunham-Bush, Inc.

6. Engineered Air.

7. McQuay International.

8. Trane Co. (The); Worldwide Applied Systems Group.

9. York International Corp.

10. USA Coil & Air Inc.

11. <Insert manufacturer's name.>

2.2 MANUFACTURED UNITS

A. Description:  Factory assembled and tested; consisting of casing, condenser coils, condenser fans and motors, and unit controls.

B. Condenser Coil:  Seamless copper-tube, finned coil; factory tested at 425 psig (2930 kPa).

1. Coil Fin:  [Aluminum] [Copper].

Retain first subparagraph below if coating is required.

2. Coil Coating:  <Insert coating required.>

3. Circuit:  To match compressors[ with liquid subcooling coil].

Accessories in subparagraph below are usually optional.

4. Refrigerant Accessories:  Provide receiver, pressure control, and solenoid valve for each circuit.

C. Condenser Fans and Drives:  Propeller fans with [aluminum or galvanized-steel] [galvanized-steel] [stainless-steel] fan blades, for [vertical] [horizontal] air discharge; directly driven with permanently lubricated ballbearing motors with integral current- and thermal-overload protection.

Retain paragraph above or first paragraph and subparagraphs below for fan type.

D. Condenser Fans and Drives:  Forward-curved centrifugal fans for [vertical] [horizontal] air discharge.

1. Fan on steel shaft with self-aligning ball bearings.

2. V-belt drive with minimum of two belts; variable pitch drive pulley.

3. Motor mounted on adjustable slide base.

E. Operating and Safety Controls:  Include condenser fan motor thermal and overload cutouts; 115-V control transformer, if required; magnetic contactors for condenser fan motors and a nonfused factory-mounted and -wired disconnect switch for single external electrical power connection.

F. Unit Casings:  [Galvanized or zinc-coated steel treated and finished with manufacturer's standard paint coating] [Stainless steel], designed for [outdoor installation with weather protection for components and controls] [indoor installation], and with the following:

1. Removable panels for access to controls, condenser fans, motors, and drives.

Accessories listed below are for propeller fan, outdoor units.

2. [Plated] [Stainless]-steel fan guards.

3. Lifting eyes.

4. Removable legs.

Accessory below is for centrifugal fan, indoor units.

5. 1-inch- (25-mm-) thick inlet filter.

2.3 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add paragraphs below to suit Project.

A. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

2. Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 26 Sections.

2.4 SOURCE QUALITY CONTROL

A. Verification of Performance:  Rate air-cooled condensers according to ARI 460.

B. Testing Requirements:  Factory test sound-power-level ratings according to ARI 270.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of air-cooled condensers.

B. Examine roughing-in for refrigerant piping systems to verify actual locations of piping connections before equipment installation.

C. Examine walls, floors, and roofs for suitable conditions where air-cooled condensers will be installed.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install units level and plumb, firmly anchored in locations indicated; maintain manufacturer's recommended clearances.

Retain first two paragraphs and associated subparagraphs below for air-cooled condensers mounted on grade.

B. Install air-cooled condensers on concrete base.  Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

Retain paragraph and subparagraphs below based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.  Delete if retaining vibration isolation equipment bases.

C. Concrete Bases:

1. Install dowel rods to connect concrete base to concrete slab.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of the base.

2. For equipment supported on structural slab, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Install anchor bolts according to anchor-bolt manufacturer's written instructions.

Retain paragraph below and delete two paragraphs and associated subparagraphs above if units are installed on roof.

D. Install roof-mounting units on equipment supports specified in Division 07.

Retain one of two paragraphs below.  Coordinate with Drawings and Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Retain first paragraph for equipment supported on slabs-on-grade.  Delete both paragraphs if vibration and seismic controls are scheduled on Drawings.

E. Vibration Isolation:  Mount air-cooled condensers on rubber pads with a minimum deflection of [1/4 inch (6.35 mm)] <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Based on supporting structure and seismic requirements, insert amount of required deflection in paragraph below.

F. Vibration Isolation:  Mount air-cooled condensers on restrained spring isolators with a minimum deflection of <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Retain one of first two paragraphs and associated subparagraph below for suspended units.

Delete first paragraph and subparagraph if vibration and seismic controls are scheduled on Drawings.  If not scheduled, identify required vibration- and seismic-control device by using the titles of devices described in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."and identify its required static deflection.

G. Support suspended units from structure using threaded steel rods and [spring hangers] <Insert other vibration isolators> having a static deflection of [1 inch (25 mm)] <Insert other deflection>.  Vibration- and seismic-control devices are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Secure vibration and seismic controls, and suspended units to structure.

H. Support suspended units from structure using threaded steel rods.

I. Maintain manufacturer's recommended clearances for service and maintenance.

J. Loose Components:  Install electrical components, devices, and accessories that are not factory mounted.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to machine to allow service and maintenance.

C. Refrigerant Piping:  Connect piping to unit with pressure relief, service valve, filter-dryer, and moisture indicator on each refrigerant-circuit liquid line.  Refrigerant piping and specialties are specified in Division 23 Section "Refrigerant Piping."

3.4 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. Perform electrical test and visual and mechanical inspection.

2. Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.  Complete manufacturer's starting checklist.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

5. Verify proper airflow over coils.

B. Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

C. Remove and replace malfunctioning air-cooled condensers and retest as specified above.

3.5 STARTUP SERVICE

A. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Inspect for physical damage to unit casing.

2. Verify that access doors move freely and are weathertight.

3. Clean units and inspect for construction debris.

4. Verify that all bolts and screws are tight.

5. Adjust vibration isolation and flexible connections.

6. Verify that controls are connected and operational.

B. Lubricate bearings on fans.

C. Verify that fan wheel is rotating in the correct direction and is not vibrating or binding.

D. Start unit according to manufacturer's written instructions and complete manufacturer's startup checklist.

E. Measure and record airflow over coils.

F. Verify proper operation of capacity control device.

G. Verify that vibration isolation and flexible connections properly dampen vibration transmission to structure.

H. After startup and performance test, lubricate bearings.

3.6 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain air-cooled condensers.

END OF SECTION 236313

AIR-COOLED REFRIGERANT CONDENSERS
236313 - 1

