Copyright 2000 and 2005 AIA
MASTERSPEC Full Length
12/00 (R 06/06)

Copyright 2000 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 236333 - EVAPORATIVE REFRIGERANT CONDENSERS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes factory-assembled and -tested, [induced] [forced]-draft evaporative condensers.

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, pressure drop, fan performance data, installation instructions, furnished specialties, and accessories.

Retain paragraph and subparagraphs below if evaporative condensers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

B. Shop Drawings:  Signed and sealed by a qualified professional engineer.

1. Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

2. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include handrails, ladders, and equipment mounting frame.

3. Detail equipment assemblies and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field piping and wiring connection.

4. Wiring Diagrams:  Power, signal, and control wiring.

Retain paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Plans, elevations, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

1. Structural supports.

2. Piping and wiring roughing-in requirements (determine spaces reserved for electrical equipment).

3. Access requirements for service and maintenance.

Retain first paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

D. Manufacturer Seismic Qualification Certification:  Submit certification that evaporative condensers, accessories, and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

E. Operation and Maintenance Data:  For evaporative condensers to include in emergency, operation, and maintenance manuals.

F. Warranties:  Special warranties specified in this Section.

G. LEED Submittal:

Retain subparagraph below for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

1. Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment and refrigerants comply.

1.4 QUALITY ASSURANCE

A. Product Options:  Information on Drawings and in Specifications establishes requirements for system's aesthetic effects and performance characteristics.  Aesthetic effects are indicated by dimensions, arrangements, alignment, and profiles of components and assemblies as they relate to sightlines, to one another, and to adjoining construction.  Performance characteristics are indicated by criteria subject to verification by one or more methods including preconstruction testing, field testing, and in-service performance.

Retain paragraph above or first paragraph below.  Retain below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 01 requirements.

B. Product Options:  Drawings indicate size, profiles, and dimensional requirements of evaporative condensers and are based on the specific system indicated.  Refer to Division 01 Section "Product Requirements."

Retain subparagraph below with either "Product Options" Paragraph above or revise to suit Project.

1. Do not modify intended aesthetic effects, as judged solely by Architect, except with Architect's approval.  If modifications are proposed, submit comprehensive explanatory data to Architect for review.

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

D. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

Retain first paragraph below if Owner prefers the security of a coil designed and fabricated according to ASME Boiler and Pressure Vessel Code or where state or local codes require it.

E. ASME Compliance:  Fabricate and label heat-exchange coils to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

F. Comply with NFPA 70.

1.5 COORDINATION

A. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

B. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace the following components of evaporative condensers that fail in materials or workmanship within specified warranty period:

1. Fan, motor, drive shaft, bearings, and motor supports.

2. Tube bundle.

3. External-circuit circulating pump.

4. <Insert other components requiring extended warranty.>

Verify available warranties for units and components and insert number below.

5. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Baltimore Aircoil Company.

2. Recold.

3. <Insert manufacturer's name.>

2.2 MANUFACTURED UNITS

A. Description:  Factory-assembled and -tested, [induced] [forced]-draft evaporative condensers.

Retain first paragraph below for projects in seismic areas.

B. Fabricate evaporative condenser mounting frame and attachments with reinforcement strong enough to resist evaporative condenser movement during a seismic event when evaporative condenser mounting frame is attached to the building structure.

C. Evaporative Condenser Characteristics and Capacities:

1. Cooling Capacity:  <Insert Btuh (kW).>

2. Internal Circuit:

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second, third, or fourth option in first subparagraph or retain second subparagraph to comply with Credit EA 4.

a. Refrigerant Type:  [R-22] [R-407C] [R-410A] [HFC-134a] <Insert type.>

b. Refrigerant:  R-407C or R-410A.

c. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C).>

d. Condensing Temperature:  <Insert deg F (deg C).>

e. Minimum Heat Rejection:  <Insert Btuh (kW).>

3. External-Circuit [Water] [Glycol] Flow:  <Insert gpm (L/s).>

4. Maximum Drift Loss:  <Insert number> percent of external-circuit flow.

5. External-Circuit Circulating Pump Motor Electrical Characteristics:  [240] [480] <Insert other>-V ac, 3 phase, 60 Hz.

6. Number of Fans:  [One] [Two] <Insert number>.

7. Fan Motor Electrical Characteristics:  [240] [480] <Insert other>-V ac, 3 phase, 60 Hz.

8. Noise Rating:  <Insert dBA> at <Insert distance in feet (m)>.

9. Basin Heater:  Maintain 40 deg F (4 deg C) external-circuit-[water] [glycol] temperature at 0 deg F (minus 18 deg C) outside-air temperature.

2.3 MATERIALS

Retain one of first two paragraphs below.

A. Casing Material:  Galvanized sheet steel complying with ASTM A 653/A 653M, [G210 (Z600)] [G235 (Z700)] coating designation.

Retain paragraph above or first paragraph below.

B. Casing Material:  Stainless steel.

Retain four subparagraphs below with either paragraph above.

1. Fasteners:  Corrosion resistance equal to or better than materials being fastened.

2. Joints:  Sealed watertight.

3. Welded Connections:  Continuous and watertight.

4. Rigging Supports:  For handling evaporative condensers at construction site.

C. Collection Basin Material:  Galvanized sheet steel complying with ASTM A 653/A 653M, [G210 (Z600)] [G235 (Z700)] coating designation.

Retain paragraph above or first paragraph below.

D. Collection Basin Material:  Stainless steel.

Retain four subparagraphs below with either of last two paragraphs above.

1. Removable strainer with openings smaller than nozzle orifices.

2. Overflow connection.

3. Makeup water connection.

4. Drain Connection:  [Oversized for use with remote sump] [Side] [Bottom].

E. Tube Bundle Material and Construction:  [Carbon-steel, hot-dip galvanized after fabrication,] [Copper] [Stainless-steel] serpentine tubes designed for low pressure drop and free drainage of refrigerant; factory tested at 350-psig (2400-kPa) air pressure while underwater.

Retain one of four subparagraphs below.  Note that coil selection might eliminate one or more vendors.

1. ASME Coil:  Comply with requirements in ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, and bear the ASME "U" stamp.

2. Multiple-circuit coil.

3. Subcooling Coil:  [Plus 10 deg F (Minus 12 deg C)] <Insert deg F (deg C)>.

4. Extended-surface coil.

Retain one of first three paragraphs below if required.

F. Drift Eliminator Material:  PVC with maximum flame-spread index of 5 according to ASTM E 84.

G. Drift Eliminator Material:  Galvanized sheet steel complying with ASTM A 653/A 653M, [G210 (Z600)] [G235 (Z700)] coating designation[ with polymer coating].

H. Drift Eliminator Material:  Stainless steel.

I. External-Water Distribution System:  Header pipe and removable branch pipes for even distribution of water over the coil.

1. Pipe Material:  Schedule [40, galvanized steel] [40, PVC] [80, PVC].

2. Nozzles:  Removable plastic or brass with a maximum pressure drop of 12 psig (83 kPa) <Insert psig (kPa)>.

3. Hot-Water-Basin Control Valves:  Manufacturer's standard butterfly or globe valves arranged to balance flow to each distribution basin and shut flow off during servicing.

Retain one of three paragraphs below.

J. Inlet Screen Material:  Galvanized-steel mesh mounted in removable frames.

K. Inlet Screen Material:  Hot-dip galvanized-steel mesh with polymer coating, mounted in removable frames.

L. Inlet Screen Material:  Stainless-steel mesh mounted in removable frames.

Retain one of two paragraphs below if discharge hoods are required.

M. Draft Hood Material:  Galvanized steel according to ASTM A 653/A 653M, [G210 (Z600)] [G235 (Z700)] coating designation[ with polymer coating].

N. Draft Hood Material:  Stainless steel with access door.

2.4 COMPONENTS

Retain one of first three paragraphs below if makeup water valve is supplied with evaporative condenser.  Mechanical makeup water valve in first paragraph is most common.

A. Water-Level Control:  Manufacturer's standard mechanical makeup water valve and plastic or bronze float with an adjustable linkage.

B. Water-Level Control:  Electric float switch; characteristics coordinated with solenoid-operated, makeup water valve.

C. Water-Level Control:  Electric float switch and solenoid-operated, makeup water valve.

D. Fan(s):  [Galvanized steel, propeller] [Cast aluminum, propeller] [Galvanized steel, centrifugal].

1. Drive:  Direct or belt.

2. Bearings:  Self-aligning ball bearings or bronze sleeve bearings with lubrication lines and fittings.

Vibration switches are optional.  Retain subparagraph below if required.

3. Vibration Cutout Switch:  Solid state, with adjustable time delay and NEMA 250, Type 4 enclosure.

E. External-Circuit Circulating Pump:  Close-coupled, end-suction, single-stage, bronze-fitted, mechanical seal, centrifugal pump; with a totally enclosed, fan-cooled motor; and suitable for outdoor service.

Retain fan-discharge dampers in first paragraph below for centrifugal fans if required.

F. Capacity-Control Dampers:  Galvanized-steel, fan-discharge dampers, with linkages, electric damper operator, controller, end switches, transformer, and weatherproof enclosure.  Reset dampers to vary airflow through evaporative condenser to control leaving condenser-water temperature.

G. Basin Heater:  [Steam injector] [Steam coil] [Hot-water coil] [Electric-resistance coil].

2.5 MOTORS

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add paragraphs below to suit Project.

A. Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

See Evaluations for discussion on enclosure types for various applications.  Retain first paragraph below if enclosure is not open-dripproof type.

B. Enclosure Type:  [Totally enclosed, fan cooled] [Totally enclosed, air over].

C. Motor Speed:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Inverter type for variable-speed controller].

2.6 HANDRAILS, LADDERS, AND PLATFORMS

Requirements for handrails, ladders, and platforms for evaporative condensers depend on condenser height and accessibility of maintenance items.  Edit this Article accordingly.

A. Handrails:  Galvanized steel or aluminum complying with 29 CFR 1910.23.  Pipe-rail materials and fabrication are specified in Division 05 Section "Pipe and Tube Railings."

B. Ladders and Safety Cages:  Galvanized steel or aluminum complying with 29 CFR 1910.27.

C. Platforms:  Galvanized steel with a bar grating floor.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in for concrete bases, anchor-bolt sizes and locations, piping, and electrical to verify actual locations and sizes before evaporative condenser installation and other conditions affecting evaporative condenser performance, maintenance, and operation.

1. Final evaporative condenser locations indicated are approximate.  Determine exact locations before roughing-in water piping and electrical connections.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain first two paragraphs and associated subparagraphs below for evaporative condensers mounted on grade.

A. Install evaporative condensers on concrete bases.  Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

Retain paragraph and subparagraphs below based on installed equipment.  Indicate dowel rod quantity, size, and spacing on Drawings if evaporative condensers are mounted on vibration isolators.  Delete if retaining vibration isolation equipment bases.

B. Concrete Bases:  Anchor evaporative condenser to concrete base.

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of the base.

2. For equipment supported on structural slab, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

5. Install anchor bolts according to anchor-bolt manufacturer's written instructions.

6. Cast-in-place concrete materials and placement requirements are specified in Division 03.

Retain one of first four paragraphs below.  Coordinate with Drawings and Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Retain first paragraph for equipment supported on slabs-on-grade.

C. Vibration Isolation:  Rubber pads with a minimum deflection of [0.25 inch (6.35 mm)] <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

D. Vibration Isolation:  Install evaporative condensers with spring isolators per manufacturer's written recommendation.

Based on supporting structure and seismic requirements, insert amount of required deflection in paragraph below.

E. Vibration Isolation:  Restrained spring isolators with a minimum deflection of <Insert measurement>.  Vibration isolation devices and installation requirements are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

If retaining first paragraph below, delete "Concrete Bases" Paragraph and subparagraphs above.

F. Vibration Isolation:  Mount evaporative condensers on a vibration isolation equipment base as specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

G. Maintain manufacturer's recommended clearances for service and maintenance.

H. Loose Equipment:  Install electrical components, devices, and accessories that are not factory mounted.

3.3 CONNECTIONS

Coordinate piping installation and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to evaporative condensers to allow service and maintenance.

C. Install flexible pipe connectors at final connection of evaporative condensers mounted on vibration isolators.

D. Connect overflow drain and bleed lines to sanitary sewage system.

E. Domestic Water Piping:  Comply with applicable requirements in Division 22 Section "Domestic Water Piping." Connect to water-level control with shutoff valve and union or flange at each connection.

F. Refrigerant Piping:  Comply with applicable requirements in Division 23 Section "Refrigerant Piping." Connect to evaporative condenser coil with isolation valves and union at each connection.

G. Hot-Water Piping:  Comply with applicable requirements in Division 23 Section "Hydronic Piping." Connect to supply and return basin-heater tappings with shutoff valve, strainer, control valve, and union or flange on supply connection and union or flange and balancing valve on return connection.

Retain paragraph above if hot-water basin heater is installed; retain paragraph below if steam basin heater is installed; delete both if electric basin heaters or no heaters are installed.

H. Steam and Condensate Piping:  Comply with applicable requirements in Division 23 Section "Steam and Condensate Heating Piping." Connect steam supply to basin heater with shutoff valve, strainer, control valve, and union or flange and condensate piping with union or flange, shutoff valve, strainer, and an appropriate steam trap.

Retain first paragraph below only if evaporative condenser is installed indoors.

I. Ducts:  Comply with applicable requirements in Division 23 Section "Metal Ducts." Connect ducts to evaporative condenser inlet and outlet, full size of outlet, with flexible duct connection.

J. Ground evaporative condenser according to Division 26 Section "Grounding and Bonding for Electrical Systems."

K. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

L. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

3.4 STARTUP SERVICE

Delete first paragraph below if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

B. Inspect field-assembled components, equipment installation, and piping and electrical connections for proper assemblies, installations, and connections.

C. Obtain performance tables from manufacturer.

D. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

1. Clean entire unit including basins.

2. Verify that accessories are properly installed.

3. Check makeup water float.

4. Verify clearances for airflow and for evaporative condenser servicing.

5. Check for vibration isolation and structural support.

6. Lubricate bearings on fans and shafts.

7. Verify fan wheel rotation for correct direction and for vibration or binding.  Correct vibration and binding problems.

8. Adjust belts to proper alignment and tension.

9. Verify water level in basin.  Fill to proper startup level.

10. Start external-circuit circulating pumps.

11. Verify operation of tower basin, makeup line, automatic freeze protect dump, and controlling device.  Replace defective and malfunctioning units.

12. Verify operation of basin heater and control thermostat.  Replace defective and malfunctioning units.

13. Verify that tower discharge is not recirculating into air intakes.  Recommend corrective action.

E. Check HVAC water treatment system for proper operation, and measure chemical treatment levels.  Verify operation of evaporative condenser basin automatic blowdown, and controlling device.

F. Start evaporative condenser.  Follow manufacturer's written starting procedures.

G. Prepare a written startup report that records the results of tests and inspections.

3.5 ADJUSTING

A. Adjust water-level control for proper operating level.

B. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site in assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to site outside normal occupancy hours for this purpose.

3.6 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain evaporative condensers.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 236333

EVAPORATIVE REFRIGERANT CONDENSERS
236333 - 1

