Copyright 2005 AIA
MASTERSPEC Full Length
06/05 (R 06/06)

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 236500 - COOLING TOWERS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

Retain one or more of six subparagraphs below.

1. Closed-circuit, forced-draft, counterflow cooling towers.

2. Closed-circuit, induced-draft, combined-flow cooling towers.

3. Closed-circuit, induced-draft, counterflow cooling towers.

4. Open-circuit, forced-draft, counterflow cooling towers.

5. Open-circuit, induced-draft, counterflow cooling towers.

6. Open-circuit, induced-draft, crossflow cooling towers.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. BMS:  Building management system.

B. FRP:  Fiber-reinforced polyester.

1.4 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design:  Design cooling tower support structure[ and seismic restraints] [ and wind restraints], including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

B. Structural Performance:  Cooling tower support structure shall withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated according to [SEI/ASCE 7] <Insert requirement>.

Consult a structural engineer experienced in engineering cooling tower structural supports and seismic and wind restraints of type indicated to quantify design loads applicable to Project.  Verify compliance with codes.  See Evaluations.

Retain subparagraphs below if design loads and load combinations are not indicated on Drawings.

1. Dead Loads:  <Insert loads>.

2. Live Loads:  <Insert loads>.

3. Roof Loads:  <Insert loads>.

4. Snow Loads:  <Insert loads>.

5. Seismic Loads:  <Insert loads>.

6. Wind Loads:  <Insert loads>.

7. <Insert loads or load combinations>.

8. Deflection Limits:  Design system to withstand design loads without deflections greater than the following:

a. <Insert deflection limits>.

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

C. Seismic Performance:  Cooling towers shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.5 SUBMITTALS

First two paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include rated capacities, pressure drop, fan performance data, rating curves with selected points indicated, furnished specialties, and accessories.

1. Maximum flow rate.

2. Minimum flow rate.

3. Drift loss as percent of design flow rate.

Retain first subparagraph below if a remote storage tank is provided.

4. Volume of water in suspension for purposes of sizing a remote storage tank.

5. Sound power levels in eight octave bands for operation with fans off, fans at minimum, and design speed.

6. Performance curves for the following:

a. Varying entering-water temperatures from design to minimum.

b. Varying ambient wet-bulb temperatures from design to minimum.

c. Varying water flow rates from design to minimum.

d. Varying fan operation (off, minimum, and design speed).

7. Fan airflow, brake horsepower, and drive losses.

Retain first subparagraph below if pump is integral to closed-circuit cooling tower.

8. Pump flow rate, head, brake horsepower, and efficiency.

9. Motor amperage, efficiency, and power factor at 100, 75, 50, and 25 percent of nameplate horsepower.

10. Electrical power requirements for each cooling tower component requiring power.

B. Shop Drawings:  Complete set of manufacturer's prints of cooling tower assemblies, control panels, sections and elevations, and unit isolation.  Include the following:

1. Assembled unit dimensions.

2. Weight and load distribution.

3. Required clearances for maintenance and operation.

4. Sizes and locations of piping and wiring connections.

5. Wiring Diagrams:  For power, signal, and control wiring.

First paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

C. Delegated-Design Submittal:  For cooling tower support structure indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail fabrication and assembly of support structure.

2. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include adjustable motor bases, rails, and frames for equipment mounting.

3. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] [ and wind restraints] and for designing vibration isolation bases.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Floor plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from Installers of the items involved:

1. Structural supports.

2. Piping roughing-in requirements.

3. Wiring roughing-in requirements, including spaces reserved for electrical equipment.

4. Access requirements, including working clearances for mechanical controls and electrical equipment, and tube pull and service clearances.

Retain first paragraph below if retaining certification in "Quality Assurance" Article.

E. Certificates:  For certification required in "Quality Assurance" Article.

Some manufacturers claim not to be able to provide the certification specified in first paragraph below; however, such certification is mandated in many locations by authorities having jurisdiction.  Verify availability with manufacturers and retain below if required by seismic criteria applicable to Project.  See the "Seismic Considerations" Article in the Evaluations.  Coordinate below with Sections specifying mechanical vibration, supports, and seismic controls.  See SEI/ASCE 7 for certification requirements for equipment and components.

F. Seismic Qualification Certificates:  For cooling towers, accessories, and components, from manufacturers.

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

G. Source quality-control reports.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

H. Field quality-control reports.

I. Startup service reports.

J. Operation and Maintenance Data:  For each cooling tower to include in emergency, operation, and maintenance manuals.

K. Warranty:  Sample of special warranty.

1.6 QUALITY ASSURANCE

Retain first paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Division 01 Section "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

A. Testing Agency Qualifications:  [Certified by CTI] [An NRTL].

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

C. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

Retain first paragraph below if heat-exchanger coil of closed-circuit cooling towers requires ASME Boiler and Pressure Vessel Code construction.

D. ASME Compliance:  Fabricate and label heat-exchanger coils to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

Retain first paragraph below if CTI certification is required.  Confirm that Project requirements fall within parameters of CTI STD 201.

E. CTI Certification:  Cooling tower thermal performance according to CTI STD 201, "Certification Standard for Commercial Water-Cooling Towers Thermal Performance."

Retain paragraph below if required to comply with governing codes or insurance underwriter's requirements.

F. FMG approval and listing in the latest edition of FMG's "Approval Guide."

1.7 COORDINATION

Retain first paragraph below for mounting towers on concrete bases.

A. Coordinate sizes and locations of concrete bases with actual equipment provided.

Retain first paragraph below for mounting towers on a structural-steel support structure.

B. Coordinate sizes, locations, and anchoring attachments of structural-steel support structures.

Retain paragraph below for mounting tower on the roof.

C. Coordinate sizes and locations of roof curbs, equipment supports, and roof penetrations with actual equipment provided.

1.8 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace the following components of cooling towers that fail in materials or workmanship within specified warranty period:

1. Fan assembly including fan, drive, and motor.

In first subparagraph below, some manufacturers offer models with an extended warranty covering the entire cooling tower.  Baltimore Aircoil Company's "JE Premier Series" and Marley Cooling Technologies' "NC Diamond Series" are examples of models with a five-year warranty.

2. All components of cooling tower.

3. <Insert components requiring extended warranty>.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

4. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 CLOSED-CIRCUIT, FORCED-DRAFT, COUNTERFLOW COOLING TOWERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

A. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Baltimore Aircoil Company; Models VFL and VF1.

2. Delta Cooling Towers, Inc.; Model Pioneer.

3. Evapco Inc.; Models LSWA and LRW.

4. Recold; Models JM and JW.

5. <Insert manufacturer's name; product name or designation>.

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; or delete option and insert manufacturer's name and model number if not including them on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Baltimore Aircoil Company.

2. Delta Cooling Towers, Inc.

3. Evapco Inc.

4. Recold.

5. <Insert manufacturer's name>.

Retain first paragraph below for projects in seismic areas.

C. Fabricate cooling tower mounting base with reinforcement strong enough to resist cooling tower movement during a seismic event when cooling tower is anchored to field support structure.

D. Cooling tower designed to resist wind load of [30 lbf/sq. ft. (1.44 kPa)] <Insert value>.

E. Casing and Frame:

1. Casing[ and Frame] Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

Retain first subparagraph below and delete option in subparagraph heading above if frame material is different than casing.

2. Frame Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

3. Fasteners:  [Galvanized] [Stainless] steel.

4. Joints and Seams:  Sealed watertight.

5. Welded Connections:  Continuous and watertight.

Retain one of first two paragraphs below.  Retain first paragraph if collection basins are provided separate from cooling tower.

F. Collection Basin:  Configure tower for installation with a field-constructed collection basin.

G. Collection Basin:

1. Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Strainer:  Removable[ stainless-steel] strainer with openings smaller than nozzle orifices.

3. Overflow and drain connections.

4. Makeup water connection.

Retain subparagraph below for factory-installed basin sweeper distribution piping for field connection to field-installed filtration system to minimize sediment from collecting in the collection basin.  Not all listed manufacturers offer basin sweeper distribution piping.  Consult cooling tower manufacturers.

5. Basin Sweeper Distribution Piping and Nozzles:

a. Pipe Material:  [PVC] <Insert material>.

b. Nozzle Material:  [Plastic] <Insert material>.

c. Configure piping and nozzles to minimize sediment from collecting in the collection basin.

Retain one of first two paragraphs below if water-level control is to be provided with cooling tower.

H. Mechanically Operated, Collection Basin Water-Level Control:  Manufacturer's standard adjustable, mechanical float assembly and valve.

I. Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Sensor:  Solid-state controls with multiple electrode probes and relays factory wired to a terminal strip to provide [control of water makeup valve] [control of water makeup valve and low-level alarm] [control of water makeup valve and low- and high-level alarms] [control of water makeup valve, low- and high-level alarms, and output for shutoff of pump on low level].

3. Electrode Probes:  Stainless steel.

First option in first subparagraph below is less restrictive, while other options are limiting.

4. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

5. Solenoid Valve:  Slow closing[ with stainless-steel body], controlled and powered through level controller in response to water-level set point.

6. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

Retain one of first four paragraphs below to require basin heaters for projects subject to freezing conditions.  See Evaluations.

J. Electric Basin Heater:

1. Stainless-Steel Electric Immersion Heaters:  Installed in a threaded coupling on the side of the collection basin.

2. Heater Control Panel:  Mounted on the side of each cooling tower cell.

3. Enclosure:  NEMA 250, [Type 3R] [Type 4] [Type 4X].

4. Magnetic contactors controlled by a temperature sensor/controller to maintain collection basin water-temperature set point.  Water-level probe shall monitor cooling tower water level and de-energize the heater when the water reaches low-level set point.

5. Control-circuit transformer with primary and secondary side fuses.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] and heater branch circuiting complying with NFPA 70.

8. Factory Wiring Method:  Metal raceway for factory-installed wiring outside of enclosures, except make connections to each electric basin heater with liquidtight conduit.

K. Hot-Water-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

L. Steam-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

M. Steam-Injector Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

N. Water Distribution Piping:  Main header and lateral branch piping designed for even distribution over fill throughout the flow range without the need for balancing valves and for connecting individual, removable, nonclogging spray nozzles.

In first subparagraph below, PVC is manufacturer's most common standard offering.  Other requirements may require use of other materials.

1. Pipe Material:  [Fiberglass] [PVC] [Galvanized steel] <Insert material>.

2. Spray Nozzle Material:  [Plastic] [Polypropylene] [PVC] <Insert material>.

3. Piping Supports:  Corrosion-resistant hangers and supports designed to resist movement during operation and shipment.

Retain third option in first paragraph below if spray pump is specified in other Division 23 Sections.

O. Recirculating Piping:  [PVC] <Insert pipe material>[, with connections for separately provided, remote spray pump].

P. Spray Pump:  Close-coupled, end-suction, single-stage, bronze-fitted centrifugal pump; with suction strainer and flow balancing valve, and mechanical seal suitable for outdoor service.

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Spray Pump Motor:  Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

2. Motor Enclosure:  [Totally enclosed] [Totally enclosed nonventilated (TENV)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

3. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Service Factor:  [1.0] [1.15] <Insert value>.

Q. Heat-Exchanger Coils:

Some material options in first subparagraph below are limited to specific manufacturers.  Consult manufacturers if Project requires specific materials.

1. Tube and Tube Sheet Materials:  [Copper tube with stainless-steel sheet] [Stainless-steel tube and sheet] [Prime-coated steel tube and sheet with outer surface of tube and sheet hot-dip galvanized after fabrication].

Retain one of first two subparagraphs below.  Second subparagraph is only available with hot-dip galvanized steel tubes.  Coordinate with subparagraph above and "Quality Assurance" Article.

2. Heat-Exchanger Arrangement:  [Serpentine tubes] [Serpentine tubes with removable cover plate on inlet and outlet headers] [Straight tubes with removable header cover plate on both ends of heat exchanger for straight-through access to each tube]; and sloped for complete drainage of fluid by gravity.

3. ASME Compliance:  Designed, manufactured, and tested according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1, and bearing ASME "U" stamp; and sloped for complete drainage of fluid by gravity.

4. Field Piping Connections:  Vent, supply, and return[ suitable for mating to ASME B16.5, Class 150 flange].

Retain option in first paragraph below to limit placement of drift eliminators.

R. [Removable ]Drift Eliminator:

1. Material:  [FRP] [PVC] [FRP or PVC] <Insert material>; with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Configuration:  Multipass, designed and tested to reduce water carryover to achieve performance indicated.

Retain first paragraph below if screens are required.

S. [Removable ]Air-Intake Screens:  [Galvanized] [Polymer-coated, galvanized] [Stainless]-steel wire mesh.

T. Centrifugal Fan:  Double-width, double-inlet, forward-curved blades, and statically and dynamically balanced at the factory after assembly.

1. Number of Fans:  Each cooling tower cell shall have a single fan or multiple fans connected to a common shaft.

2. Fan Wheel and Housing Materials:  Galvanized steel.

3. Fan Shaft:  Steel, coated to resist corrosion.

4. Protective Enclosure:  Removable, galvanized-steel, wire-mesh screens complying with OSHA regulations.

5. Fan Shaft Bearings:  Self-aligning, grease-lubricated ball or roller bearings with moisture-proof seals and premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).  Bearings designed for an L-10 life of [40,000] [50,000] <Insert value> hours.

6. Bearings Grease Fittings:  Extended lubrication lines to an easily accessible location.

U. Belt Drive:

1. Belt-Drive Service Factor:  [1.5] <Insert value> based on motor nameplate horsepower.

2. Sheaves:  Fan and motor shafts shall have taper-lock sheaves fabricated from corrosion-resistant materials.

Retain one of first two subparagraphs below.  Second subparagraph provides better performance.

3. Belt:  Multiple V-belt design with a matched set of[ cogged] belts.

4. Belt:  One-piece, multigrooved, solid-back belt.

5. Belt Material:  Oil resistant, nonstatic conducting, and constructed of neoprene polyester cord.

6. Belt-Drive Guard:  Comply with OSHA regulations.

Retain subparagraph below if Project requires functionality of a single fan with two motors.  Feature is proprietary.  See Evaluations.

7. Two-Motor, Single-Fan Drive:

a. Two single-speed motors per fan, one sized for full speed and load, and the other sized for [67] <Insert value> percent of full-load speed.

b. Belt Drives:  Each motor shall have belt drive complying with requirements for belt drives and configured for operation when other motor fails.

c. Motor controller and wiring same as two-speed, two-winding motor.

V. Fan Motor:

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Fan Motors:  Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

2. Motor Enclosure:  [Totally enclosed] [Totally enclosed air over (TEAO)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

3. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Service Factor:  [1.15] <Insert value>.

5. Insulation:  [Class F] [Class H] <Insert class>.

6. Variable-Speed Motors:  Inverter-duty rated per NEMA MG-1, Section IV, "Performance Standard Applying to All Machines," Part 31, "Definite-Purpose, Inverter-Fed, Polyphase Motors."

Retain first subparagraph below, based on Project conditions, to require additional protection.

7. Severe-duty rating with the following features:

a. Rotor and stator protected with corrosion-inhibiting epoxy resin.

b. Double-shielded, vacuum-degassed bearings lubricated with premium moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).

First subparagraph below requires a separate, single-phase, field-power connection for heater operation.

c. Internal heater automatically energized when motor is de-energized.

Retain subparagraph below for belt-drive units.

8. Motor Base:  Adjustable, or other suitable provision for adjusting belt tension.

Retain first paragraph below if cooling tower requires a discharge hood.  See Evaluations.

W. Discharge Hoods:

1. Hood Configuration:  [Tapered] [Straight]; totally surrounding drift eliminators and constructed of same material as casing; and having factory-installed [insulation and ]access doors.

Retain subparagraph below if discharge dampers are required.

2. Discharge Dampers:  Positive-closure, automatic, isolation dampers with electric actuators.

Retain subparagraph below if cooling towers are not provided with factory-installed and -wired control package.

a. Provide field power and controls to open dampers when pump is energized and close dampers when pump is de-energized.

Retain first paragraph below if Project requires capacity-control dampers to improve leaving-water temperature control.

X. Capacity-Control Dampers:  [Galvanized-steel] [Stainless-steel] <Insert material> dampers, with linkages, electric operator, controller, limit switches, transformer, and weatherproof enclosure.

Retain first paragraph below to require a vibration switch furnished with cooling tower.

Y. Vibration Switch:  For each fan drive.

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Vibration Detection:  Sensor with a field-adjustable acceleration sensitivity set point in a range of 0 to 1 g and frequency range of 0 to 3000 cycles per minute.  Cooling tower manufacturer shall recommend switch set point for proper operation and protection.

3. Provide switch[ with manual-reset button] for [field connection to a BMS and ]hardwired connection to fan motor electrical circuit.

4. Switch shall, on sensing excessive vibration,[ signal an alarm through the BMS and] shut down the fan.

Retain first paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC." Retain second paragraph if controls are provided with cooling tower.

Z. Controls:  Comply with requirements in Division 23 Section "Instrumentation and Control for HVAC."

Retain first paragraph below, based on Project conditions, to require cooling tower to be equipped with factory-installed control package.  Not all manufacturers offer factory-installed control packages; those that do offer control packages have limited features available with the package.  Consult manufacturers for additional information.

AA. Control Package:  Factory installed and wired, and functionally tested at factory before shipment.

Sixteen subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features and to correspond with components retained in paragraphs above.

1. NEMA 250, [Type 3R] [Type 4] [Type 4X] enclosure with removable internally mount backplate.

2. Control-circuit transformer with primary and secondary side fuses.

3. Terminal blocks with numbered and color-coded wiring to match wiring diagram.  Spare wiring terminal block for connection to external controls or equipment.

4. Microprocessor-based controller for automatic control of fan[ and spray pump] based on cooling tower leaving-water temperature with control features to improve operating efficiency based on outdoor ambient wet-bulb temperature by using adaptive logic.

5. Fan motor sequencer for multiple-cell and two-speed applications with automatic lead stage rotation.

If retaining "Mechanically Operated, Collection Basin Water-Level Control" Paragraph, delete first subparagraph below.

6. Collection basin, electric/electronic level controller complying with requirements in "Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve" Paragraph.

7. Electric basin heaters with temperature control and low-water-level safety switch for each cell, complying with requirements in "Electric Basin Heater" Paragraph.

8. Vibration switch for each fan, complying with requirements in "Vibration Switch" Paragraph.

9. Controls and wiring for "two-motor, single-fan drives" shall be same as two-speed, two-winding motor.

10. Power and controls to open discharge hood dampers when pump is energized and close dampers when pump is de-energized.

11. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] [for each cooling tower cell].

a. Branch power circuit to each motor and electric basin heater and to controls[ with a disconnect switch or circuit breaker].

b. NEMA-rated motor controller, hand-off-auto switch, and overcurrent protection for each motor.  Provide variable frequency controller with manual bypass and line reactors for each variable-speed motor indicated.

12. Factory-installed wiring outside of enclosures shall be in metal raceway, except make connections to each motor and electric basin heater with liquidtight conduit.

13. Visual indication of status and alarm[ with momentary test push button] for each motor.

Retain first subparagraph below for audible alarm.  Coordinate with control sequence.

14. Audible alarm and silence switch.

15. Visual indication of elapsed run time, graduated in hours for each motor.

Retain subparagraph below if unit controls interface with BMS.

16. Cooling tower shall have hardware to enable BMS to remotely monitor and display the following:

Subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features.

a. Operational status of each motor.

b. Position of dampers.

c. Cooling tower leaving-fluid temperature.

d. Fan vibration alarm.

e. Collection basin [high] [low] [high- and low]-water-level alarms.

f. <Insert conditions to be monitored>.

AB. Personnel Access Components:

Five subparagraphs below are optional components.  Retain applicable subparagraphs, based on Project conditions, to require these components.

1. Doors:  Large enough for personnel to access cooling tower internal components from [both ]cooling tower end walls.[  Doors shall be operable from both sides of the door.]

2. External Ladders with Safety Cages:  Aluminum, galvanized- or stainless-steel, fixed ladders with ladder extensions to access external platforms and top of cooling tower from adjacent grade without the need for portable ladders.  Comply with 29 CFR 1910.27.

3. External Platforms with Handrails:  Aluminum, FRP, or galvanized-steel bar grating at cooling tower access doors when cooling towers are elevated and not accessible from grade.

4. Handrail:  Aluminum, galvanized steel, or stainless steel complete with kneerail and toeboard at platforms and around top of cooling tower.  Comply with 29 CFR 1910.23.

5. Internal Platforms:  Aluminum, FRP, or galvanized-steel bar grating.

a. Spanning the collection basin from one end of cooling tower to the other and positioned to form a path between the access doors.  Platform shall be elevated so that all parts are above the high water level of the collection basin.

If Project has more than one type or configuration of cooling tower, delete paragraph below and schedule cooling towers on Drawings.

AC. Capacities and Characteristics:

1. Number of Cells:  <Insert quantity>.

2. Maximum Drift Loss:  [0.005] <Insert number> percent of design water flow.

3. Heat-Exchanger Coil:

a. Fluid Type:  [Water] <Insert type>.

b. Fluid Flow/Cell:  <Insert gpm (L/s)>.

c. Minimum Fluid Flow/Cell:  <Insert gpm (L/s)>.

d. Fluid Pressure Drop:  <Insert psig (kPa)>.

e. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

f. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

g. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below if cooling tower will be used in favorable weather as an economizer rather than operating water chillers.  See Evaluations.

4. Economizer Mode:

a. Fluid Flow/Cell:  <Insert gpm (L/s)>.

b. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

c. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

d. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

5. Fan Location:  [Bottom] [Side].

6. Fan Motor:

a. Type:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Variable speed].

b. Horsepower/Cell:  <Insert horsepower>.

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

7. Spray Pump and Motor:

a. Water Flow/Cell:  <Insert gpm (L/s)>.

b. Horsepower/Cell:  <Insert horsepower>.

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [120] [208] [240] [277] [480] <Insert value>-V ac, [single] [3] phase, 60 Hz.

8. Sound Pressure Level:  <Insert dBA> at <Insert distance in feet (m)> [when measured according to CTI ATC 128].

Retain subparagraph below for projects with basin heaters.

9. Basin Heater:

a. Basin Water Temperature:  [40 deg F (5 deg C)] <Insert deg F (deg C)>.

b. Outdoor Ambient Temperature:  [0 deg F (minus 18 deg C)] [Minus 20 deg F (Minus 29 deg C)] <Insert deg F (deg C)>.

Retain first five subparagraphs below for projects with electric basin heaters.

c. Capacity/Cell:  <Insert kilowatts>.

d. Full-Load Ampacity:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection Device:  <Insert amperage>.

g. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

Retain first four subparagraphs below for projects with hot-water-coil basin heaters.

h. Capacity/Cell:  <Insert MBtu/h (kW)>.

i. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

j. Fluid Flow Rate:  <Insert gpm (L/s)>.

k. Fluid Pressure Drop:  <Insert psig (kPa)>.

Retain three subparagraphs below for projects with steam-coil or -injection basin heaters.

l. Capacity/Cell:  <Insert MBtu/h (kW)>.

m. Steam Flow:  <Insert lb/h (L/s)>.

n. Steam Pressure:  <Insert psig (kPa)>.

2.2 CLOSED-CIRCUIT, INDUCED-DRAFT, COMBINED-FLOW COOLING TOWERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

A. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Baltimore Aircoil Company; Model FXV.

2. Marley Cooling Technologies, an SPX Corporation; Model MH.

3. <Insert manufacturer's name; product name or designation>.

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; or delete option and insert manufacturer's name and model number if not including them on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Baltimore Aircoil Company.

2. Marley Cooling Technologies; an SPX Corporation.

3. <Insert manufacturer's name>.

Retain first paragraph below for projects in seismic areas.

C. Fabricate cooling tower mounting base with reinforcement strong enough to resist cooling tower movement during a seismic event when cooling tower is anchored to field support structure.

D. Cooling tower designed to resist wind load of [30 lbf/sq. ft. (1.44 kPa)] <Insert value>.

E. Casing and Frame:

1. Casing[ and Frame] Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

Retain first subparagraph below and delete option in subparagraph heading above if frame material is different than casing.

2. Frame Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

3. Fasteners:  [Galvanized] [Stainless] steel.

4. Joints and Seams:  Sealed watertight.

5. Welded Connections:  Continuous and watertight.

Retain one of first two paragraphs below.  Retain first paragraph if collection basins are provided separate from cooling tower.

F. Collection Basin:  Configure tower for installation with a field-constructed collection basin.

G. Collection Basin:

1. Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Strainer:  Removable[ stainless-steel] strainer with openings smaller than nozzle orifices.

3. Overflow and drain connections.

4. Makeup water connection.

Retain subparagraph below for factory-installed basin sweeper distribution piping for field connection to field-installed filtration system to minimize sediment from collecting in the collection basin.  Not all listed manufacturers offer basin sweeper distribution piping.  Consult cooling tower manufacturers.

5. Basin Sweeper Distribution Piping and Nozzles:

a. Pipe Material:  [PVC] <Insert material>.

b. Nozzle Material:  [Plastic] <Insert material>.

c. Configure piping and nozzles to minimize sediment from collecting in the collection basin.

Retain one of first three paragraphs below if water-level control is to be provided with cooling tower.

H. Mechanically Operated, Collection Basin Water-Level Control:  Manufacturer's standard adjustable, mechanical float assembly and valve.

I. Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Sensor:  Solid-state controls with multiple electrode probes and relays factory wired to a terminal strip to provide [control of water makeup valve] [control of water makeup valve and low-level alarm] [control of water makeup valve and low- and high-level alarms] [control of water makeup valve, low- and high-level alarms, and output for shutoff of pump on low level].

3. Electrode Probes:  Stainless steel.

First option in first subparagraph below is less restrictive, while other options are limiting.

4. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

5. Solenoid Valve:  Slow closing[ with stainless-steel body], controlled and powered through level controller in response to water-level set point.

6. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

J. Ultrasonic Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Controller:  Ultrasonic level sensor/transmitter and relays factory wired to a terminal strip to control water makeup valve and signal a level alarm.  Controller shall provide continuous level indication through a 4- to 20-mA signal[ for connection to BMS].

First option in first subparagraph below is less restrictive, while other options are limiting.

3. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

4. Solenoid Valve:  Slow closing[ with stainless-steel body], controlled and powered through level controller in response to water-level set point.

5. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

Retain one of first four paragraphs below to require basin heaters for projects subject to freezing conditions.  See Evaluations.

K. Electric Basin Heater:

1. Stainless-Steel Electric Immersion Heaters:  Installed in a threaded coupling on the side of the collection basin.

2. Heater Control Panel:  Mounted on the side of each cooling tower cell.

3. Enclosure:  NEMA 250, [Type 3R] [Type 4] [Type 4X].

4. Magnetic contactors controlled by a temperature sensor/controller to maintain collection basin water-temperature set point.  Water-level probe shall monitor cooling tower water level and de-energize the heater when the water reaches low-level set point.

5. Control-circuit transformer with primary and secondary side fuses.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] and heater branch circuiting complying with NFPA 70.

8. Factory Wiring Method:  Metal raceway for factory-installed wiring outside of enclosures, except make connections to each electric basin heater with liquidtight conduit.

L. Hot-Water-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

M. Steam-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

N. Steam-Injector Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

O. Gravity Water Distribution Basin:  Nonpressurized design with head of water level in basin adequate to overcome spray nozzle losses and designed to evenly distribute water over fill throughout the flow range indicated.

1. Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Location:  Over each bank of fill with easily replaceable [plastic] <Insert material> spray nozzles mounted in bottom of basin.

3. Joints and Seams:  Sealed watertight.

Retain first subparagraph below for projects subject to freezing conditions.

4. Partitioning Dams:  Same material as basin to distribute water over the fill to minimize icing while operating throughout the flow range indicated.

5. Removable Panels:  Same material as basin to completely cover top of basin.  Secure panels to basin with removable [corrosion-resistant] [stainless-steel] hardware.

Retain subparagraph below if valves are to be provided with cooling tower.

6. Valves:  Manufacturer's standard valve installed at each inlet connection and arranged to balance or shut off flow to each gravity water distribution basin.

P. Pressurized Water Distribution Piping:  Main header and lateral branch piping designed for even distribution over heat-exchanger coil or fill throughout the flow range without the need for balancing valves and for connecting individual, removable, nonclogging spray nozzles.

In first subparagraph below, PVC is manufacturer's most common standard offering.  Other requirements may require use of other materials.

1. Pipe Material:  [PVC] [Galvanized steel] <Insert material>.

2. Spray Nozzle Material:  [Plastic] [Polypropylene] <Insert material>.

3. Piping Supports:  Corrosion-resistant hangers and supports to resist movement during operation and shipment.

Retain third option in first paragraph below if spray pump is specified in other Division 23 Sections.

Q. Recirculating Piping:  [PVC] <Insert pipe material>[, with connections for separately provided, remote spray pump].

R. Spray Pump:  Close-coupled, end-suction, single-stage, bronze-fitted centrifugal pump; with suction strainer and flow balancing valve, and mechanical seal suitable for outdoor service.

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Spray Pump Motor:  Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

2. Motor Enclosure:  [Totally enclosed] [Totally enclosed nonventilated (TENV)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

3. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Service Factor:  [1.0] [1.15] <Insert value>.

S. Fill:

In first subparagraph below, PVC is manufacturer's most common standard offering.

1. Materials:  [PVC] <Insert material>, with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

Retain first subparagraph below if other than manufacturer's standard fill is required.  Thicker fill is used primarily in applications with elevated water temperatures.

2. Minimum Thickness:  [15 mils (0.4 mm)] [20 mils (0.5 mm)] <Insert value>, before forming.

3. Fabrication:  Fill-type sheets fabricated, formed, and bonded together after forming into removable assemblies that are factory installed by manufacturer.

Consult manufacturers for fill options at elevated temperatures.

4. Fill Material Operating Temperature:  Suitable for entering-water temperatures up through [120 deg F (49 deg C)] <Insert temperature>.

T. Heat-Exchanger Coils:

Some material options in first subparagraph below are limited to specific manufacturers.  Consult manufacturers if Project requires specific materials.

1. Tube and Tube Sheet Materials:  [Copper tube with stainless-steel sheet] [Stainless-steel tube and sheet] [Prime-coated steel tube and sheet with outer surface of tube and sheet hot-dip galvanized after fabrication].

Retain one of first two subparagraphs below.  Second subparagraph is only available with hot-dip galvanized-steel tubes.  Coordinate with subparagraph above and "Quality Assurance" Article.

2. Heat-Exchanger Arrangement:  [Serpentine tubes] [Serpentine tubes with removable cover plate on inlet and outlet headers] [Straight tubes with removable header cover plate on both ends of heat exchanger for straight-through access to each tube]; and sloped for complete drainage of fluid by gravity.

3. ASME Compliance:  Designed, manufactured, and tested according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1 and bearing ASME "U" stamp; and sloped for complete drainage of fluid by gravity.

4. Field Piping Connections:  Vent, supply, and return[ suitable for mating to ASME B16.5, Class 150 flange].

U. Drift Eliminator:

1. Material:  [FRP] [PVC] [FRP or PVC] <Insert material>; with maximum flame-spread index of [5] <Insert value> according to ASTM E 84.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Configuration:  Multipass, designed and tested to reduce water carryover to achieve performance indicated.

Retain first subparagraph below to limit placement of fill drift eliminators.

4. Fill Drift Eliminators:  [Integral to] [Separate and removable from] fill.

5. Heat-Exchanger Coil Drift Eliminators:  Located on discharge side and removable.

V. Air-Intake Louvers:

1. Material:  [FRP] [PVC] [Matching casing].

Retain first subparagraph below with FRP or PVC louvers.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Louver Blades:  Arranged to uniformly direct air into cooling tower, to minimize air resistance, and to prevent water from splashing out of tower during all modes of operation including operation with fans off.

Retain subparagraph below to limit placement of louvers.

4. Location:  [Integral to] [Separate from] fill.

Retain first paragraph below if screens are required.

W. [Removable ]Air-Intake Screens:  [Galvanized] [Polymer-coated, galvanized] [Stainless]-steel wire mesh.

X. Axial Fan:  Balanced at the factory after assembly.

1. Blade Material:  [Aluminum] [FRP].

2. Hub Material:  [Aluminum] [FRP].

First subparagraph below is an optional feature.  Retain, based on Project conditions, to require feature.

3. Blade Pitch:  Field adjustable.

4. Protective Enclosure:  Removable, galvanized-steel, wire-mesh screens complying with OSHA regulations.

5. Fan Shaft Bearings:  Self-aligning ball or roller bearings with moisture-proof seals and premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).  Bearings designed for an L-10 life of [40,000] [50,000] <Insert value> hours.

6. Bearings Grease Fittings:  Extended lubrication lines to an easily accessible location.

Retain first paragraph below if belt drive is used.

Y. Belt Drive:

1. Service Factor:  [1.5] <Insert value> based on motor nameplate horsepower.

2. Sheaves:  Fan and motor shafts shall have taper-lock sheaves fabricated from corrosion-resistant materials.

Retain one of first two subparagraphs below.  Second subparagraph provides better performance.

3. Belt:  Multiple V-belt design with a matched set of[ cogged] belts.

4. Belt:  One-piece, multigrooved, solid-back belt.

5. Belt Material:  Oil resistant, nonstatic conducting, and constructed of neoprene polyester cord.

6. Belt-Drive Guard:  Comply with OSHA regulations.

Retain subparagraph below if Project requires functionality of a single fan with two motors.  Feature is proprietary.  See Evaluations.

7. Two-Motor, Single-Fan Drive:

a. Two single-speed motors per fan, one sized for full speed and load and the other sized for [67] <Insert value> percent of full-load speed.

b. Each motor with belt drive and configured for operation when other motor fails.

c. Controls and wiring same as two-speed, two-winding motor.

Retain first paragraph below if gear drive is used.  See Evaluations.

Z. Gear Drive:  Right angle, reduced speed, and designed for cooling tower applications according to CTI STD 111.  Motor and gear drive shall be aligned before shipment.

1. Gear Drive and Coupling Service Factor:  [2.0] <Insert value> based on motor nameplate horsepower.

2. Housing:  Cast iron, with epoxy or polyurethane finish, beveled high-strength steel gears continuously bathed in oil, and with lubrication to other internal parts at all operating speeds.

3. Mounting:  Directly mounted to fan hub and connected to motor so motor shaft is in horizontal position.

4. Operation:  Able to operate both forward and in reverse.

Coordinate motor requirements with options in first subparagraph below.

5. Drive-to-Motor Connection:  [Close coupled to motor using a flexible coupling] [Connected to motor located outside of cooling tower casing by a full-floating drive shaft].

Retain first subparagraph below with second option in last subparagraph above.

6. Drive Shaft Material:  [Corrosion resistant] [Stainless steel], and fitted with flexible couplings on both ends.  Provide exposed shaft and couplings with guards according to OSHA regulations.

7. Extend oil fill, drain, and vent to outside of cooling tower casing using galvanized-steel piping.  Provide installation with oil-level sight glass.

AA. Fan Motor:

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Fan Motors:  Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

2. Motor Enclosure:  [Totally enclosed] [Totally enclosed air over (TEAO)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

3. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Service Factor:  [1.15] <Insert value>.

5. Insulation:  [Class F] [Class H] <Insert class>.

6. Variable-Speed Motors:  Inverter-duty rated per NEMA MG-1, Section IV, "Performance Standard Applying to All Machines," Part 31, "Definite-Purpose, Inverter-Fed, Polyphase Motors."

Retain first subparagraph below if Project requires specific motor location.  Standard offering by most manufacturers is motor mounted internally or in the airstream.

7. Motor Location:  Mounted outside of cooling tower casing and cooling tower discharge airstream.

Retain first subparagraph below, based on Project conditions, to require additional protection.

8. Severe-duty rating with the following features:

a. Rotor and stator protected with corrosion-inhibiting epoxy resin.

b. Double-shielded, vacuum-degassed bearings lubricated with premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).

First subparagraph below requires a separate, single-phase, field-power connection for heater operation.

c. Internal heater automatically energized when motor is de-energized.

Retain subparagraph below for belt-drive units.

9. Motor Base:  Adjustable, or other suitable provision for adjusting belt tension.

AB. Fan Discharge Stack:  Material shall match casing, [manufacturer's standard] [velocity recovery] design.

Retain first subparagraph below if Project requires a minimum stack height to clear an obstruction.

1. Stack Extension:  Fabricated to extend above fan deck <Insert distance> unless otherwise indicated.

2. Stack Termination:  Wire-mesh, galvanized-steel screens; complying with OSHA regulations.

Retain first paragraph below to require a vibration switch furnished with cooling tower.

AC. Vibration Switch:  For each fan drive.

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Vibration Detection:  Sensor with a field-adjustable, acceleration-sensitivity set point in a range of 0 to 1 g and frequency range of 0 to 3000 cycles per minute.  Cooling tower manufacturer shall recommend switch set point for proper operation and protection.

3. Provide switch[ with manual-reset button] for [field connection to a BMS and ]hardwired connection to fan motor electrical circuit.

4. Switch shall, on sensing excessive vibration,[ signal an alarm through the BMS and] shut down the fan.

Retain first paragraph below for cooling towers with fan gear drives to require an oil-level switch furnished with cooling tower.

AD. Gear-Drive, Oil-Level Switch:  Low-oil-level warning switch[ for connection to a BMS].

1. Switch shall, on reaching a low-oil-level set point recommended by cooling tower manufacturer, signal an alarm[ through the BMS].

Retain first paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC." Retain second paragraph if controls are provided with cooling tower.

AE. Controls:  Comply with requirements in Division 23 Section "Instrumentation and Control for HVAC."

Retain first paragraph below, based on Project conditions, to require cooling tower to be equipped with factory-installed controls.  Not all manufacturers offer factory-installed control packages; those that do offer control packages have limited features available with the package.  Consult manufacturers for additional information.

AF. Control Package:  Factory installed and wired, and functionally tested at factory before shipment.

Fifteen subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features and to correspond with components retained in paragraphs above.

1. NEMA 250, [Type 3R] [Type 4] [Type 4X] enclosure with removable internally mount backplate.

2. Control-circuit transformer with primary and secondary side fuses.

3. Terminal blocks with numbered and color-coded wiring to match wiring diagram.  Spare wiring terminal block for connection to external controls or equipment.

4. Microprocessor-based controller for automatic control of fan[ and spray pump] based on cooling tower leaving-water temperature with control features to improve operating efficiency based on outdoor ambient wet-bulb temperature by using adaptive logic.

5. Fan motor sequencer for multiple-cell and two-speed applications with automatic lead stage rotation.

If retaining "Mechanically Operated, Collection Basin Water-Level Control" Paragraph, delete first subparagraph below.

6. Collection basin level controller complying with requirements in ["Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve"] ["Ultrasonic Collection Basin Water-Level Controller with Solenoid Valve"] Paragraph.

7. Electric basin heaters with temperature control and low-water-level safety switch for each cell, complying with requirements in "Electric Basin Heater" Paragraph.

8. Vibration switch for each fan, complying with requirements in "Vibration Switch" Paragraph.

9. Oil-level switch for each fan with a gear drive, complying with requirement in "Gear-Drive, Oil-Level Switch" Paragraph.

10. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] [for each cooling tower cell].

a. Branch power circuit to each motor and electric basin heater and to controls[ with a disconnect switch or circuit breaker].

b. NEMA-rated motor controller, hand-off-auto switch, and overcurrent protection for each motor.  Provide variable frequency controller with manual bypass and line reactors for each variable-speed motor indicated.

11. Factory-installed wiring outside of enclosures shall be in metal raceway, except make connections to each motor and electric basin heater with liquidtight conduit.

12. Visual indication of status and alarm[ with momentary test push button] for each motor.

Retain first subparagraph below for audible alarm.  Coordinate with control sequence.

13. Audible alarm and silence switch.

14. Visual indication of elapsed run time, graduated in hours for each motor.

Retain subparagraph below if unit controls interface with BMS.

15. Cooling tower shall have hardware to enable BMS to remotely monitor and display the following:

Seven subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features.

a. Operational status of each motor.

b. Position of dampers.

c. Cooling tower leaving-fluid temperature.

d. Fan vibration alarm.

Retain first subparagraph below if Project requires an oil-level alarm through BMS.  Coordinate requirements with "Gear-Drive, Oil-Level Switch" Paragraph.

e. Oil-level alarm.

f. Collection basin [high] [low] [high- and low]-water-level alarms.

g. <Insert conditions to be monitored>.

AG. Personnel Access Components:

Five subparagraphs below are optional components.  Retain applicable subparagraphs, based on Project conditions, to require these components.

1. Doors:  Large enough for personnel to access cooling tower internal components from both cooling tower end walls.  Doors shall be operable from both sides of the door.

2. External Ladders with Safety Cages:  Aluminum, galvanized- or stainless-steel, fixed ladders with ladder extensions to access external platforms and top of cooling tower from adjacent grade without the need for portable ladders.  Comply with 29 CFR 1910.27.

3. External Platforms with Handrails:  Aluminum, FRP, or galvanized-steel bar grating at cooling tower access doors when cooling towers are elevated and not accessible from grade.

4. Handrail:  Aluminum, galvanized steel, or stainless steel complete with kneerail and toeboard, around top of cooling tower.  Comply with 29 CFR 1910.23.

5. Internal Platforms:  Aluminum, FRP, or galvanized-steel bar grating.

a. Spanning the collection basin from one end of cooling tower to the other and positioned to form a path between the access doors.  Platform shall be elevated so that all parts are above the high water level of the collection basin.

b. Elevated internal platforms with handrails accessible from fixed vertical ladders to access the fan drive assembly when out of reach from collection basin platform.

If Project has more than one type or configuration of cooling tower, delete paragraph below and schedule cooling towers on Drawings.

AH. Capacities and Characteristics:

1. Number of Cells:  <Insert quantity>.

Retain first subparagraph below to limit options.  Marley manufactures first two options only.  Baltimore Aircoil manufactures third option only.

2. Air-Inlet Arrangement:  [Single side] [Two sides] [Sides and top].

3. Maximum Drift Loss:  [0.005] <Insert number> percent of design water flow.

4. Heat-Exchanger Coil:

a. Fluid Type:  [Water] <Insert type>.

b. Fluid Flow/Cell:  <Insert gpm (L/s)>.

c. Minimum Fluid Flow/Cell:  <Insert gpm (L/s)>.

d. Fluid Pressure Drop:  <Insert psig (kPa)>.

e. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

f. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

g. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below if cooling tower will be used in favorable weather as an economizer rather than operating water chillers.  See Evaluations.

5. Economizer Mode:

a. Fluid Flow/Cell:  <Insert gpm (L/s)>.

b. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

c. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

d. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below to allow Contractor to choose drive type.  Coordinate with "Belt Drive" and "Gear Drive" paragraphs above.

6. Fan Drive:  Belt or gear.

7. Fan Motor:

a. Type:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Variable speed].

b. Horsepower/Cell:  <Insert horsepower>.

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

8. Spray Pump and Motor:

a. Water Flow/Cell:  <Insert gpm (L/s)>.

b. Horsepower/Cell:  <Insert horsepower>.

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [120] [208] [240] [277] [480] <Insert value>-V ac, [single] [3] phase, 60 Hz.

9. Sound Pressure Level:  <Insert dBA> at <Insert distance in feet (m)> [when measured according to CTI ATC 128].

Retain subparagraph below for projects with basin heaters.

10. Basin Heater:

a. Basin Water Temperature:  [40 deg F (5 deg C)] <Insert deg F (deg C)>.

b. Outdoor Ambient Temperature:  [0 deg F (minus 18 deg C)] [Minus 20 deg F (Minus 29 deg C)] <Insert deg F (deg C)>.

Retain first five subparagraphs below for projects with electric basin heaters.

c. Capacity/Cell:  <Insert kilowatts>.

d. Full-Load Ampacity:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection Device:  <Insert amperage>.

g. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

Retain first four subparagraphs below for projects with hot-water-coil basin heaters.

h. Capacity/Cell:  <Insert MBtu/h (kW)>.

i. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

j. Fluid Flow Rate:  <Insert gpm (L/s)>.

k. Fluid Pressure Drop:  <Insert psig (kPa)>.

Retain three subparagraphs below for projects with steam-coil or -injection basin heaters.

l. Capacity/Cell:  <Insert MBtu/h (kW)>.

m. Steam Flow:  <Insert lb/h (L/s)>.

n. Steam Pressure:  <Insert psig (kPa)>.

2.3 CLOSED-CIRCUIT, INDUCED-DRAFT, COUNTERFLOW COOLING TOWERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

A. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Evapco Inc.; Models ATW, ESW, and UBW.

2. Recold; Model MW.

3. <Insert manufacturer's name; product name or designation>.

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; or delete option and insert manufacturer's name and model number if not including them on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Evapco Inc.

2. Recold.

3. <Insert manufacturer's name>.

Retain first paragraph below for projects in seismic areas.

C. Fabricate cooling tower mounting base with reinforcement strong enough to resist cooling tower movement during a seismic event when cooling tower is anchored to field support structure.

D. Cooling tower designed to resist wind load of [30 lbf/sq. ft. (1.44 kPa)] <Insert value>.

E. Casing and Frame:

1. Casing[ and Frame] Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Stainless steel].

Retain first subparagraph below and delete option in subparagraph heading above if frame material is different than casing.

2. Frame Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

3. Fasteners:  [Galvanized] [Stainless] steel.

4. Joints and Seams:  Sealed watertight.

5. Welded Connections:  Continuous and watertight.

Retain one of first two paragraphs below.  Retain first paragraph if collection basins are provided separate from cooling tower.

F. Collection Basin:  Configure tower for installation with a field-constructed collection basin.

G. Collection Basin:

1. Material:  [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Stainless steel].

2. Overflow and drain connections.

3. Makeup water connection.

Retain one of first two paragraphs below if water-level control is to be provided with cooling tower.

H. Mechanically Operated, Collection Basin Water-Level Control:  Manufacturer's standard adjustable, mechanical float assembly and valve.

I. Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Sensor:  Solid-state controls with multiple electrode probes and relays factory wired to a terminal strip to provide [control of water makeup valve] [control of water makeup valve and low-level alarm] [control of water makeup valve and low- and high-level alarms] [control of water makeup valve, low- and high-level alarms, and output for shutoff of pump on low level].

3. Electrode Probes:  Stainless steel.

First option in first subparagraph below is less restrictive, while other options are limiting.

4. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

5. Solenoid Valve:  Slow closing[ with stainless-steel body]; controlled and powered through level controller in response to water-level set point.

6. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

Retain one of first four paragraphs below to require basin heaters for projects subject to freezing conditions.  See Evaluations.

J. Electric Basin Heater:

1. Stainless-Steel Electric Immersion Heaters:  Installed in a threaded coupling on the side of the collection basin.

2. Heater Control Panel:  Mounted on the side of each cooling tower cell.

3. Enclosure:  NEMA 250, [Type 3R] [Type 4] [Type 4X].

4. Magnetic contactors controlled by a temperature sensor/controller to maintain collection basin water-temperature set point.  Water-level probe shall monitor cooling tower water level and de-energize the heater when the water reaches low-level set point.

5. Control-circuit transformer with primary and secondary side fuses.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] and heater branch circuiting complying with NFPA 70.

8. Factory Wiring Method:  Metal raceway for factory-installed wiring outside of enclosures, except make connections to each electric basin heater with liquidtight conduit.

K. Hot-Water-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

L. Steam-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

M. Steam-Injector Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

N. Pressurized Water Distribution Piping:  Main header and lateral branch piping designed for even distribution over heat-exchanger coil or fill throughout the flow range without the need for balancing valves and for connecting individual, removable, nonclogging spray nozzles.

In first subparagraph below, PVC is manufacturer's most common standard offering.  Other requirements may require use of other materials.

1. Pipe Material:  [Fiberglass] [PVC] [Galvanized steel] <Insert material>.

2. Spray Nozzle Material:  [Plastic] [Polypropylene] [PVC] <Insert material>.

3. Piping Supports:  Corrosion-resistant hangers and supports to resist movement during operation and shipment.

Retain third option in first paragraph below if spray pump is specified in other Division 23 Sections.

O. Recirculating Piping:  [PVC] <Insert pipe material>[, with connections for separately provided, remote spray pump].

P. Spray Pump:  Close-coupled, end-suction, single-stage, bronze-fitted centrifugal pump; with suction strainer and flow balancing valve, and mechanical seal suitable for outdoor service.

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Q. General Requirements for Spray Pump Motor:  Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

1. Motor Enclosure:  [Totally enclosed] [Totally enclosed nonventilated (TENV)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

2. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

3. Service Factor:  [1.0] [1.15] <Insert value>.

R. Heat-Exchanger Coils:

Some material options in first subparagraph below are limited to specific manufacturers.  Consult manufacturers if Project requires specific materials.

1. Tube and Tube Sheet Materials:  [Copper tube with stainless-steel sheet] [Stainless-steel tube and sheet] [Prime-coated steel tube and sheet with outer surface of tube and sheet hot-dip galvanized after fabrication].

Retain one of first two subparagraphs below.  Second subparagraph is only available with hot-dip galvanized-steel tubes.  Coordinate with subparagraph above and "Quality Assurance" Article.

2. Heat-Exchanger Arrangement:  [Serpentine tubes] [Serpentine tubes with removable cover plate on inlet and outlet headers] [Straight tubes with removable header cover plate on both ends of heat exchanger for straight-through access to each tube]; and sloped for complete drainage of fluid by gravity.

3. ASME Compliance:  Designed, manufactured, and tested according to ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1 and bearing ASME "U" stamp; and sloped for complete drainage of fluid by gravity.

4. Field Piping Connections:  Vent, supply, and return[ suitable for mating to ASME B16.5, Class 150 flange].

Retain option in first paragraph below to limit placement of drift eliminators.

S. [Removable ]Drift Eliminator:

1. Material:  [FRP] [PVC] [FRP or PVC] <Insert material>; with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Configuration:  Multipass, designed and tested to reduce water carryover to achieve performance indicated.

T. Air-Intake Louvers:

1. Material:  [FRP] [PVC] [Matching casing].

Retain first subparagraph below with FRP or PVC louvers.

2. UV Treatment:  Treat louvers with inhibitors to protect against damage caused by UV radiation.

3. Louver Blades:  Arranged to uniformly direct air into cooling tower, to minimize air resistance, and to prevent water from splashing out during all modes of operation including operation with fans off.

U. Axial Fan:  Balanced at the factory after assembly.

1. Blade Material:  [Aluminum] [FRP] [Galvanized steel].

2. Hub Material:  [Aluminum] [FRP] [Galvanized steel].

First subparagraph below is an optional feature.  Retain, based on Project conditions, to require feature.

3. Blade Pitch:  Field adjustable.

4. Protective Enclosure:  Removable, galvanized-steel, wire-mesh screens complying with OSHA regulations.

5. Fan Shaft Bearings:  Self-aligning ball or roller bearings with moisture-proof seals and premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).  Bearings designed for an L-10 life of [40,000] [50,000] <Insert value> hours.

6. Bearings Grease Fittings:  Extended lubrication lines to an easily accessible location.

V. Belt Drive:

1. Service Factor:  [1.5] <Insert value> based on motor nameplate horsepower.

2. Sheaves:  Fan and motor shafts shall have taper-lock sheaves fabricated from corrosion-resistant materials.

Retain one of first two subparagraphs below.  Second subparagraph provides better performance.

3. Belt:  Multiple V-belt design with a matched set of[ cogged] belts.

4. Belt:  One-piece, multigrooved, solid-back belt.

5. Belt Material:  Oil resistant, nonstatic conducting, and constructed of neoprene polyester cord.

6. Belt-Drive Guard:  Comply with OSHA regulations.

Retain subparagraph below if Project requires functionality of a single fan with two motors.  Feature is proprietary.  See Evaluations.

7. Two-Motor, Single-Fan Drive:

a. Two single-speed motors per fan, one sized for full speed and load and the other sized for [67] <Insert value> percent of full-load speed.

b. Each motor with belt drive and configured for operation when other motor fails.

c. Controls and wiring same as two-speed, two-winding motor.

W. Fan Motor:

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment"

1. General Requirements for Fan Motors:  Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

2. Motor Enclosure:  [Totally enclosed] [Totally enclosed air over (TEAO)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

3. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Service Factor:  [1.15] <Insert value>.

5. Insulation:  [Class F] [Class H] <Insert class>.

6. Variable-Speed Motors:  Inverter-duty rated per NEMA MG-1, Section IV, "Performance Standard Applying to All Machines," Part 31, "Definite-Purpose, Inverter-Fed, Polyphase Motors."

Retain first subparagraph below, based on Project conditions, to require additional protection.

7. Severe-duty rating with the following features:

a. Rotor and stator protected with corrosion-inhibiting epoxy resin.

b. Double-shielded, vacuum-degassed bearings lubricated with premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).

First subparagraph below requires a separate, single-phase, field-power connection for heater operation.

c. Internal heater automatically energized when motor is de-energized.

Retain subparagraph below for belt-drive units.

8. Motor Base:  Adjustable, or other suitable provision for adjusting belt tension.

X. Fan Discharge Stack:  Material shall match casing, [manufacturer's standard] [velocity recovery] design.

Retain first subparagraph below if Project requires a minimum stack height to clear an obstruction.

1. Stack Extension:  Fabricated to extend above fan deck <Insert distance> unless otherwise indicated.

2. Stack Termination:  Wire-mesh, galvanized-steel screens; complying with OSHA regulations.

Retain first paragraph below to require a vibration switch furnished with cooling tower.

Y. Vibration Switch:  For each fan drive.

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Vibration Detection:  Sensor with a field-adjustable, acceleration-sensitivity set point in a range of 0 to 1 g and frequency range of 0 to 3000 cycles per minute.  Cooling tower manufacturer shall recommend switch set point for proper operation and protection.

3. Provide switch[ with manual-reset button] for [field connection to a BMS and ]hardwired connection to fan motor electrical circuit.

4. Switch shall, on sensing excessive vibration,[ signal an alarm through the BMS and] shut down the fan.

Retain first paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC." Retain second paragraph if controls are provided with cooling tower.

Z. Controls:  Comply with requirements in Division 23 Section "Instrumentation and Control for HVAC."

Retain first paragraph below, based on Project conditions, to require cooling tower to be equipped with factory-installed controls.  Not all manufacturers offer factory-installed control packages; those that do offer control packages have limited features available with the package.  Consult manufacturers for additional information.

AA. Control Package:  Factory installed and wired, and functionally tested at factory before shipment.

Fourteen subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features and to correspond with components retained in paragraphs above.

1. NEMA 250, [Type 3R] [Type 4] [Type 4X] enclosure with removable internally mount backplate.

2. Control-circuit transformer with primary and secondary side fuses.

3. Terminal blocks with numbered and color-coded wiring to match wiring diagram.  Spare wiring terminal block for connection to external controls or equipment.

4. Microprocessor-based controller for automatic control of fan[ and spray pump] based on cooling tower leaving-water temperature with control features to improve operating efficiency based on outdoor ambient wet-bulb temperature by using adaptive logic.

5. Fan motor sequencer for multiple-cell and two-speed applications with automatic lead stage rotation.

If retaining "Mechanically Operated, Collection Basin Water-Level Control" Paragraph, delete first subparagraph below.

6. Collection basin electric/electronic level controller complying with requirements in "Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve" Paragraph.

7. Electric basin heaters with temperature control and low-water-level safety switch for each cell, complying with requirements in "Electric Basin Heater" Paragraph.

8. Vibration switch for each fan, complying with requirements in "Vibration Switch" Paragraph.

9. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] [for each cooling tower cell].

a. Branch power circuit to each motor and electric basin heater and to controls[ with a disconnect switch or circuit breaker].

b. NEMA-rated motor controller, hand-off-auto switch, and overcurrent protection for each motor.  Provide variable frequency controller with manual bypass and line reactors for each variable-speed motor indicated.

10. Factory-installed wiring outside of enclosures shall be in metal raceway, except make connections to each motor and electric basin heater with liquidtight conduit.

11. Visual indication of status and alarm[ with momentary test push button] for each motor.

Retain first subparagraph below for audible alarm.  Coordinate with control sequence.

12. Audible alarm and silence switch.

13. Visual indication of elapsed run time, graduated in hours for each motor.

Retain subparagraph below if unit controls interface with BMS.

14. Cooling tower shall have hardware to enable BMS to remotely monitor and display the following:

Subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features.

a. Operational status of each motor.

b. Cooling tower leaving-fluid temperature.

c. Fan vibration alarm.

d. Collection basin [high] [low] [high- and low]-water-level alarms.

e. <Insert conditions to be monitored>.

AB. Personnel Access Components:

Five subparagraphs below are optional components.  Retain applicable subparagraphs, based on Project conditions, to require these components.

1. Doors:  Large enough for personnel to access cooling tower internal components from both cooling tower end walls.  Doors shall be operable from both sides of the door.

2. External Ladders with Safety Cages:  Aluminum, galvanized- or stainless-steel, fixed ladders with ladder extensions to access external platforms and top of cooling tower from adjacent grade without the need for portable ladders.  Comply with 29 CFR 1910.27.

3. External Platforms with Handrails:  Aluminum, FRP, or galvanized-steel bar grating at cooling tower access doors when cooling towers are elevated and not accessible from grade.

4. Handrail:  Aluminum, galvanized steel, or stainless steel complete with kneerail and toeboard, around top of cooling tower.  Comply with 29 CFR 1910.23.

5. Internal Platforms:  Aluminum, FRP, or galvanized-steel bar grating.

a. Spanning the collection basin from one end of cooling tower to the other and positioned to form a path between the access doors.  Platform shall be elevated so that all parts are above the high water level of the collection basin.

b. Elevated internal platforms with handrails accessible from fixed vertical ladders to access the fan drive assembly when out of reach from collection basin platform.

If Project has more than one type or configuration of cooling tower, delete paragraph below and schedule cooling towers on Drawings.

AC. Capacities and Characteristics:

1. Number of Cells:  <Insert quantity>.

2. Maximum Drift Loss:  [0.005] <Insert number> percent of design water flow.

3. Heat-Exchanger Coil:

a. Fluid Type:  [Water] <Insert type>.

b. Fluid Flow/Cell:  <Insert gpm (L/s)>.

c. Minimum Fluid Flow/Cell:  <Insert gpm (L/s)>.

d. Fluid Pressure Drop:  <Insert psig (kPa)>.

e. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

f. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

g. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below if cooling tower will be used in favorable weather as an economizer rather than operating water chillers.  See Evaluations.

4. Economizer Mode:

a. Fluid Flow/Cell:  <Insert gpm (L/s)>.

b. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

c. Leaving-Fluid Temperature:  <Insert deg F (deg C)>.

d. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

5. Fan Motor:

a. Type:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Variable speed].

b. Horsepower/Cell:  <Insert horsepower>.

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

6. Spray Pump and Motor:

a. Water Flow/Cell:  <Insert gpm (L/s)>.

b. Horsepower/Cell:  <Insert horsepower> .

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [120] [208] [240] [277] [480] <Insert value>-V ac, [single] [3] phase, 60 Hz.

7. Sound Pressure Level:  <Insert dBA> at <Insert distance in feet (m)> [when measured according to CTI ATC 128].

Retain subparagraph below for projects with basin heaters.

8. Basin Heater:

a. Basin Water Temperature:  [40 deg F (5 deg C)] <Insert deg F (deg C)>.

b. Outdoor Ambient Temperature:  [0 deg F (minus 18 deg C)] [Minus 20 deg F (Minus 29 deg C)] <Insert deg F (deg C)>.

Retain first five subparagraphs below for projects with electric basin heaters.

c. Capacity/Cell:  <Insert kilowatts>.

d. Full-Load Ampacity:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection Device:  <Insert amperage>.

g. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

Retain first four subparagraphs below for projects with hot-water-coil basin heaters.

h. Capacity/Cell:  <Insert MBtu/h (kW)>.

i. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

j. Fluid Flow Rate:  <Insert gpm (L/s)>.

k. Fluid Pressure Drop:  <Insert psig (kPa)>.

Retain three subparagraphs below for projects with steam-coil or -injection basin heaters.

l. Capacity/Cell:  <Insert MBtu/h (kW)>.

m. Steam Flow:  <Insert lb/h (L/s)>.

n. Steam Pressure:  <Insert psig (kPa)>.

2.4 OPEN-CIRCUIT, FORCED-DRAFT, COUNTERFLOW COOLING TOWERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

A. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Baltimore Aircoil Company; Models VTL, VTO, and VT1.

2. Delta Cooling Towers, Inc.; Model Pioneer.

3. Evapco Inc.; Models LRT and LSTA.

4. Tower Tech, Inc.; Model TTXE.

5. <Insert manufacturer's name; product name or designation>.

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; or delete option and insert manufacturer's name and model number if not including them on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Baltimore Aircoil Company.

2. Delta Cooling Towers, Inc.

3. Evapco Inc.

4. Tower Tech, Inc.

5. <Insert manufacturer's name>.

Retain first paragraph below for projects in seismic areas.

C. Fabricate cooling tower mounting base with reinforcement strong enough to resist cooling tower movement during a seismic event when cooling tower is anchored to field support structure.

D. Cooling tower designed to resist wind load of [30 lbf/sq. ft. (1.44 kPa)] <Insert value>.

E. Casing and Frame:

1. Casing[ and Frame] Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

Retain first subparagraph below and delete option in subparagraph heading above if frame material is different than casing.

2. Frame Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

3. Fasteners:  [Galvanized] [Stainless] steel.

4. Joints and Seams:  Sealed watertight.

5. Welded Connections:  Continuous and watertight.

Retain one of first two paragraphs below.  Retain first paragraph if collection basins are provided separate from cooling tower.

F. Collection Basin:  Configure tower for installation with a field-constructed collection basin.

G. Collection Basin:

1. Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Strainer:  Removable[ stainless-steel] strainer with openings smaller than nozzle orifices.

3. Overflow and drain connections.

4. Makeup water connection.

Retain subparagraph below for factory-installed basin sweeper distribution piping for field connection to field-installed filtration system to minimize sediment from collecting in the collection basin.  Not all listed manufacturers offer basin sweeper distribution piping.  Consult cooling tower manufacturers.

5. Basin Sweeper Distribution Piping and Nozzles:

a. Pipe Material:  [PVC] <Insert material>.

b. Nozzle Material:  [Plastic] <Insert material>.

c. Configure piping and nozzles to minimize sediment from collecting in the collection basin.

Retain one of first three paragraphs below if water-level control is to be provided with cooling tower.

H. Mechanically Operated, Collection Basin Water-Level Control:  Manufacturer's standard adjustable, mechanical float assembly and valve.

I. Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Sensor:  Solid-state controls with multiple electrode probes and relays factory wired to a terminal strip to provide [control of water makeup valve] [control of water makeup valve and low-level alarm] [control of water makeup valve and low- and high-level alarms] [control of water makeup valve, low- and high-level alarms, and output for shutoff of pump on low level].

3. Electrode Probes:  Stainless steel.

First option in first subparagraph below is less restrictive, while other options are limiting.

4. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

5. Solenoid Valve:  Slow closing[ with stainless-steel body], controlled and powered through level controller in response to water-level set point.

6. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

Retain one of first four paragraphs below to require basin heaters for Projects subject to freezing conditions.  See Evaluations.

J. Electric Basin Heater:

1. Stainless-Steel Electric Immersion Heaters:  Installed in a threaded coupling on the side of the collection basin.

2. Heater Control Panel:  Mounted on the side of each cooling tower cell.

3. Enclosure:  NEMA 250, [Type 3R] [Type 4] [Type 4X].

4. Magnetic contactors controlled by a temperature sensor/controller to maintain collection basin water-temperature set point.  Water-level probe shall monitor cooling tower water level and de-energize the heater when the water reaches low-level set point.

5. Control-circuit transformer with primary and secondary side fuses.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] and heater branch circuiting complying with NFPA 70.

8. Factory Wiring Method:  Metal raceway for factory-installed wiring outside of enclosures, except make connections to each electric basin heater with liquidtight conduit.

K. Hot-Water-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

L. Steam-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

M. Steam-Injector Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

N. Pressurized Water Distribution Piping:  Main header and lateral branch piping designed for even distribution over heat-exchanger coil or fill throughout the flow range without the need for balancing valves and for connecting individual, removable, nonclogging spray nozzles.

In first subparagraph below, PVC is manufacturer's most common standard offering.  Other requirements may require use of other materials.

1. Pipe Material:  [Fiberglass] [PVC] [Galvanized steel] <Insert material>.

2. Spray Nozzle Material:  [Plastic] [Polypropylene] [PVC] <Insert material>.

3. Piping Supports:  Corrosion-resistant hangers and supports to resist movement during operation and shipment.

O. Fill:

In first subparagraph below, PVC is manufacturer's most common standard offering.

1. Materials:  [PVC] <Insert material>, with maximum flame-spread index of 5 according to ASTM E 84.

Retain first subparagraph below if other than manufacturer's standard fill is required.  Thicker fill is used primarily in applications with elevated water temperatures.

2. Minimum Thickness:  [15 mils (0.4 mm)] [20 mils (0.5 mm)] <Insert value>, before forming.

3. Fabrication:  Fill-type sheets, fabricated, formed, and bonded together after forming into removable assemblies that are factory installed by manufacturer.

Consult manufacturers for fill options at elevated temperatures.

4. Fill Material Operating Temperature:  Suitable for entering-water temperatures up through [120 deg F (49 deg C)] <Insert temperature>.

Retain option in first paragraph below to limit placement of drift eliminators.

P. [Removable ]Drift Eliminator:

1. Material:  [FRP] [PVC] [FRP or PVC] <Insert material>; with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Configuration:  Multipass, designed and tested to reduce water carryover to achieve performance indicated.

Retain first paragraph below if screens are required.

Q. [Removable ]Air-Intake Screens:  [Galvanized] [Polymer-coated, galvanized] [Stainless]-steel wire mesh.

Retain one or both of first two paragraphs below.  Retaining only second paragraph could result in a proprietary product.

R. Centrifugal Fan:  Double-width, double-inlet, forward-curved blades, and statically and dynamically balanced at the factory after assembly.

1. Number of Fans:  Each cooling tower cell shall have a single fan or multiple fans connected to a common shaft.

2. Fan Wheel and Housing Materials:  Galvanized steel.

3. Fan Shaft:  Steel, coated to resist corrosion.

4. Protective Enclosure:  Removable, galvanized-steel, wire-mesh screens complying with OSHA regulations.

5. Fan Shaft Bearings:  Self-aligning, grease-lubricated ball or roller bearings with moisture-proof seals and premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).  Bearings designed for an L-10 life of [40,000] [50,000] <Insert value> hours.

6. Bearings Grease Fittings:  Extended lubrication lines to an easily accessible location.

First paragraph below is available only from Tower Tech.  See Evaluations.

S. Axial Fan:  Balanced at the factory after assembly.

1. Blade Material:  [FRP] <Insert material>.

2. Hub Material:  [Aluminum] [FRP] <Insert material>.

First subparagraph below is an optional feature.  Retain, based on Project conditions, to require feature.

3. Blade Pitch:  Field adjustable.

4. Protective Enclosure:  Removable, galvanized-steel, wire-mesh screens complying with OSHA regulations.

5. Fan Shaft Bearings:  Self-aligning ball or roller bearings with moisture-proof seals and premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).  Bearings designed for an L-10 life of [40,000] [50,000] <Insert value> hours.

6. Bearings Grease Fittings:  Extended lubrication lines to an easily accessible location.

T. Belt Drive:

1. Service Factor:  [1.5] <Insert value> based on motor nameplate horsepower.

2. Sheaves:  Fan and motor shafts shall have taper-lock sheaves fabricated from corrosion-resistant materials.

Retain one of first two subparagraphs below.  Second subparagraph provides better performance.

3. Belt:  Multiple V-belt design with a matched set of[ cogged] belts.

4. Belt:  One-piece, multigrooved, solid-back belt.

5. Belt Material:  Oil resistant, nonstatic conducting, and constructed of neoprene polyester cord.

6. Belt-Drive Guard:  Comply with OSHA regulations.

Retain subparagraph below if Project requires functionality of a single fan with two motors.  Feature is proprietary.  See Evaluations.

7. Two-Motor, Single-Fan Drive:

a. Two single-speed motors per fan, one sized for full speed and load and the other sized for [67] <Insert value> percent of full-load speed.

b. Each motor with belt drive and configured for operation when other motor fails.

c. Controls and wiring same as two-speed, two-winding motor.

First paragraph below is available only from Tower Tech.  See Evaluations.

U. Direct Drive:  Fan hub directly connected, and properly secured, to motor shaft.

V. Fan Motor:

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Fan Motors:  Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

2. Motor Enclosure:  [Totally enclosed] [Totally enclosed air over (TEAO)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

3. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Service Factor:  [1.15] <Insert value>.

5. Insulation:  [Class F] [Class H] <Insert class>.

6. Variable-Speed Motors:  Inverter-duty rated per NEMA MG-1, Section IV, "Performance Standard Applying to All Machines," Part 31, "Definite-Purpose, Inverter-Fed, Polyphase Motors."

Retain first subparagraph below, based on Project conditions, to require additional protection.

7. Severe-duty rating with the following features:

a. Rotor and stator protected with corrosion-inhibiting epoxy resin.

b. Double-shielded, vacuum-degassed bearings lubricated with premium, moisture-resistant grease suitable for temperatures between minus 20 and 300 deg F (minus 29 and 149 deg C).

First subparagraph below requires a separate, single-phase, field-power connection for heater operation.

c. Internal heater automatically energized when motor is de-energized.

Retain subparagraph below for belt-drive units.

8. Motor Base:  Adjustable, or other suitable provision for adjusting belt tension.

Retain first paragraph below if cooling tower requires a discharge hood.  See Evaluations.

W. Discharge Hoods:

1. Hood Configuration:  [Tapered] [Straight]; totally surrounding drift eliminators and constructed of same material as casing; and having factory-installed [insulation and ] access doors.

Retain subparagraph below if discharge dampers are required.

2. Discharge Dampers:  Positive-closure, automatic, isolation dampers with electric actuators.

Retain subparagraph below if cooling towers are not provided with factory-installed and -wired control package.

a. Provide field power and controls to open dampers when pump is energized and close dampers when pump is de-energized.

Retain first paragraph below if Project requires capacity-control dampers to improve leaving-water temperature control.

X. Capacity-Control Dampers:  [Galvanized-steel] [Stainless-steel] <Insert material> dampers, with linkages, electric operator, controller, limit switches, transformer, and weatherproof enclosure.

Retain first paragraph below to require a vibration switch furnished with cooling tower.

Y. Vibration Switch:  For each fan drive.

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Vibration Detection:  Sensor with a field-adjustable, acceleration-sensitivity set point in a range of 0 to 1 g and frequency range of 0 to 3000 cycles per minute.  Cooling tower manufacturer shall recommend switch set point for proper operation and protection.

3. Provide switch[ with manual-reset button] for [field connection to a BMS and ]hardwired connection to fan motor electrical circuit.

4. Switch shall, on sensing excessive vibration,[ signal an alarm through the BMS and] shut down the fan.

Retain first paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC." Retain second paragraph if controls are provided with cooling tower.

Z. Controls:  Comply with requirements in Division 23 Section "Instrumentation and Control for HVAC."

Retain first paragraph below, based on Project conditions, to require cooling tower to be equipped with factory-installed control package.  Not all manufacturers offer factory-installed control packages; those that do offer control packages have limited features available with the package.  Consult manufacturers for additional information.

AA. Control Package:  Factory installed and wired, and functionally tested at factory before shipment.

Sixteen subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features and to correspond with components retained in paragraphs above.

1. NEMA 250, [Type 3R] [Type 4] [Type 4X] enclosure with removable internally mount backplate.

2. Control-circuit transformer with primary and secondary side fuses.

3. Terminal blocks with numbered and color-coded wiring to match wiring diagram.  Spare wiring terminal block for connection to external controls or equipment.

4. Microprocessor-based controller for automatic control of fan based on cooling tower leaving-water temperature with control features to improve operating efficiency based on outdoor ambient wet-bulb temperature by using adaptive logic.

5. Fan motor sequencer for multiple-cell and two-speed applications with automatic lead stage rotation.

6. Factory-installed and -wired, collection basin electric/electronic level controller.

If retaining "Mechanically Operated, Collection Basin Water-Level Control" Paragraph, delete first subparagraph below.

7. Collection basin electric/electronic level controller complying with requirements in "Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve" Paragraph.

8. Electric basin heaters with temperature control and low-water-level safety switch for each cell, complying with requirements in "Electric Basin Heater" Paragraph.

9. Vibration switch for each fan, complying with requirements in "Vibration Switch" Paragraph.

10. Controls and wiring for "two-motor, single-fan drives" shall be same as two-speed, two-winding motor.

11. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] [for each cooling tower cell].

a. Branch power circuit to each motor and electric basin heater and to controls[ with a disconnect switch or circuit breaker].

b. NEMA-rated motor controller, hand-off-auto switch, and overcurrent protection for each motor.  Provide variable frequency controller with manual bypass and line reactors for each variable-speed motor indicated.

12. Factory-installed wiring outside of enclosures shall be in metal raceway, except make connections to each motor and electric basin heater with liquidtight conduit.

13. Visual indication of status and alarm[ with momentary test push button] for each motor.

Retain first subparagraph below for audible alarm.  Coordinate with control sequence.

14. Audible alarm and silence switch.

15. Visual indication of elapsed run time, graduated in hours for each motor.

Retain subparagraph below if unit controls interface with BMS.

16. Cooling tower shall have hardware to enable BMS to remotely monitor and display the following:

Subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features.

a. Operational status of each motor.

b. Position of dampers.

c. Cooling tower leaving-fluid temperature.

d. Fan vibration alarm.

e. Collection basin [high] [low] [high- and low]-water-level alarms.

f. <Insert conditions to be monitored>.

AB. Personnel Access Components:

Five subparagraphs below are optional components.  Retain applicable subparagraphs, based on Project conditions, to require these components.

1. Doors:  Large enough for personnel to access cooling tower internal components from both cooling tower end walls.  Doors shall be operable from both sides of the door.

2. External Ladders with Safety Cages:  Aluminum, galvanized- or stainless-steel, fixed ladders with ladder extensions to access external platforms and top of cooling tower from adjacent grade without the need for portable ladders.  Comply with 29 CFR 1910.27.

3. External Platforms with Handrails:  Aluminum, FRP, or galvanized-steel bar grating at cooling tower access doors when cooling towers are elevated and not accessible from grade.

4. Handrail:  Aluminum, galvanized steel, or stainless steel complete with kneerail and toeboard, around top of cooling tower.  Comply with 29 CFR 1910.23.

5. Internal Platforms:  Aluminum, FRP, or galvanized-steel bar grating.

a. Spanning the collection basin from one end of cooling tower to the other and positioned to form a path between the access doors.  Platform shall be elevated so that all parts are above the high water level of the collection basin.

b. Elevated internal platforms with handrails accessible from fixed vertical ladders to access the fan drive assembly when out of reach from collection basin platform.

If Project has more than one type or configuration cooling tower, delete paragraph below and schedule cooling towers on Drawings.

AC. Capacities and Characteristics:

1. Number of Cells:  <Insert quantity>.

2. Air-Inlet Arrangement:  [Single side] [Four sides].

3. Maximum Drift Loss:  [0.005] <Insert number> percent of design water flow.

4. Water Flow/Cell:  <Insert gpm (L/s)>.

5. Minimum Water Flow/Cell:  <Insert gpm (L/s)>.

6. Water Pressure Drop:  <Insert psig (kPa)>.

7. Entering-Water Temperature:  <Insert deg F (deg C)>.

8. Leaving-Water Temperature:  <Insert deg F (deg C)>.

9. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below if cooling tower will be used in favorable weather as an economizer rather than operating water chillers.  See Evaluations.

10. Economizer Mode:

a. Water Flow/Cell:  <Insert gpm (L/s)>.

b. Entering-Water Temperature:  <Insert deg F (deg C)>.

c. Leaving-Water Temperature:  <Insert deg F (deg C)>.

d. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

11. Fan Location:  [Bottom] [Side] [Bottom or side].

Retain first subparagraph below to allow Contractor to choose fan type.  Coordinate with "Axial Fan" and "Centrifugal Fan" paragraphs above.

12. Fan and Drive Type:  Axial with direct drive or centrifugal with belt drive.

13. Fan Motor:

a. Type:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Variable speed].

b. Horsepower/Cell:  <Insert horsepower>.

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

14. Sound Pressure Level:  <Insert dBA> at <Insert distance in feet (m)> [when measured according to CTI ATC 128].

Retain subparagraph below for projects with basin heaters.

15. Basin Heater:

a. Basin Water Temperature:  [40 deg F (5 deg C)] <Insert deg F (deg C)>.

b. Outdoor Ambient Temperature:  [0 deg F (minus 18 deg C)] [Minus 20 deg F (Minus 29 deg C)] <Insert deg F (deg C)>.

Retain first five subparagraphs below for projects with electric basin heaters.

c. Capacity/Cell:  <Insert kilowatts>.

d. Full-Load Ampacity:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection Device:  <Insert amperage>.

g. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

Retain first four subparagraphs below for projects with hot-water-coil basin heaters.

h. Capacity/Cell:  <Insert MBtu/h (kW)>.

i. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

j. Fluid Flow Rate:  <Insert gpm (L/s)>.

k. Fluid Pressure Drop:  <Insert psig (kPa)>.

Retain three subparagraphs below for projects with steam-coil or -injection basin heaters.

l. Capacity/Cell:  <Insert MBtu/h (kW)>.

m. Steam Flow:  <Insert lb/h (L/s)>.

n. Steam Pressure:  <Insert psig (kPa)>.

2.5 OPEN-CIRCUIT, INDUCED-DRAFT, COUNTERFLOW COOLING TOWERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

A. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Amcot Cooling Tower Corp.; Model ST.

2. Delta Cooling Towers, Inc.; Model Paragon, Premier, TM Series.

3. Evapco Inc.; Models AT, ICT, REP, UBT, and USS.

4. Protec Cooling Towers, Inc.; Model PTC.

5. Recold; Model MT.

6. Thermal Care, Inc., a division of MFRI, Inc.; Models FC and FT.

7. <Insert manufacturer's name; product name or designation>.

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; or delete option and insert manufacturer's name and model number if not including them on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Amcot Cooling Tower Corp.

2. Delta Cooling Towers, Inc.

3. Evapco Inc.

4. Protec Cooling Towers, Inc.

5. Recold.

6. Thermal Care, Inc., a division of MFRI, Inc.

7. <Insert manufacturer's name>.

Retain first paragraph below for projects in seismic areas.

C. Fabricate cooling tower mounting base with reinforcement strong enough to resist cooling tower movement during a seismic event when cooling tower is anchored to field support structure.

D. Cooling tower designed to resist wind load of [30 lbf/sq. ft. (1.44 kPa)] <Insert value>.

E. Casing and Frame:

1. Casing[ and Frame] Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Stainless steel].

Retain first subparagraph below and delete option in subparagraph heading above if frame material is different than casing.

2. Frame Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Stainless steel].

3. Fasteners:  [Galvanized] [Stainless] steel.

4. Joints and Seams:  Sealed watertight.

5. Welded Connections:  Continuous and watertight.

Retain one of first two paragraphs below.  Retain first paragraph if collection basins are provided separate from cooling tower.

F. Collection Basin:  Configure tower for installation with a field-constructed collection basin.

G. Collection Basin:

1. Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G210 (Z600) coating] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Strainer:  Removable[ stainless-steel] strainer with openings smaller than nozzle orifices.

3. Overflow and drain connections.

4. Makeup water connection.

5. Outlet Connection:  ASME B16.5, Class 150 flange.

If Project has a multiple-cell cooling tower or multiple cooling towers, retain one of first two subparagraphs below.

6. Removable equalization flume plate between adjacent cells of multiple-cell towers.

7. Equalizer connection for field-installed equalizer piping.

Retain subparagraph below for factory-installed basin sweeper distribution piping for field connection to field-installed filtration system to minimize sediment from collecting in the collection basin.  Not all listed manufacturers offer basin sweeper distribution piping.  Consult cooling tower manufacturers.

8. Basin Sweeper Distribution Piping and Nozzles:

a. Pipe Material:  [PVC] <Insert material>.

b. Nozzle Material:  [Plastic] <Insert material>.

c. Configure piping and nozzles to minimize sediment from collecting in the collection basin.

Retain one of first three paragraphs below if water-level control is to be provided with cooling tower.

H. Mechanically Operated, Collection Basin Water-Level Control:  Manufacturer's standard adjustable, mechanical float assembly and valve.

I. Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Sensor:  Solid-state controls with multiple electrode probes and relays factory wired to a terminal strip to provide [control of water makeup valve] [control of water makeup valve and low-level alarm] [control of water makeup valve and low- and high-level alarms] [control of water makeup valve, low- and high-level alarms, and output for shutoff of pump on low level].

3. Electrode Probes:  Stainless steel.

First option in first subparagraph below is less restrictive, while other options are limiting.

4. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

5. Solenoid Valve:  Slow closing[ with stainless-steel body]; controlled and powered through level controller in response to water-level set point.

6. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

J. Ultrasonic Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Controller:  Ultrasonic level sensor/transmitter and relays factory wired to a terminal strip to control water makeup valve and signal a level alarm.  Controller shall provide continuous level indication through a 4- to 20-mA signal[ for connection to BMS].

First option in first subparagraph below is less restrictive, while other options are limiting.

3. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

4. Solenoid Valve:  Slow closing[ with stainless-steel body]; controlled and powered through level controller in response to water-level set point.

5. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

Retain one of first four paragraphs below to require basin heaters for projects subject to freezing conditions.  See Evaluations.

K. Electric Basin Heater:

1. Stainless-Steel Electric Immersion Heaters:  Installed in a threaded coupling on the side of the collection basin.

2. Heater Control Panel:  Mounted on the side of each cooling tower cell.

3. Enclosure:  NEMA 250, [Type 3R] [Type 4] [Type 4X].

4. Magnetic contactors controlled by a temperature sensor/controller to maintain collection basin water-temperature set point.  Water-level probe shall monitor cooling tower water level and de-energize the heater when the water reaches low-level set point.

5. Control-circuit transformer with primary and secondary side fuses.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] and heater branch circuiting complying with NFPA 70.

8. Factory Wiring Method:  Metal raceway for factory-installed wiring outside of enclosures, except make connections to each electric basin heater with liquidtight conduit.

L. Hot-Water-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

M. Steam-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

N. Steam-Injector Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

O. Pressurized Water Distribution Piping:  Main header and lateral branch piping designed for even distribution over heat-exchanger coil or fill throughout the flow range without the need for balancing valves and for connecting individual, removable, nonclogging spray nozzles.

In first subparagraph below, PVC is manufacturer's most common standard offering.  Other requirements may require use of other materials.

1. Pipe Material:  [Fiberglass] [PVC] [Galvanized steel] <Insert material>.

2. Spray Nozzle Material:  [Plastic] [Polypropylene] [PVC] <Insert material>.

3. Piping Supports:  Corrosion-resistant hangers and supports to resist movement during operation and shipment.

P. Fill:

In first subparagraph below, PVC is manufacturer's most common standard offering.

1. Materials:  [CPVC] [PVC] <Insert material>, resistant to rot, decay, and biological attack; with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

Retain first subparagraph below if other than manufacturer's standard fill is required.  Thicker fill is used primarily in applications with elevated water temperatures.

2. Minimum Thickness:  [15 mils (0.4 mm)] [20 mils (0.5 mm)] <Insert value> before forming.

3. Fabrication:  Fill-type sheets, fabricated, formed, and bonded together after forming into removable assemblies that are factory installed by manufacturer.

Consult manufacturers for fill options at elevated temperatures.

4. Fill Material Operating Temperature:  Suitable for entering-water temperatures up through [120 deg F (49 deg C)] <Insert temperature>.

Retain option in first paragraph below to limit placement of drift eliminators.

Q. [Removable ]Drift Eliminator:

1. Material:  [FRP] [PVC] [FRP or PVC] <Insert material>; resistant to rot, decay, and biological attack; with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Configuration:  Multipass, designed and tested to reduce water carryover to achieve performance indicated.

R. Air-Intake Louvers:

1. Material:  [FRP] [PVC] [Matching casing].

Retain first subparagraph below with FRP or PVC louvers.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Louver Blades:  Arranged to uniformly direct air into cooling tower, to minimize air resistance, and to prevent water from splashing out of tower during all modes of operation including operation with fans off.

Retain first paragraph below if screens are required.

S. [Removable ]Air-Intake Screens:  [Galvanized] [Polymer-coated, galvanized] [Stainless]-steel wire mesh.

T. Axial Fan:  Balanced at the factory after assembly.

1. Blade Material:  [Aluminum] [FRP] [Galvanized steel].

2. Hub Material:  [Aluminum] [FRP] [Galvanized steel].

First subparagraph below is an optional feature.  Retain, based on Project conditions, to require feature.

3. Blade Pitch:  Field adjustable.

4. Protective Enclosure:  Removable, galvanized-steel, wire-mesh screens, complying with OSHA regulations.

5. Fan Shaft Bearings:  Self-aligning ball or roller bearings with moisture-proof seals and premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).  Bearings designed for an L-10 life of [40,000] [50,000] <Insert value> hours.

6. Bearings Grease Fittings:  Extended lubrication lines to an easily accessible location.

Retain first paragraph below if belt drive is used.  See Evaluations.

U. Belt Drive:

1. Service Factor:  [1.5] <Insert value> based on motor nameplate horsepower.

2. Sheaves:  Fan and motor shafts shall have taper-lock sheaves fabricated from corrosion-resistant materials.

Retain one of first two subparagraphs below.  Second subparagraph provides better performance.

a. Belt:  Multiple V-belt design with a matched set of[ cogged] belts.

b. Belt:  One-piece, multigrooved, solid-back belt.

c. Belt Material:  Oil resistant, nonstatic conducting, and constructed of neoprene polyester cord.

d. Belt-Drive Guard:  Comply with OSHA regulations.

Retain first paragraph below if direct drive is used.  See Evaluations.

V. Direct Drive:  Fan hub directly connected, and properly secured, to motor shaft.

Retain first paragraph below if gear drive is used.  See Evaluations.

W. Gear Drive:  Right angle, reduced speed, and designed for cooling tower applications according to CTI STD 111.  Motor and gear drive shall be aligned before shipment.

1. Gear Drive and Coupling Service Factor:  [2.0] <Insert value> based on motor nameplate horsepower.

2. Housing:  Cast iron, with epoxy or polyurethane finish, beveled high-strength steel gears continuously bathed in oil, and with lubrication to other internal parts at all operating speeds.

3. Mounting:  Directly mounted to fan hub and connected to motor so motor shaft is in horizontal position.

4. Operation:  Able to operate both forward and in reverse.

Coordinate motor requirements with options in first subparagraph below.

5. Drive-to-Motor Connection:  [Close coupled to motor using a flexible coupling] [Connected to motor located outside of cooling tower casing by a full-floating drive shaft].

Retain first subparagraph below with second option in last subparagraph above.

6. Drive Shaft Material:  [Corrosion resistant] [Stainless steel], and fitted with flexible couplings on both ends.  Provide exposed shaft and couplings with guards according to OSHA regulations.

7. Extend oil fill, drain, and vent to outside of cooling tower casing using galvanized-steel piping.  Provide installation with oil-level sight glass.

X. Fan Motor:

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Fan Motors: Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

2. Motor Enclosure:  [Totally enclosed] [Totally enclosed air over (TEAO)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

3. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Service Factor:  [1.15] <Insert value>.

5. Insulation:  [Class F] [Class H] <Insert class>.

6. Variable-Speed Motors:  Inverter-duty rated per NEMA MG-1, Section IV, "Performance Standard Applying to All Machines," Part 31, "Definite-Purpose, Inverter-Fed, Polyphase Motors."

Retain first subparagraph below if Project requires specific motor location.  Standard offering by most manufacturers is motor mounted internally or in the airstream.

7. Motor Location:  Mounted outside of cooling tower casing and cooling tower discharge airstream.

Retain first subparagraph below, based on Project conditions, to require additional protection.

8. Severe-duty rating with the following features:

a. Rotor and stator protected with corrosion-inhibiting epoxy resin.

b. Double-shielded, vacuum-degassed bearings lubricated with premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).

First subparagraph below requires a separate, single-phase, field-power connection for heater operation.

c. Internal heater automatically energized when motor is de-energized.

Retain subparagraph below for belt-drive units.

9. Motor Base:  Adjustable, or other suitable provision for adjusting belt tension.

Y. Fan Discharge Stack:  Material shall match casing, [manufacturer's standard] [velocity recovery] design.

Retain first subparagraph below to if Project requires a minimum stack height to clear an obstruction.

1. Stack Extension:  Fabricated to extend above fan deck <Insert distance> unless otherwise indicated.

2. Stack Termination:  Wire-mesh, galvanized-steel screens; complying with OSHA regulations.

Retain first paragraph below to require a vibration switch furnished with cooling tower.

Z. Vibration Switch:  For each fan drive.

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Vibration Detection:  Sensor with a field-adjustable, acceleration-sensitivity set point in a range of 0 to 1 g and frequency range of 0 to 3000 cycles per minute.  Cooling tower manufacturer shall recommend switch set point for proper operation and protection.

3. Provide switch[ with manual-reset button] for [field connection to a BMS and ]hardwired connection to fan motor electrical circuit.

4. Switch shall, on sensing excessive vibration,[ signal an alarm through the BMS and] shut down the fan.

Retain first paragraph below for cooling towers with fan gear drives to require an oil-level switch furnished with cooling tower.

AA. Gear-Drive, Oil-Level Switch:  Low-oil-level warning switch[ for connection to a BMS].

1. Switch shall, on reaching a low-oil-level set point recommended by cooling tower manufacturer, signal an alarm[ through the BMS].

Retain first paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC." Retain second paragraph if controls are provided with cooling tower.

AB. Controls:  Comply with requirements in Division 23 Section "Instrumentation and Control for HVAC."

Retain first paragraph below, based on Project conditions, to require cooling tower to be equipped with factory-installed controls.  Not all manufacturers offer factory-installed control packages; those that do offer control packages have limited features available with the package.  Consult manufacturers for additional information.

AC. Control Package:  Factory installed and wired, and functionally tested at factory before shipment.

Fifteen subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features and to correspond with components retained in paragraphs above.

1. NEMA 250, [Type 3R] [Type 4] [Type 4X] enclosure with removable internally mount backplate.

2. Control-circuit transformer with primary and secondary side fuses.

3. Terminal blocks with numbered and color-coded wiring to match wiring diagram.  Spare wiring terminal block for connection to external controls or equipment.

4. Microprocessor-based controller for automatic control of fan based on cooling tower leaving-water temperature with control features to improve operating efficiency based on outdoor ambient wet-bulb temperature by using adaptive logic.

5. Fan motor sequencer for multiple-cell and two-speed applications with automatic lead stage rotation.

If retaining "Mechanically Operated, Collection Basin Water-Level Control" Paragraph, delete first subparagraph below.

6. Collection basin level controller complying with requirements in ["Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve"] ["Ultrasonic Collection Basin Water-Level Controller with Solenoid Valve"] Paragraph.

7. Electric basin heaters with temperature control and low-water-level safety switch for each cell, complying with requirements in "Electric Basin Heater" Paragraph.

8. Vibration switch for each fan, complying with requirements in "Vibration Switch" Paragraph.

9. Oil-level switch for each fan with a gear drive, complying with requirement in "Gear-Drive, Oil-Level Switch" Paragraph.

10. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] [for each cooling tower cell].

a. Branch power circuit to each motor and electric basin heater and to controls[ with a disconnect switch or circuit breaker].

b. NEMA-rated motor controller, hand-off-auto switch, and overcurrent protection for each motor.  Provide variable frequency controller with manual bypass and line reactors for each variable-speed motor indicated.

11. Factory-installed wiring outside of enclosures shall be in metal raceway, except make connections to each motor and electric basin heater with liquidtight conduit.

12. Visual indication of status and alarm[ with momentary test push button] for each motor.

Retain first subparagraph below for audible alarm.  Coordinate with control sequence.

13. Audible alarm and silence switch.

14. Visual indication of elapsed run time, graduated in hours for each motor.

Retain subparagraph below if unit controls interface with BMS.

15. Cooling tower shall have hardware to enable BMS to remotely monitor and display the following:

Seven subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features.

a. Operational status of each motor.

b. Position of dampers.

c. Cooling tower leaving-fluid temperature.

d. Fan vibration alarm.

Retain first subparagraph below if Project requires an oil-level alarm through BMS.  Coordinate requirements with "Gear-Drive, Oil-Level Switch" Paragraph.

e. Oil-level alarm.

f. Collection basin [high] [low] [high- and low]-water-level alarms.

g. <Insert conditions to be monitored>.

AD. Personnel Access Components:

Five subparagraphs below are optional components.  Retain applicable subparagraphs, based on Project conditions, to require these components.

1. Doors:  Large enough for personnel to access cooling tower internal components from both cooling tower end walls.  Doors shall be operable from both sides of the door.

2. External Ladders with Safety Cages:  Aluminum, galvanized- or stainless-steel, fixed ladders with ladder extensions to access external platforms and top of cooling tower from adjacent grade without the need for portable ladders.  Comply with 29 CFR 1910.27.

3. External Platforms with Handrails:  Aluminum, FRP, or galvanized-steel bar grating at cooling tower access doors when cooling towers are elevated and not accessible from grade.

4. Handrail:  Aluminum, galvanized steel, or stainless steel complete with kneerail and toeboard, around top of cooling tower.  Comply with 29 CFR 1910.23.

5. Internal Platforms:  Aluminum, FRP, or galvanized-steel bar grating.

a. Spanning the collection basin from one end of cooling tower to the other and positioned to form a path between the access doors.  Platform shall be elevated so that all parts are above the high water level of the collection basin.

b. Elevated internal platforms with handrails accessible from fixed vertical ladders to access the fan drive assembly when out of reach from collection basin platform.

If Project has more than one type or configuration of cooling tower, delete paragraph below and schedule cooling towers on Drawings.

AE. Capacities and Characteristics:

1. Number of Cells:  <Insert quantity>.

2. Air-Inlet Arrangement:  All sides.

3. Maximum Drift Loss:  [0.005] <Insert number> percent of design water flow.

4. Water Flow/Cell:  <Insert gpm (L/s)>.

5. Minimum Water Flow/Cell:  <Insert gpm (L/s)>.

6. Water Pressure Drop:  <Insert psig (kPa)>.

7. Entering-Water Temperature:  <Insert deg F (deg C)>.

8. Leaving-Water Temperature:  <Insert deg F (deg C)>.

9. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below if cooling tower will be used in favorable weather as an economizer rather than operating water chillers.  See Evaluations.

10. Economizer Mode:

a. Water Flow/Cell:  <Insert gpm (L/s)>.

b. Entering-Water Temperature:  <Insert deg F (deg C)>.

c. Leaving-Water Temperature:  <Insert deg F (deg C)>.

d. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below to allow Contractor to choose drive type.  Coordinate with "Belt Drive," "Direct Drive," and "Gear Drive" paragraphs above.

11. Fan Drive:  Belt, direct, or gear.

12. Fan Motor:

a. Type:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Variable speed].

b. Horsepower/Cell:  <Insert horsepower>.

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

13. Sound Pressure Level:  <Insert dBA> at <Insert distance in feet (m)> [when measured according to CTI ATC 128].

Retain subparagraph below for projects with basin heaters.

14. Basin Heater:

a. Basin Water Temperature:  [40 deg F (5 deg C)] <Insert deg F (deg C)>.

b. Outdoor Ambient Temperature:  [0 deg F (minus 18 deg C)] [Minus 20 deg F (Minus 29 deg C)] <Insert deg F (deg C)>.

Retain first five subparagraphs below for projects with electric basin heaters.

c. Capacity/Cell:  <Insert kilowatts>.

d. Full-Load Ampacity:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection Device:  <Insert amperage>.

g. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

Retain first four subparagraphs below for projects with hot-water-coil basin heaters.

h. Capacity/Cell:  <Insert MBtu/h (kW)>.

i. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

j. Fluid Flow Rate:  <Insert gpm (L/s)>.

k. Fluid Pressure Drop:  <Insert psig (kPa)>.

Retain three subparagraphs below for projects with steam-coil or -injection basin heaters.

l. Capacity/Cell:  <Insert MBtu/h (kW)>.

m. Steam Flow:  <Insert lb/h (L/s)>.

n. Steam Pressure:  <Insert psig (kPa)>.

2.6 OPEN-CIRCUIT, INDUCED-DRAFT, CROSSFLOW COOLING TOWERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

A. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Amcot Cooling Tower Corp.; Models LRC-H, LRC-LNS Series.

2. Baltimore Aircoil Company; Series 1500 and 3000.

3. Marley Cooling Technologies, an SPX Corporation; Models Aquatower, AV series, NC Class, Primus.

4. <Insert manufacturer's name; product name or designation>.

If retaining first paragraph below, retain option if manufacturer's name and model number are indicated in schedules or plans on Drawings; or delete option and insert manufacturer's name and model number if not including them on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Amcot Cooling Tower Corp.

2. Baltimore Aircoil Company.

3. Marley Cooling Technologies; an SPX Corporation.

4. <Insert manufacturer's name>.

Retain first paragraph below for projects in seismic areas.

C. Fabricate cooling tower mounting base with reinforcement strong enough to resist cooling tower movement during a seismic event when cooling tower is anchored to field support structure.

D. Cooling tower designed to resist wind load of [30 lbf/sq. ft. (1.44 kPa)] <Insert value>.

E. Casing and Frame:

1. Casing[ and Frame] Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

Retain first subparagraph below and delete option in subparagraph heading above if frame material is different than casing.

2. Frame Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

3. Fasteners:  [Galvanized] [Stainless] steel.

4. Joints and Seams:  Sealed watertight.

5. Welded Connections:  Continuous and watertight.

Retain one of first two paragraphs below.  Retain first paragraph if collection basins are provided separate from cooling tower.

F. Collection Basin:  Configure tower for installation with a field-constructed collection basin.

G. Collection Basin:

1. Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Removable[ stainless-steel] strainer with openings smaller than nozzle orifices.

3. Overflow and drain connections.

4. Makeup water connection.

5. Outlet Connection:  ASME B16.5, Class 150 flange.

If Project has a multiple-cell cooling tower or multiple cooling towers, retain one of first two subparagraphs below.

6. Removable equalization flume plate between adjacent cells of multiple-cell towers.

7. Equalizer connection for field-installed equalizer piping.

Retain subparagraph below for factory-installed basin sweeper distribution piping for field connection to field-installed filtration system to minimize sediment from collecting in the collection basin.  Not all listed manufacturers offer basin sweeper distribution piping.  Consult cooling tower manufacturers.

8. Basin Sweeper Distribution Piping and Nozzles:

a. Pipe Material:  [PVC] <Insert material>.

b. Nozzle Material:  [Plastic] <Insert material>.

c. Configure piping and nozzles to minimize sediment from collecting in the collection basin.

Retain one of first three paragraphs below if water-level control is to be provided with cooling tower.

H. Mechanically Operated, Collection Basin Water-Level Control:  Manufacturer's standard adjustable, mechanical float assembly and valve.

I. Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosures:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Sensor:  Solid-state controls with multiple electrode probes and relays factory wired to a terminal strip to provide [control of water makeup valve] [control of water makeup valve and low-level alarm] [control of water makeup valve and low- and high-level alarms] [control of water makeup valve, low- and high-level alarms, and output for shutoff of pump on low level].

3. Electrode Probes:  Stainless steel.

First option in first subparagraph below is less restrictive, while other options are limiting.

4. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

5. Solenoid Valve:  Slow closing[ with stainless-steel body], controlled and powered through level controller in response to water-level set point.

6. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

J. Ultrasonic Collection Basin Water-Level Controller with Solenoid Valve:

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Controller:  Ultrasonic level sensor/transmitter and relays factory wired to a terminal strip to control water makeup valve and signal a level alarm.  Controller shall provide continuous level indication through a 4- to 20-mA signal[ for connection to BMS].

First option in first subparagraph below is less restrictive, while other options are limiting.

3. Water Stilling Chamber:  [Corrosion-resistant material] [FRP] [Galvanized steel] [PVC pipe] [Stainless steel].

4. Solenoid Valve:  Slow closing[ with stainless-steel body]; controlled and powered through level controller in response to water-level set point.

5. Electrical Connection Requirements:  120 V, single phase, 60 Hz.

Retain one of first four paragraphs below to require basin heaters for projects subject to freezing conditions.  See Evaluations.

K. Electric Basin Heater:

1. Stainless-Steel Electric Immersion Heaters:  Installed in a threaded coupling on the side of the collection basin.

2. Heater Control Panel:  Mounted on the side of each cooling tower cell.

3. Enclosure:  NEMA 250, [Type 3R] [Type 4] [Type 4X].

4. Magnetic contactors controlled by a temperature sensor/controller to maintain collection basin water-temperature set point.  Water-level probe shall monitor cooling tower water level and de-energize the heater when the water reaches low-level set point.

5. Control-circuit transformer with primary and secondary side fuses.

6. Terminal blocks with numbered and color-coded wiring to match wiring diagram.

7. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] and heater branch circuiting complying with NFPA 70.

8. Factory Wiring Method:  Metal raceway for factory-installed wiring outside of enclosures, except make connections to each electric basin heater with liquidtight conduit.

L. Hot-Water-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

M. Steam-Coil Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

N. Steam-Injector Basin Heater:  Manufacturer's standard offering to provide capacity indicated.

O. Gravity Water Distribution Basin:  Nonpressurized design with head of water level in basin adequate to overcome spray nozzle losses and designed to evenly distribute water over fill throughout the flow range indicated.

1. Material:  [FRP with UV inhibitors] [Galvanized steel, ASTM A 653/A 653M, G235 (Z700) coating] [Polymer-coated galvanized steel] [Stainless steel].

2. Location:  Over each bank of fill with easily replaceable [plastic] <Insert material> spray nozzles mounted in bottom of basin.

3. Inlet Connection:  ASME B16.5, Class 150 flange.

4. Joints and Seams:  Sealed watertight.

Retain first subparagraph below for projects subject to freezing conditions.

5. Partitioning Dams:  Same material as basin to distribute water over the fill to minimize icing while operating throughout the flow range indicated.

6. Removable Panels:  Same material as basin to completely cover top of basin.  Secure panels to basin with removable [corrosion-resistant] [stainless-steel] hardware.

Retain first subparagraph below if valves are to be provided with cooling tower.  Delete if retaining "Single-Inlet, Field Pipe Connection" Subparagraph below.

7. Valves:  Manufacturer's standard valve installed at each inlet connection and arranged to balance or shut off flow to each gravity distribution basin.

Retain subparagraph below for a single-inlet pipe connection.

8. Single-Inlet, Field Pipe Connection:  [Galvanized-steel] [PVC] pipe arranged to provide balancing of flow within cooling tower cell without the need for additional balancing valves.  Pipe each cooling tower cell internally to a single, field connection suitable for mating to ASME B16.5, Class 150 flange and located on the [bottom] [side] unless otherwise indicated.

P. Fill:

1. Materials:  PVC, with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

Retain first subparagraph below if other than manufacturer's standard fill is required.  Thicker fill is used primarily in applications with elevated water temperatures.

2. Minimum Thickness:  [15 mils (0.4 mm)] [20 mils (0.5 mm)] <Insert value>, before forming.

3. Fabrication:  Fill-type sheets, fabricated, formed, and bonded together after forming into removable assemblies that are factory installed by manufacturer.

Consult manufacturers for fill options at elevated temperatures.

4. Fill Material Operating Temperature:  Suitable for entering-water temperatures up through [120 deg F (49 deg C)] <Insert temperature>.

Q. Drift Eliminator:

1. Material:  [FRP] [PVC] [FRP or PVC] <Insert material>; with maximum flame-spread index of [5] [25] <Insert value> according to ASTM E 84.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Configuration:  Multipass, designed and tested to reduce water carryover to achieve performance indicated.

Retain subparagraph below to limit placement of drift eliminators.

4. Location:  [Integral to] [Separate and removable from] fill.

R. Air-Intake Louvers:

1. Material:  [FRP] [PVC] [Matching casing].

Retain first subparagraph below with FRP or PVC louvers.

2. UV Treatment:  Inhibitors to protect against damage caused by UV radiation.

3. Louver Blades:  Arranged to uniformly direct air into cooling tower, to minimize air resistance, and to prevent water from splashing out of tower during all modes of operation including operation with fans off.

Retain subparagraph below to limit placement of louvers.

4. Location:  [Integral to] [Separate from] fill.

Retain first paragraph below if screens are required.

S. [Removable ]Air-Intake Screens:  [Galvanized] [Polymer-coated, galvanized] [Stainless]-steel wire mesh.

T. Axial Fan:  Balanced at the factory after assembly.

1. Blade Material:  [Aluminum] [FRP] [Galvanized steel].

2. Hub Material:  [Aluminum] [FRP] [Galvanized steel].

First subparagraph below is an optional feature.  Retain, based on Project conditions, to require feature.

3. Blade Pitch:  Field adjustable.

4. Protective Enclosure:  Removable, galvanized-steel, wire-mesh screens complying with OSHA regulations.

5. Fan Shaft Bearings:  Self-aligning ball or roller bearings with moisture-proof seals and premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).  Bearings designed for an L-10 life of [40,000] [50,000] <Insert value> hours.

6. Bearings Grease Fittings:  Extended lubrication lines to an easily accessible location.

Retain first paragraph below if belt drive is used.

U. Belt Drive:

1. Service Factor:  [1.5] <Insert value> based on motor nameplate horsepower.

2. Sheaves:  Fan and motor shafts shall have taper-lock sheaves fabricated from corrosion-resistant materials.

Retain one of first two subparagraphs below.  Second subparagraph provides better performance.

3. Belt:  Multiple V-belt design with a matched set of[ cogged] belts.

4. Belt:  One-piece, multigrooved, solid-back belt.

5. Belt Material:  Oil resistant, nonstatic conducting, and constructed of neoprene polyester cord.

6. Belt-Drive Guard:  Comply with OSHA regulations.

Retain subparagraph below if Project requires functionality of a single fan with two motors.  Feature is proprietary.  See Evaluations.

7. Two-Motor, Single-Fan Drive:

a. Two single-speed motors per fan, one sized for full speed and load and the other sized for [67] <Insert value> percent of full-load speed.

b. Each motor with belt drive and configured for operation when other motor fails.

c. Controls and wiring same as two-speed, two-winding motor.

Retain first paragraph below if gear drive is used.  See Evaluations.

V. Gear Drive:  Right angle, reduced speed, and designed for cooling tower applications according to CTI STD 111.  Motor and gear drive shall be aligned before shipment.

1. Gear Drive and Coupling Service Factor:  [2.0] <Insert value> based on motor nameplate horsepower.

2. Housing:  Cast iron, with epoxy or polyurethane finish, beveled high-strength steel gears continuously bathed in oil, and with lubrication to other internal parts at all operating speeds.

3. Mounting:  Directly mounted to fan hub and connected to motor so motor shaft is in horizontal position.

4. Operation:  Able to operate both forward and in reverse.

Coordinate motor requirements with options in first subparagraph below.

5. Drive-to-Motor Connection:  [Close coupled to motor using a flexible coupling] [Connected to motor located outside of cooling tower casing by a full-floating drive shaft].

Retain first subparagraph below with second option in last subparagraph above.

6. Drive Shaft Material:  [Corrosion resistant] [Stainless steel], and fitted with flexible couplings on both ends.  Provide exposed shaft and couplings with guards according to OSHA regulations.

7. Extend oil fill, drain, and vent to outside of cooling tower casing using galvanized-steel piping.  Provide installation with oil-level sight glass.

W. Fan Motor:

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

1. General Requirements for Fan Motors: Comply with NEMA designation and temperature-rating requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment" and not indicated below.

Retaining first option in first subparagraph below allows manufacturer to choose either the second or third option.  Third option provides highest degree of protection and must be used when motor is not located in the airstream.

2. Motor Enclosure:  [Totally enclosed] [Totally enclosed air over (TEAO)] [Totally enclosed fan cooled (TEFC)] [with epoxy or polyurethane finish].

3. Energy Efficiency:  [Comply with ASHRAE/IESNA 90.1] [NEMA Premium Efficient].

4. Service Factor:  [1.15] <Insert value>.

5. Insulation:  [Class F] [Class H] <Insert class>.

6. Variable-Speed Motors:  Inverter-duty rated per NEMA MG-1, Section IV, "Performance Standard Applying to All Machines," Part 31, "Definite-Purpose, Inverter-Fed, Polyphase Motors."

Retain first subparagraph below if Project requires specific motor location.  Standard offering by most manufacturers is motor mounted internally or in the airstream.

7. Motor Location:  Mounted outside of cooling tower casing and cooling tower discharge airstream.

Retain first subparagraph below, based on Project conditions, to require additional protection.

8. Severe-duty rating with the following features:

a. Rotor and stator protected with corrosion-inhibiting epoxy resin.

b. Double-shielded, vacuum-degassed bearings lubricated with premium, moisture-resistant grease suitable for temperatures between minus 20 and plus 300 deg F (minus 29 and plus 149 deg C).

First subparagraph below requires a separate, single-phase, field-power connection for heater operation.

c. Internal heater automatically energized when motor is de-energized.

Retain subparagraph below for belt-drive units.

9. Motor Base:  Adjustable, or other suitable provision for adjusting belt tension.

X. Fan Discharge Stack:  Material shall match casing, [manufacturer's standard] [velocity recovery] design.

Retain first subparagraph below if Project requires a minimum stack height to clear an obstruction.

1. Stack Extension:  Fabricated to extend above fan deck <Insert distance> unless otherwise indicated.

2. Stack Termination:  Wire-mesh, galvanized-steel screens; complying with OSHA regulations.

Retain first paragraph below to require a vibration switch furnished with cooling tower.

Y. Vibration Switch:  For each fan drive.

1. Enclosure:  NEMA 250, [Type 4] [Type 4X] <Insert type>.

2. Vibration Detection:  Sensor with a field-adjustable, acceleration-sensitivity set point in a range of 0 to 1 g and frequency range of 0 to 3000 cycles per minute.  Cooling tower manufacturer shall recommend switch set point for proper operation and protection.

3. Provide switch[ with manual-reset button] for [field connection to a BMS and ]hardwired connection to fan motor electrical circuit.

4. Switch shall, on sensing excessive vibration,[ signal an alarm through the BMS and] shut down the fan.

Retain first paragraph below for cooling towers with fan gear drives to require an oil-level switch furnished with cooling tower.

Z. Gear-Drive, Oil-Level Switch:  Low-oil-level warning switch[ for connection to a BMS].

1. Switch shall, on reaching a low-oil-level set point recommended by cooling tower manufacturer, signal an alarm[ through the BMS].

Retain first paragraph below if Project requires capacity-control dampers to improve leaving-water temperature control.

AA. Capacity-Control Dampers:  [Galvanized-steel] [Stainless-steel] <Insert material> dampers, with linkages, electric operator, controller, limit switches, transformer, and weatherproof enclosure.

Retain first paragraph below if controls are specified in Division 23 Section "Instrumentation and Control for HVAC." Retain second paragraph if controls are provided with cooling tower.

AB. Controls:  Comply with requirements in Division 23 Section "Instrumentation and Control for HVAC."

Retain first paragraph below, based on Project conditions, to require cooling tower to be equipped with factory-installed controls.  Not all manufacturers offer factory-installed control packages; those that do offer control packages have limited features available with the package.  Consult manufacturers for additional information.

AC. Control Package:  Factory installed and wired, and functionally tested at factory before shipment.

Fifteen subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features and to correspond with components retained in paragraphs above.

1. NEMA 250, [Type 3R] [Type 4] [Type 4X] enclosure with removable internally mount backplate.

2. Control-circuit transformer with primary and secondary side fuses.

3. Terminal blocks with numbered and color-coded wiring to match wiring diagram.  Spare wiring terminal block for connection to external controls or equipment.

4. Microprocessor-based controller for automatic control of fan based on cooling tower leaving-water temperature with control features to improve operating efficiency based on outdoor ambient wet-bulb temperature by using adaptive logic.

5. Fan motor sequencer for multiple-cell and two-speed applications with automatic lead stage rotation.

If retaining "Mechanically Operated, Collection Basin Water-Level Control" Paragraph, delete first subparagraph below.

6. Collection basin level controller complying with requirements in ["Electric/Electronic, Collection Basin Water-Level Controller with Solenoid Valve"] ["Ultrasonic Collection Basin Water-Level Controller with Solenoid Valve"] Paragraph.

7. Electric basin heaters with temperature control and low-water-level safety switch for each cell, complying with requirements in "Electric Basin Heater" Paragraph.

8. Vibration switch for each fan, complying with requirements in "Vibration Switch" Paragraph.

9. Oil-level switch for each fan with a gear drive, complying with requirement in "Gear-Drive, Oil-Level Switch" Paragraph.

10. Single-point, field-power connection to a [fused disconnect switch] [nonfused disconnect switch] [circuit breaker] [for each cooling tower cell].

a. Branch power circuit to each motor and electric basin heater and to controls[ with a disconnect switch or circuit breaker].

b. NEMA-rated motor controller, hand-off-auto switch, and overcurrent protection for each motor.  Provide variable frequency controller with manual bypass and line reactors for each variable-speed motor indicated.

11. Factory-installed wiring outside of enclosures shall be in metal raceway, except make connections to each motor and electric basin heater with liquidtight conduit.

12. Visual indication of status and alarm[ with momentary test push button] for each motor.

Retain first subparagraph below for audible alarm.  Coordinate with control sequence.

13. Audible alarm and silence switch.

14. Visual indication of elapsed run time, graduated in hours for each motor.

Retain subparagraph below if unit controls interface with BMS.

15. Cooling tower shall have hardware to enable BMS to remotely monitor and display the following:

Seven subparagraphs below are optional features.  Retain applicable subparagraphs, based on Project conditions, to require these features.

a. Operational status of each motor.

b. Position of dampers.

c. Cooling tower leaving-fluid temperature.

d. Fan vibration alarm.

Retain first subparagraph below if Project requires an oil-level alarm through BMS.  Coordinate requirements with "Gear-Drive, Oil-Level Switch" Paragraph.

e. Oil-level alarm.

f. Collection basin [high] [low] [high- and low]-water-level alarms.

g. <Insert conditions to be monitored>.

AD. Personnel Access Components:

Five subparagraphs below are optional components.  Retain applicable subparagraphs, based on Project conditions, to require these components.

1. Doors:  Large enough for personnel to access cooling tower internal components from both cooling tower end walls.  Doors shall be operable from both sides of the door.

2. External Ladders with Safety Cages:  Aluminum, galvanized- or stainless-steel, fixed ladders with ladder extensions to access external platforms and top of cooling tower from adjacent grade without the need for portable ladders.  Comply with 29 CFR 1910.27.

3. External Platforms with Handrails:  Aluminum, FRP, or galvanized-steel bar grating at cooling tower access doors when cooling towers are elevated and not accessible from grade.

4. Handrail:  Aluminum, galvanized steel, or stainless steel complete with kneerail and toeboard, around top of cooling tower.  Comply with 29 CFR 1910.23.

5. Internal Platforms:  Aluminum, FRP, or galvanized-steel bar grating.

a. Spanning the collection basin from one end of cooling tower to the other and positioned to form a path between the access doors.  Platform shall be elevated so that all parts are above the high water level of the collection basin.

b. Elevated internal platforms with handrails accessible from fixed vertical ladders to access the fan drive assembly when out of reach from collection basin platform.

If Project has more than one type or configuration of cooling tower, delete paragraph below and schedule cooling towers on Drawings.

AE. Capacities and Characteristics:

1. Number of Cells:  <Insert quantity>.

2. Air-Inlet Arrangement:  [Single side] [Two sides].

3. Maximum Drift Loss:  [0.005] <Insert number> percent of design water flow.

4. Water Flow/Cell:  <Insert gpm (L/s)>.

5. Minimum Water Flow/Cell:  <Insert gpm (L/s)>.

6. Water Pressure Drop:  <Insert psig (kPa)>.

7. Entering-Water Temperature:  <Insert deg F (deg C)>.

8. Leaving-Water Temperature:  <Insert deg F (deg C)>.

9. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below if cooling tower will be used in favorable weather as an economizer rather than operating water chillers.  See Evaluations.

10. Economizer Mode:

a. Water Flow/Cell:  <Insert gpm (L/s)>.

b. Entering-Water Temperature:  <Insert deg F (deg C)>.

c. Leaving-Water Temperature:  <Insert deg F (deg C)>.

d. Entering-Air Wet-Bulb Temperature:  <Insert deg F (deg C)>.

Retain first subparagraph below to allow Contractor to choose drive type.  Coordinate with "Belt Drive" and "Gear Drive" paragraphs above.

11. Fan Drive:  Belt or gear.

12. Fan Motor:

a. Type:  [Single speed] [Two speed, single winding] [Two speed, two winding] [Variable speed].

b. Horsepower/Cell:  <Insert horsepower>.

c. Full-Load Ampacity:  <Insert value>.

d. Minimum Circuit Ampacity:  <Insert value>.

e. Maximum Overcurrent Protection Device:  <Insert amperage>.

f. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

13. Sound Pressure Level:  <Insert dBA> at <Insert distance in feet (m)> [when measured according to CTI ATC 128].

Retain subparagraph below for projects with basin heaters.

14. Basin Heater:

a. Basin Water Temperature:  [40 deg F (5 deg C)] <Insert deg F (deg C)>.

b. Outdoor Ambient Temperature:  [0 deg F (minus 18 deg C)] [Minus 20 deg F (Minus 29 deg C)] <Insert deg F (deg C)>.

Retain first five subparagraphs below for projects with electric basin heaters.

c. Capacity/Cell:  <Insert kilowatts> .

d. Full-Load Ampacity:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection Device:  <Insert amperage>.

g. Electrical Characteristics:  [208] [240] [480] <Insert value>-V ac, 3 phase, 60 Hz.

Retain first four subparagraphs below for projects with hot-water-coil basin heaters.

h. Capacity/Cell:  <Insert MBtu/h (kW)>.

i. Entering-Fluid Temperature:  <Insert deg F (deg C)>.

j. Fluid Flow Rate:  <Insert gpm (L/s)>.

k. Fluid Pressure Drop:  <Insert psig (kPa)>.

Retain three subparagraphs below for projects with steam-coil or -injection basin heaters.

l. Capacity/Cell:  <Insert MBtu/h (kW)>.

m. Steam Flow:  <Insert lb/h (L/s)>.

n. Steam Pressure:  <Insert psig (kPa)>.

2.7 SOURCE QUALITY CONTROL

Retain first paragraph below and delete "Field Quality Control" Article as an alternative method of certifying performance.  Confirm Project requirements fall within parameters of CTI STD 201 and listed manufacturers comply with requirements.  See Evaluations.

A. Verification of Performance:  Test and certify cooling tower performance according to CTI STD 201, "Certification Standard for Commercial Water-Cooling Towers Thermal Performance."

Retain paragraph below for closed-circuit cooling towers.

B. Factory pressure test heat exchangers after fabrication and prove to be free of leaks.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Before cooling tower installation, examine roughing-in for tower support, anchor-bolt sizes and locations, piping, and electrical connections to verify actual locations, sizes, and other conditions affecting tower performance, maintenance, and operation.

1. Cooling tower locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

B. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain first paragraph below if cooling towers are to be installed on a support structure other than a concrete base.  Indicate design of support structure on Drawings.

A. Install cooling towers on support structure indicated.

Retain first paragraph below for equipment supported on concrete base and vibration isolation devices.

B. Equipment Mounting:  Install cooling tower on concrete bases using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>.  Comply with requirements in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]." Comply with requirements for vibration isolation devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection:  [1/2 inch (13 mm)] [1 inch (25 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension>.

Retain first subparagraph below if retaining "elastomeric pads" option in "Equipment Mounting" Paragraph above.

2. Provide [galvanized] [stainless]-steel plate to equally distribute weight over elastomeric pad.

3. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

4. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

5. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

Retain first paragraph below for equipment supported on vibration isolation devices without a concrete base.

C. Equipment Mounting:  Install cooling tower using [elastomeric pads] [elastomeric mounts] [restrained spring isolators] <Insert device>.  Comply with requirements for vibration isolation devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection:  [1/2 inch (13 mm)] [1 inch (25 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension>.

Retain subparagraph below if retaining "elastomeric pads" option in "Equipment Mounting" Paragraph above.

2. Provide [galvanized] [stainless]-steel plate to equally distribute weight over elastomeric pad.

Retain first paragraph below for equipment to be installed on concrete bases without vibration isolation devices.  This may be appropriate for towers on structural slabs-on-grade.

D. Equipment Mounting:  Install cooling tower on concrete bases.  Comply with requirements in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]."

1. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

E. Install anchor bolts to elevations required for proper attachment to supported equipment.

F. Maintain manufacturer's recommended clearances for service and maintenance.

G. Loose Components:  Install electrical components, devices, and accessories that are not factory mounted.

3.3 CONNECTIONS

Coordinate piping installation and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be omitted.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to cooling towers to allow service and maintenance.

C. Install flexible pipe connectors at pipe connections of cooling towers mounted on vibration isolators.

D. Provide drain piping with valve at cooling tower drain connections and at low points in piping.

E. Connect cooling tower overflows and drains, and piping drains to sanitary sewage system.

F. Domestic Water Piping:  Comply with applicable requirements in Division 22 Section "Domestic Water Piping." Connect to water-level control with shutoff valve and union, flange, or mechanical coupling at each connection.

G. Supply and Return Piping:  Comply with applicable requirements in Division 23 Section "Hydronic Piping." Connect to entering cooling tower connections with shutoff valve, balancing valve, thermometer, plugged tee with pressure gage,[ flow meter,] and drain connection with valve.  Connect to leaving cooling tower connection with shutoff valve.  Make connections to cooling tower with a [union] [flange] [mechanical coupling] [union, flange, or mechanical coupling].

Retain first paragraph below if external equalizer piping is required.

H. Equalizer Piping:  Piping requirements to match supply and return piping.  Connect an equalizer pipe, full size of cooling tower connection, between tower cells.  Connect to cooling tower with shutoff valve.

Retain first paragraph below if hot-water basin heater is installed.

I. Hot-Water Piping:  Comply with applicable requirements in Division 23 Section "Hydronic Piping." Connect to supply and return basin heater with shutoff valve, strainer, control valve, and union or flange on supply connection and union or flange and balancing valve on return connection.  Provide supply and return piping with pressure gage and thermometer.

Retain paragraph below if steam basin heater is installed.

J. Steam and Condensate Piping:  Comply with applicable requirements in Division 23 Section "Steam and Condensate Heating Piping." Connect steam supply to basin heater with shutoff valve, strainer, control valve, and union or flange and condensate piping with union or flange, shutoff valve, strainer, and an appropriate steam trap.

3.4 FIELD QUALITY CONTROL

Retain this article and delete "Verification of Performance" Paragraph in "Source Quality Control" Article as an alternative method of certifying performance.

Retain one of first three paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second or third paragraph, retain "Field quality-control reports" Paragraph in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to perform field tests and inspections.

Retain first paragraph below to require Contractor to perform tests and inspections.

C. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

D. Tests and Inspections:  Comply with [ASME PTC 23, "ASME Performance Test Codes - Code on Atmospheric Water Cooling Equipment] [CTI ATC 105, "Acceptance Test Code for Water Cooling Towers]."

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

E. Cooling towers will be considered defective if they do not pass tests and inspections.

F. Prepare test and inspection reports.

3.5 STARTUP SERVICE

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

B. Inspect field-assembled components, equipment installation, and piping and electrical connections for proper assemblies, installations, and connections.

C. Obtain performance data from manufacturer.

1. Complete installation and startup checks according to manufacturer's written instructions and perform the following:

a. Clean entire unit including basins.

b. Verify that accessories are properly installed.

c. Verify clearances for airflow and for cooling tower servicing.

d. Check for vibration isolation and structural support.

e. Lubricate bearings.

f. Verify fan rotation for correct direction and for vibration or binding and correct problems.

Retain first subparagraph below for cooling towers with belt drives.

g. Adjust belts to proper alignment and tension.

Retain first subparagraph below for towers with gear drives.

h. Verify proper oil level in gear-drive housing.  Fill with oil to proper level.

Retain first subparagraph below for cooling towers with variable-speed fans.

i. Operate variable-speed fans through entire operating range and check for harmonic vibration imbalance.  Set motor controller to skip speeds resulting in abnormal vibration.

Retain first subparagraph below for cooling towers with vibration switches.

j. Check vibration switch setting.  Verify operation.

k. Verify water level in tower basin.  Fill to proper startup level.  Check makeup water-level control and valve.

Retain first subparagraph below for cooling towers with basin heaters.

l. Verify operation of basin heater and control.

m. Verify that cooling tower air discharge is not recirculating air into tower or HVAC air intakes.  Recommend corrective action.

n. Replace defective and malfunctioning units.

D. Start cooling tower and associated water pumps.  Follow manufacturer's written starting procedures.

E. Prepare a written startup report that records the results of tests and inspections.

3.6 ADJUSTING

A. Set and balance water flow to each tower inlet.

B. Adjust water-level control for proper operating level.

3.7 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain cooling towers.

END OF SECTION 236500

COOLING TOWERS
236500 - 1

