Copyright 2006 AIA
MASTERSPEC Full Length
06/06

Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 237313 - MODULAR INDOOR CENTRAL-STATION AIR-HANDLING UNITS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Constant-air-volume, single-zone air-handling units.

2. Constant-air-volume, multizone air-handling units.

3. Constant-air-volume, dual-duct air-handling units.

4. Variable-air-volume, single-zone air-handling units.

5. Variable-air-volume, dual-duct air-handling units.

1.3 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design:  Design vibration isolation and seismic-restraint details, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

B. Structural Performance:  Casing panels shall be self-supporting and capable of withstanding 133 percent of internal static pressures indicated, without panel joints exceeding a deflection of [L/200] [L/100] <Insert value> where "L" is the unsupported span length within completed casings.

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Submittals" Article for projects requiring seismic design.  Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

C. Seismic Performance:  Air-handling units shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.4 SUBMITTALS

First two paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each air-handling unit indicated.

1. Unit dimensions and weight.

2. Cabinet material, metal thickness, finishes, insulation, and accessories.

3. Fans:

a. Certified fan-performance curves with system operating conditions indicated.

b. Certified fan-sound power ratings.

c. Fan construction and accessories.

d. Motor ratings, electrical characteristics, and motor accessories.

4. Certified coil-performance ratings with system operating conditions indicated.

Retain both subparagraphs below if items are furnished as parts of air-handling units.

5. Dampers, including housings, linkages, and operators.

6. Filters with performance characteristics.

B. LEED Submittal:

1. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

First paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

C. Delegated-Design Submittal:  For vibration isolation[ and seismic restraints] indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include adjustable motor bases, rails, and frames for equipment mounting.

2. Design Calculations:  Calculate requirements for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Floor plans and other details, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Mechanical-room layout and relationships between components and adjacent structural and mechanical elements.

2. Support location, type, and weight.

3. Field measurements.

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." See ASCE/SEI 7 for certification requirements for equipment and components.

E. Seismic Qualification Certificates:  For air-handling units, accessories, and components, from manufacturer.

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

F. Source quality-control reports.

G. Field quality-control reports.

H. Operation and Maintenance Data:  For air-handling units to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. NFPA Compliance:  Comply with NFPA 90A for design, fabrication, and installation of air-handling units and components.

Units from manufacturers that do not participate in ARI's certification program might comply with requirements in this Section; delete first paragraph below if not required.

C. ARI Certification:  Air-handling units and their components shall be factory tested according to ARI 430, "Central-Station Air-Handling Units," and shall be listed and labeled by ARI.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, the availability of units with components and features that comply with these requirements.

D. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

E. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

F. Comply with NFPA 70.

1.6 COORDINATION

A. Coordinate sizes and locations of concrete bases with actual equipment provided.

B. Coordinate sizes and locations of structural-steel support members, if any, with actual equipment provided.

1.7 EXTRA MATERIALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Filters:  [One] <Insert number> set(s) for each air-handling unit.

2. Gaskets:  [One] <Insert number> set(s) for each access door.

3. Fan Belts:  [One] <Insert number> set(s) for each air-handling unit fan.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Air Enterprises, Inc.

2. Airtherm; a Mestek company.

3. Buffalo Air Handling.

4. Carrier Corporation; a member of the United Technologies Corporation Family.

5. Coil Company, LLC.

6. Dunham-Bush, Inc.

7. Engineered Air.

8. Mammoth Inc.

9. McQuay International

10. Scott Springfield Mfg. Inc.

11. Trane; American Standard Inc.

12. USA Coil & Air.

13. YORK International Corporation.

14. <Insert manufacturer's name>.

2.2 UNIT CASINGS

Air-handling unit configuration, casing materials, and thicknesses may be scheduled.  If so, scheduled information may be deleted from this article.

A. General Fabrication Requirements for Casings:

1. Forming:  Form walls, roofs, and floors with at least two breaks at each joint.

2. Casing Joints:  Sheet metal screws or pop rivets.

3. Sealing:  Seal all joints with water-resistant sealant.

Retain one of first three subparagraphs below.

4. Factory Finish for [Steel] [and] [Galvanized-Steel] Casings:  Apply manufacturer's standard primer immediately after cleaning and pretreating.

5. Factory Finish for [Steel] [and] [Galvanized-Steel] Casings:  Immediately after cleaning and pretreating, apply manufacturer's standard two-coat, baked-on enamel finish, consisting of prime coat and thermosetting topcoat.

6. Casing Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel] <Insert special coating>.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

7. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

B. Casing Insulation and Adhesive:

In first subparagraph below, Type I is blanket and Type II is board insulation.

1. Materials:  ASTM C 1071, [Type I] [Type II].

Retain one of two "Location and Application" subparagraphs below.

2. Location and Application:  Factory applied with adhesive and mechanical fasteners to the internal surface of section panels downstream from, and including, the cooling-coil section.

a. Liner Adhesive:  Comply with ASTM C 916, Type I.

b. Mechanical Fasteners:  Galvanized steel, suitable for adhesive attachment, mechanical attachment, or welding attachment to duct without damaging liner when applied as recommended by manufacturer and without causing leakage in cabinet.

c. Liner materials applied in this location shall have air-stream surface coated with a temperature-resistant coating or faced with a plain or coated fibrous mat or fabric depending on service-air velocity.

3. Location and Application:  Encased between outside and inside casing.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 5.14 - "Access for Inspection, Cleaning, and Maintenance" sets requirements for equipment access.  If applying for LEED certification, comply with requirements in ASHRAE 62.1-2004.

C. Inspection and Access Panels and Access Doors:

1. Panel and Door Fabrication:  Formed and reinforced, single- or double-wall and insulated panels of same materials and thicknesses as casing.

2. Inspection and Access Panels:

a. Fasteners:  Two or more camlock type for panel lift-out operation.  Arrangement shall allow panels to be opened against air-pressure differential.

b. Gasket:  Neoprene, applied around entire perimeters of panel frames.

c. Size:  Large enough to allow inspection and maintenance of air-handling unit's internal components.

3. Access Doors:

a. Hinges:  A minimum of two ball-bearing hinges or stainless-steel piano hinge and two wedge-lever-type latches, operable from inside and outside.  Arrange doors to be opened against air-pressure differential.

b. Gasket:  Neoprene, applied around entire perimeters of panel frames.

Retain first subparagraph below to add windows in doors.  Windows add cost and are considered optional features.  Retain option in subparagraph to limit windows to specific location.

c. Fabricate windows in [fan section ]doors of double-glazed, wire-reinforced safety glass with an air space between panes and sealed with interior and exterior rubber seals.

d. Size:  At least [18 inches (450 mm)] [24 inches (600 mm)] <Insert width> wide by full height of unit casing up to a maximum height of [60 inches (1500 mm)] [72 inches (1800 mm)] <Insert height>.

4. Locations and Applications:

Verify that the sections listed below are large enough for panels and doors.  Verify applicability with listed manufacturers.

a. Fan Section:  [Inspection and access panels] [Doors] [Doors and inspection and access panels].

b. Access Section:  Doors.

c. Coil Section:  Inspection and access panel.

d. Damper Section:  [Inspection and access panels] [Doors].

e. Filter Section:  [Inspection and access panels] [Doors] large enough to allow periodic removal and installation of filters.

f. Mixing Section:  Doors.

g. Humidifier Section:  Doors.

Retain subparagraph below to add service lights.  Service lights add cost and are considered optional features.

5. Service Light:  100-W vaporproof fixture with switched junction box located [outside] [inside] adjacent to door.

a. Locations:  [Each section accessed with door] [Fan section] <Insert location>.

D. Condensate Drain Pans:

First option in first subparagraph below is minimum slope in ASHRAE 62.1-2004.

1. Fabricated with [one] [two] percent slope in at least two planes to collect condensate from cooling coils (including coil piping connections, coil headers, and return bends) and from humidifiers and to direct water toward drain connection.

Retain option in first subparagraph below to comply with LEED-NC Prerequisite EQ 1; otherwise, insert distance.

a. Length:  Extend drain pan downstream from leaving face [to comply with ASHRAE 62.1-2004] <Insert distance>.

b. Depth:  A minimum of [2 inches (50 mm)] <Insert depth> deep.

2. [Formed sections] [Integral part of floor plating].

Retain one of first two subparagraphs below.

3. Single-wall, [galvanized] [stainless]-steel sheet.

4. Double-wall, [galvanized] [stainless]-steel sheet with space between walls filled with foam insulation and moisture-tight seal.

5. Drain Connection:  Located at lowest point of pan and sized to prevent overflow.  Terminate with threaded nipple on [one end] [both ends] of pan.

a. Minimum Connection Size:  [NPS 1 (DN 25)] [NPS 2 (DN 50)] <Insert size>.

Retain first subparagraph below for galvanized-steel drain pans; delete for stainless-steel drain pans.

6. Pan-Top Surface Coating:  Asphaltic waterproofing compound.

7. Units with stacked coils shall have an intermediate drain pan to collect condensate from top coil.

Retain first paragraph below if Project includes units that are suspended at a height that does not allow maintenance and service from the floor without use of ladders or portable platforms.

E. Service Platform:  [Steel] [Galvanized steel] [Aluminum], [42 inches (1070 mm)] <Insert width> wide running entire length of unit and located on service access side, with angle side rails, 4-inch (100-mm) kick plates, and expanded metal floor.  Provide platform with a fixed ladder that extends from the top of the side rail to the floor.

F. Air-Handling-Unit Mounting Frame:  Formed galvanized-steel channel or structural channel supports, designed for low deflection, welded with integral lifting lugs.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Seismic Qualification Certificates" Paragraph in "Submittals" Article.

1. Seismic Fabrication Requirements:  Fabricate mounting base and attachment to air-handling unit sections, accessories, and components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when air-handling unit frame is anchored to building structure.

2.3 FAN, DRIVE, AND MOTOR SECTION

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.5.3 - "Air System Design and Control" sets requirements for fans and fan controls.  If applying for LEED certification, comply with requirements in ASHRAE/IESNA 90.1-2004.

A. Fan and Drive Assemblies:  Statically and dynamically balanced and designed for continuous operation at maximum-rated fan speed and motor horsepower.

1. Shafts:  Designed for continuous operation at maximum-rated fan speed and motor horsepower, and with field-adjustable alignment.

a. Turned, ground, and polished hot-rolled steel with keyway.  Ship with a protective coating of lubricating oil.

b. Designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

B. Centrifugal Fan Housings:  Formed- and reinforced-steel panels to form curved scroll housings with shaped cutoff and spun-metal inlet bell.

1. Bracing:  Steel angle or channel supports for mounting and supporting fan scroll, wheel, motor, and accessories.

2. Horizontal-Flanged, Split Housing:  Bolted construction.

3. Housing for Supply Fan:  Attach housing to fan-section casing with metal-edged flexible duct connector.

4. Flexible Connector:  Factory fabricated with a fabric strip [3-1/2 inches (89 mm)] [5-3/4 inches (146 mm)] wide attached to 2 strips of 2-3/4-inch- (70-mm-) wide, 0.028-inch- (0.7-mm-) thick, galvanized-steel sheet or 0.032-inch- (0.8-mm-) thick aluminum sheets; select metal compatible with casing.

a. Flexible Connector Fabric:  Glass fabric, double coated with neoprene.  Fabrics, coatings, and adhesives shall comply with UL 181, Class 1.

1) Fabric Minimum Weight:  26 oz./sq. yd. (880 g/sq. m).

2) Fabric Tensile Strength:  480 lbf/inch (84 N/mm) in the warp and 360 lbf/inch (63 N/mm) in the filling.

3) Fabric Service Temperature:  Minus 40 to plus 200 deg F (Minus 40 to plus 93 deg C).

C. Plenum Fan Housings:  Steel frame and panel; fabricated without fan scroll and volute housing.

Retain one of first four paragraphs below.

Cast-steel hub is common on AMCA 99-2408, Class III fans.

D. Backward-Inclined, Centrifugal Fan Wheels:  Single-width-single-inlet and double-width-double-inlet construction with curved inlet flange, backplate, backward-inclined blades welded or riveted to flange and backplate; cast-iron or cast-steel hub riveted to backplate and fastened to shaft with set screws.

E. Forward-Curved, Centrifugal Fan Wheels:  Inlet flange, backplate, and shallow blades with inlet and tip curved forward in direction of airflow and mechanically fastened to flange and backplate; cast-steel hub swaged to backplate and fastened to shaft with set screws.

F. Airfoil, Centrifugal Fan Wheels:  Smooth-curved inlet flange, backplate, and hollow die-formed airfoil-shaped blades continuously welded at tip flange and backplate; cast-iron or cast-steel hub riveted to backplate and fastened to shaft with set screws.

G. Axial Fans:  Fan wheel and housing, straightening-vane section, factory-mounted motor with belt drive or direct drive, an inlet cone section, and accessories.

1. Variable-Pitch Fans:  Internally mounted [pneumatic] [electric] [electronic] actuator, externally mounted positive positioner, and mechanical-blade-pitch indicator.

2. Housings:  [Steel] [Galvanized steel] [Aluminum].

a. Inlet and Outlet Connections:  Flanges.

b. Guide Vane Section:  Integral guide vanes downstream from fan wheel designed to straighten airflow.

H. Fan Shaft Bearings:

Retain one of three subparagraphs below if Project has more than one air-handling unit and the bearings required for each unit are different, or retain all three subparagraphs and include bearing types for each in a schedule.  See "Sample Schedule" Article in the Evaluations.  Other bearing types may be available; those specified below may not be available from all manufacturers.

1. Prelubricated and Sealed, Ball Bearings:  Self-aligning, pillow-block type with a rated life of [50,000] [120,000] <Insert number> hours according to ABMA 9.

2. Grease-Lubricated, Tapered-Roller Bearings:  Self-aligning, pillow-block type with double-locking collars and 2-piece, cast-iron housing[ with grease lines extended to outside unit] and a rated life of [50,000] [120,000] <Insert number> hours according to ABMA 11.

3. Grease-Lubricated Bearings:  Self-aligning, pillow-block-type, ball or roller bearings with adapter mount and two-piece, cast-iron housing[ with grease lines extended to outside unit].

I. Belt Drives:  Factory mounted, with adjustable alignment and belt tensioning, and with [1.5] [1.4] [1.3] [1.2] service factor based on fan motor.

1. Pulleys:  Cast iron or cast steel with split, tapered bushing; dynamically balanced at factory.

5-hp limit in first subparagraph below is standard with many manufacturers but is a designer's choice.

2. Motor Pulleys:  Adjustable pitch for use with [5] <Insert number>-hp motors and smaller; fixed pitch for use with motors larger than [5] <Insert number> hp.  Select pulley size so pitch adjustment is at the middle of adjustment range at fan design conditions.

3. Belts:  Oil resistant, nonsparking, and nonstatic; in matched sets for multiple-belt drives.

Retain subparagraph below for air-handling units with motors mounted on outside of casing.

4. Belt Guards:  Comply with requirements specified by OSHA and fabricate according to SMACNA's "HVAC Duct Construction Standards"; 0.1046-inch- (2.7-mm-) thick, 3/4-inch (20-mm) diamond-mesh wire screen, welded to steel angle frame; prime coated.

Retain one of first two paragraphs below or delete both.  Retain both if multiple units are required and indicate which is required for each unit in a schedule.

J. Variable-Inlet Vanes:  Steel, with blades supported at both ends with permanently lubricated bearings.  Variable mechanism terminating in single lever for connection to control actuator with connecting shaft for second set of variable inlet vanes on double-width fans.

K. Discharge Dampers:  Heavy-duty steel assembly with channel frame and sealed ball bearings, and [opposed] [parallel] blades constructed of two plates formed around and welded to shaft, with blades linked out of air stream to single control lever.

L. Internal Vibration Isolation[ and Seismic Control]:  Fans shall be factory mounted with manufacturer's standard[ restrained] vibration isolation mounting devices having a minimum static deflection of [1 inch (25 mm)] [2 inches (50 mm)] <Insert value>.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Seismic Qualification Certificates" Paragraph in "Submittals" Article.

1. Seismic Fabrication Requirements:  Fabricate fan section, internal mounting frame and attachment to fans, fan housings, motors, casings, accessories, and other fan section components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when fan-mounting frame and air-handling-unit mounting frame are anchored to building structure.

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, insert paragraphs to suit Project.

M. Motor:  Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Retain first subparagraph below if enclosure is not open-dripproof type.  Retain second subparagraph for premium efficiency.

1. Enclosure Type:  Totally enclosed, fan cooled.

2. NEMA Premium (TM) efficient motors as defined in NEMA MG 1.

3. Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

4. Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 26 Sections.

Retain first subparagraph below to require that disconnect switches be supplied with unit.

5. Mount unit-mounted disconnect switches on [exterior] [interior] of unit.

If unique characteristics are required for motors in this Section, insert subparagraphs below.

6. <Insert unique motor characteristics>.

Paragraph below is an example of variable frequency controllers.  Retain features and attributes to suit Project, and verify their availability with listed manufacturers.

N. Variable Frequency Controllers:

1. Description:  NEMA ICS 2, IGBT, PWM, VFC; listed and labeled as a complete unit and arranged to provide variable speed of an NEMA MG 1, Design B, 3-phase induction motor by adjusting output voltage and frequency.

2. Output Rating:  3-phase; 6 to [60 Hz, with voltage proportional to frequency throughout voltage range] [66 Hz, with torque constant as speed changes] [120 Hz, with horsepower constant throughout speed range].

3. Unit Operating Requirements:

a. Input ac voltage tolerance of [208 V, plus or minus 5] [380 to 500 V, plus or minus 10] [525 to 575 V, plus or minus 10] percent.

b. Input frequency tolerance of 50/60 Hz, plus or minus 6 percent.

c. Minimum Efficiency:  96 percent at 60 Hz, full load.

d. Minimum Displacement Primary-Side Power Factor:  96 percent.

e. Overload Capability:  1.1 times the base load current for 60 seconds; 2.0 times the base load current for 3 seconds.

f. Starting Torque:  100 percent of rated torque or as indicated.

g. Speed Regulation:  Plus or minus 1 percent.

4. Isolated control interface to allow controller to follow control signal over an 11:1 speed range.

5. Internal Adjustability Capabilities:

a. Minimum Speed:  5 to 25 percent of maximum rpm.

b. Maximum Speed:  80 to 100 percent of maximum rpm.

c. Acceleration:  2 to a minimum of 22 seconds.

d. Deceleration:  2 to a minimum of 22 seconds.

e. Current Limit:  50 to a minimum of 110 percent of maximum rating.

6. Self-Protection and Reliability Features:

Retain one or more of first nine subparagraphs below.

a. Input transient protection by means of surge suppressors.

b. Undervoltage and overvoltage trips; inverter overtemperature, overload, and overcurrent trips.

c. Adjustable motor overload relays capable of NEMA ICS 2, [Class 10] [Class 20] [Class 30] performance.

d. Notch filter to prevent operation of the controller-motor-load combination at a natural frequency of the combination.

e. Instantaneous line-to-line and line-to-ground overcurrent trips.

f. Loss-of-phase protection.

g. Reverse-phase protection.

h. Short-circuit protection.

i. Motor overtemperature fault.

Delete or revise first four subparagraphs below to suit Project.

7. Automatic Reset/Restart:  Attempts three restarts after controller fault or on return of power after an interruption and before shutting down for manual reset or fault correction.  Bidirectional autospeed search shall be capable of starting into rotating loads spinning in either direction and returning motor to set speed in proper direction, without damage to controller, motor, or load.

8. Power-Interruption Protection:  To prevent motor from re-energizing after a power interruption until motor has stopped.

9. Torque Boost:  Automatically varies starting and continuous torque to at least 1.5 times the minimum torque to ensure high-starting torque and increased torque at slow speeds.

10. Motor Temperature Compensation at Slow Speeds:  Adjustable current fall-back based on output frequency for temperature protection of self-cooled, fan-ventilated motors at slow speeds.

11. Door-mounted LED status lights shall indicate the following conditions:

a. Power on.

b. Run.

c. Overvoltage.

d. Line fault.

e. Overcurrent.

f. External fault.

12. Panel-Mounted Operator Station:  Start-stop and auto-manual selector switches with manual-speed-control potentiometer and elapsed time meter.

13. Meters or digital readout devices and selector switch, mounted flush in controller door and connected to indicate the following controller parameters:

a. Output frequency (Hertz).

b. Motor speed (rpm).

c. Motor status (running, stop, fault).

d. Motor current (amperes).

e. Motor torque (percent).

f. Fault or alarming status (code).

g. Proportional-integral-derivative (PID) feedback signal (percent).

h. DC-link voltage (volts direct current).

i. Set-point frequency (Hertz).

j. Motor output voltage (volts).

14. Control Signal Interface:

a. Electric Input Signal Interface:  A minimum of 2 analog inputs (0 to 10 V or 0/4-20 mA) and 6 programmable digital inputs.

b. Remote signal inputs capable of accepting any of the following speed-setting input signals from the control system:

1) 0 to 10-V dc.

2) 0-20 or 4-20 mA.

3) Potentiometer using up/down digital inputs.

4) Fixed frequencies using digital inputs.

5) RS485.

6) Keypad display for local hand operation.

c. Output signal interface with a minimum of 1 analog output signal (0/4-20 mA), which can be programmed to any of the following:

1) Output frequency (Hertz).

2) Output current (load).

3) DC-link voltage (volts direct current).

4) Motor torque (percent).

5) Motor speed (rpm).

6) Set-point frequency (Hertz).

d. Remote indication interface with a minimum of 2 dry circuit relay outputs (120-V ac, 1 A) for remote indication of the following:

1) Motor running.

2) Set-point speed reached.

3) Fault and warning indication (overtemperature or overcurrent).

4) High- or low-speed limits reached.

15. Communications:  RS485 interface allows VFC to be used with an external system within a multidrop LAN configuration.  Interface shall allow all parameter settings of VFC to be programmed via BMS control.  Provide capability for VFC to retain these settings within the nonvolatile memory.

Coordinate both subparagraphs below with manufacturers selected; not all manufacturers offer all optional features below.

16. Integral Disconnecting Means:  [NEMA AB 1, instantaneous-trip circuit breaker] [NEMA AB 1, molded-case switch] [NEMA KS 1, nonfusible switch] [NEMA KS 1, fusible switch] with lockable handle.

17. Accessories:

a. Devices shall be factory installed in controller enclosure unless otherwise indicated.

b. Push-Button Stations, Pilot Lights, and Selector Switches:  NEMA ICS 2, heavy-duty type.

c. Standard Displays:

1) Output frequency (Hertz).

2) Set-point frequency (Hertz).

3) Motor current (amperes).

4) DC-link voltage (volts direct current).

5) Motor torque (percent).

6) Motor speed (rpm).

7) Motor output voltage (volts).

2.4 COIL SECTION

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 5.12 - "Finned-Tube Coils and Heat Exchangers" sets requirements for coils.  If applying for LEED certification, comply with requirements in ASHRAE 62.1-2004.

A. General Requirements for Coil Section:

1. Comply with ARI 410.

2. Fabricate coil section to allow removal and replacement of coil for maintenance and to allow in-place access for service and maintenance of coil(s).

3. For multizone units, provide air deflectors and air baffles to balance airflow across coils.

4. Coils shall not act as structural component of unit.

Retain subparagraph below for projects in seismic areas.  If retaining, also retain "Seismic Qualification Certificates" Paragraph in "Submittals" Article.

5. Seismic Fabrication Requirements:  Fabricate coil section, internal mounting frame and attachment to coils, and other coil section components with reinforcement strong enough to withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" when coil-mounting frame and air-handling-unit mounting frame are anchored to building structure.

B. Electrical Heating Coils, Controls, and Accessories:  Comply with UL 1995.

1. Casing Assembly:  [Slip-in] [Flanged] type with galvanized-steel frame.

Retain one of first two subparagraphs below.

2. Sheathed Heating Elements:  Coiled resistance wire of 80 percent nickel and 20 percent chromium surrounded by compacted magnesium-oxide powder in tubular-steel sheath; with spiral-wound, copper-plated, steel fins continuously brazed to sheath.

3. Open Heating Elements:  Resistance wire of 80 percent nickel and 20 percent chromium supported and insulated by floating ceramic bushings recessed into casing openings, fastened to supporting brackets, and mounted in galvanized-steel frame.

4. Overtemperature Protection:  Disk-type, automatically resetting, thermal-cutout, safety device; serviceable through terminal box without removing heater from coil section.

5. Secondary Protection:  Load-carrying, manually resetting or manually replaceable, thermal cutouts; factory wired in series with each heater stage.

6. Control Panel:  [Unit] [Remote] mounted with disconnecting means and overcurrent protection.

a. [Magnetic] [Mercury] contactor.

b. Solid-state, stepless pulse controller.

c. Toggle switches, one per step.

d. Step controller.

e. Time-delay relay.

f. Pilot lights, one per step.

g. Airflow proving switch.

2.5 AIR FILTRATION SECTION

See Evaluations for discussion about filter characteristics and applications.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

A. General Requirements for Air Filtration Section:

1. Comply with NFPA 90A.

2. Provide minimum arrestance according to ASHRAE 52.1, and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

3. Provide filter holding frames arranged for flat or angular orientation, with access doors on both sides of unit.  Filters shall be removable from one side or lifted out from access plenum.

Retain one or more of first seven paragraphs below, as applicable.  If Project has more than one filter type, indicate filter type for each unit on Drawings.

B. Disposable Panel Filters:

1. Factory-fabricated, viscous-coated, flat-panel type.

2. Thickness:  [1 inch (25 mm)] [2 inches (50 mm)].

3. Dust-Holding Capacity:  <Insert lb (kg)>.

4. Initial Resistance:  <Insert inches wg (Pa)>.

5. Recommended Final Resistance:  <Insert inches wg (Pa)>.

6. Arrestance (ASHRAE 52.1):  [80] <Insert value>.

7. Merv (ASHRAE 52.2):  [5] <Insert value>.

8. Media:  Interlaced glass fibers sprayed with nonflammable adhesive[ and antimicrobial agent].

9. Frame:  Galvanized steel, with metal grid on outlet side, steel rod grid on inlet side, hinged, and with pull and retaining handles.

C. Extended-Surface, Disposable Panel Filters:

1. Factory-fabricated, dry, extended-surface type.

2. Thickness:  [1 inch (25 mm)] [2 inches (50 mm)] [4 inches (100 mm)].

3. Dust-Holding Capacity:  <Insert lb (kg)>.

4. Initial Resistance:  <Insert inches wg (Pa)>.

5. Recommended Final Resistance:  <Insert inches wg (Pa)>.

6. Arrestance (ASHRAE 52.1):  [90] <Insert value>.

7. Merv (ASHRAE 52.2):  [7] <Insert value>.

8. Media:  Fibrous material formed into deep-V-shaped pleats[ with antimicrobial agent] and held by self-supporting wire grid.

9. Media-Grid Frame:  [Nonflammable cardboard] [Galvanized steel] [Fire-retardant, 3/4-inch (20-mm) particleboard with gaskets].

10. Mounting Frames:  Welded, galvanized steel, with gaskets and fasteners, suitable for bolting together into built-up filter banks.

D. Extended-Surface, Nonsupported-Media Filters:

1. Factory-fabricated, dry, extended-surface, self-supporting type.

2. Dust-Holding Capacity:  <Insert lb (kg)>.

3. Initial Resistance:  <Insert inches wg (Pa)>.

4. Recommended Final Resistance:  <Insert inches wg (Pa)>.

5. Arrestance (ASHRAE 52.1):  [95] <Insert value>.

6. Merv (ASHRAE 52.2):  [13] <Insert value>.

7. Media:  Fibrous material [with antimicrobial agent] constructed so individual pleats are maintained in tapered form by flexible internal supports under rated-airflow conditions.

8. Filter-Media Frame:  [Galvanized steel] [Hard polyurethane foam].

9. Mounting Frames:  Welded, galvanized steel, with gaskets and fasteners, suitable for bolting together into built-up filter banks[ with space for prefilter].

E. Automatic Roll Filters:

1. Factory-fabricated, automatic, motor-driven, roll type.

2. Arrangement:  [Horizontal] [Vertical].

3. Dust-Holding Capacity:  <Insert lb (kg)>.

4. Initial Resistance:  <Insert inches wg (Pa)>.

5. Recommended Final Resistance:  <Insert inches wg (Pa)>.

6. Arrestance (ASHRAE 52.1):  [80] <Insert value>.

7. Merv (ASHRAE 52.2):  [5] <Insert value>.

8. Media:  Compressed and rolled, fibrous-glass material viscous coated[, and with antimicrobial agent].

9. Holding Frame:  Galvanized steel, with enclosed, clean media roll arranged to allow upstream replacement of filter media.

10. Auxiliary Frame:  Locate on downstream side of unit with [downstream] [side] access.

11. Final Filter:  Extended-surface, [retained-media] [nonsupported-media] [HEPA] filters.

12. Control and Drive:

a. Mechanism:  Electric, gear-reducer, motor-driven, feed control equipped with manual media advance and runout switches for stopping media movement of filter bank and operating remote warning signal lights.

b. Manual Control:  Manual switch to advance media and wired to override automatic controls.

c. Automatic Control:  Prewired control package to advance media [when filter resistance exceeds adjustable high limit] [after adjustable operating time].

F. Activated-Carbon Panel Filters:

1. Factory-fabricated unit with activated-carbon media.

2. Flat-Panel Media:  Multilayer filter with inlet layer of polyester fibers, layer of activated-carbon granules bonded to fibers, layer of polyurethane foam, and housed in cardboard frame.

3. Pleated Media:  Multilayer filter with inlet layer of cotton and synthetic fibers and layer of activated-carbon granules bonded to synthetic fibers, formed into deep-V-shaped pleats and held by self-wire grid, and housed in nonflammable cardboard frame.

4. Mounting Frames:  Welded galvanized steel, with polyurethane gaskets and fasteners, capable of holding media and media frame in place and suitable for bolting together into built-up filter banks.

G. Activated-Carbon Filters:

1. Factory-fabricated unit in deep-V arrangement with disposable panel prefilter.

2. Media:  Activated carbon mounted in removable carbon-cell trays of epoxy-coated steel.

3. Activated-Carbon Capacity:  [12 lb (5.4 kg) of activated carbon per 500 cfm (236 L/s)] [8.8 lb (4.0 kg) of activated carbon per 2000 cfm (944 L/s)] of airflow.

4. Housing:  0.064-inch- (1.6-mm-) thick, galvanized steel, for side servicing through gasketed access doors on both sides.  Equip housings with metal slide channel tracks to hold activated-carbon trays.

H. HEPA Filters:

1. Factory-fabricated unit.

2. Dust-Holding Capacity:  <Insert lb (kg)>.

3. Initial Resistance:  <Insert inches wg (Pa)>.

4. Recommended Final Resistance:  <Insert inches wg (Pa)>.

5. Arrestance (ASHRAE 52.1):  [95 percent on 0.3-micrometer D.O.P. particles] [99.97 percent on 0.3-micrometer D.O.P. particles] [99.9995 percent on 0.1- and 0.2-micrometer D.O.P. particles] [99.99995 percent on 0.1- and 0.2-micrometer D.O.P. particles] <Insert value>.

6. Media:  UL 586, fibrous glass, constructed of continuous sheets with closely spaced pleats with [aluminum separators] [vinyl-coated aluminum separators] [separators of ribbons of filter media].

7. Frame Material:  [3/4-inch- (19-mm-) thick, fire-retardant plywood] [3/4-inch- (19-mm-) thick, fire-retardant particleboard] [3/4-inch- (19-mm-) thick plywood] [3/4-inch- (19-mm-) thick particleboard] [Galvanized steel] [Aluminized steel] [Cadmium-plated steel] [Stainless steel] [Aluminum].

8. Media to Frame Side Bond:  [Polyurethane foam] [Silicone] [Neoprene adhesive] [Fiberglass-mat packing] [Thermosetting sealant] [Knife edge in fluid-filled channel].

9. Face Gasket:  [Neoprene expanded rubber] [Ceramic fiber] [Silicone].

10. Mounting Frames:  Downstream corners of holding device shall have cushion pads to protect media.  Bolted filter-sealing mechanism shall mount and continuously seal each individual filter.

I. Filter Gage:

1. [3-1/2-inch- (90-mm-)] [2-inch- (50-mm-)] diameter, diaphragm-actuated dial in metal case.

2. Vent valves.

3. Black figures on white background.

4. Front recalibration adjustment.

5. [2] [3] percent of full-scale accuracy.

6. Range:  [0- to 0.5-inch wg (0 to 125 Pa)] [0- to 1.0-inch wg (0 to 250 Pa)] [0- to 2.0-inch wg (0 to 500 Pa)] [0- to 3.0-inch wg (0 to 750 Pa)] [0- to 4.0-inch wg (0 to 1000 Pa)].

7. Accessories:  Static-pressure tips with integral compression fittings, 1/4-inch (6-mm) [aluminum] [plastic] tubing, and 2- or 3-way vent valves.

2.6 DAMPERS

Retain this article to require that dampers be provided by air-handling unit manufacturer; delete if dampers are specified in Division 23 Section "Instrumentation and Control for HVAC."

A. General Requirements for Dampers:  Leakage rate, according to AMCA 500, "Laboratory Methods for Testing Dampers for Rating," shall not exceed [2] <Insert number> percent of air quantity at [2000-fpm (10-m/s)] <Insert value> face velocity through damper and [4-inch wg (1000-Pa)] <Insert value> pressure differential.

Retain one of first three paragraphs below.  Retain first paragraph if damper operators are specified in Division 23 Section "Instrumentation and Control for HVAC." Retain second and third paragraphs to require that damper operators be provided by air-handling unit manufacturer.

B. Damper Operators:  Comply with requirements in Division 23 Section "Instrumentation and Control for HVAC."

C. Electronic Damper Operators:

1. Direct-coupled type designed for minimum 60,000 full-stroke cycles at rated torque.

2. Electronic damper position indicator shall have visual scale indicating percent of travel and 2- to 10-V dc, feedback signal.

Default motor characteristics are specified in Division 23 Section "Common Motor Requirements for HVAC." Insert subparagraphs to suit Project if different characteristics are required.

3. Operator Motors:

a. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 23 Section "Common Motor Requirements for HVAC."

b. Size to operate with sufficient reserve power to provide smooth modulating action or two-position action.

c. Permanent Split-Capacitor or Shaded-Pole Type:  Gear trains completely oil immersed and sealed.  Equip spring-return motors with integral spiral-spring mechanism in housings designed for easy removal for service or adjustment of limit switches, auxiliary switches, or feedback potentiometer.

4. Nonspring-Return Motors for Dampers Larger Than 25 Sq. Ft. (2.3 sq. m):  Size for running torque of 150 in. x lbf (16.9 N x m) and breakaway torque of 300 in. x lbf (33.9 N x m).

5. Spring-Return Motors for Dampers Larger Than 25 Sq. Ft. (2.3 sq. m):  Size for running and breakaway torque of 150 in. x lbf (16.9 N x m).

6. Size dampers for running torque calculated as follows:

a. Parallel-Blade Damper with Edge Seals:  7 inch-lb/sq. ft. (86.8 kg-cm/sq. m) of damper.

b. Opposed-Blade Damper with Edge Seals:  5 inch-lb/sq. ft. (62 kg-cm/sq. m) of damper.

c. Parallel-Blade Damper without Edge Seals:  4 inch-lb/sq. ft (49.6 kg-cm/sq. m) of damper.

d. Opposed-Blade Damper without Edge Seals:  3 inch-lb/sq. ft. (37.2 kg-cm/sq. m) of damper.

e. Dampers with 2- to 3-Inch wg (500 to 750 Pa) of Pressure Drop or Face Velocities of 1000 to 2500 fpm (5 to 13 m/s):  Increase running torque by 1.5.

f. Dampers with 3- to 4-Inch wg (750 to 1000 Pa) of Pressure Drop or Face Velocities of 2500 to 3000 fpm (13 to 15 m/s):  Increase running torque by 2.0.

7. Coupling:  V-bolt and V-shaped, toothed cradle.

8. Overload Protection:  Electronic overload or digital rotation-sensing circuitry.

9. Fail-Safe Operation:  Mechanical, spring-return mechanism with external, manual gear release on nonspring-return actuators.

10. Power Requirements (Two-Position Spring Return):  [24] [120] [230]-V ac.

11. Power Requirements (Modulating):  Maximum 10 VA at 24-V ac or 8 W at 24-V dc.

12. Proportional Signal:  2- to 10-V dc or 4 to 20 mA, and 2- to 10-V dc position feedback signal.

13. Temperature Rating:  [Minus 22 to plus 122 deg F (Minus 30 to plus 50 deg C)] [40 to 104 deg F (5 to 40 deg C)].

14. Run Time:  [12 seconds open, 5 seconds closed] [30 seconds] [60 seconds] [120 seconds].

D. Pneumatic Damper Operators:

1. Rolling-diaphragm piston type with adjustable stops and spring return, sized to operate with sufficient reserve power to provide smooth modulating action or two-position action.  Where actuators operate in sequence, provide pilot positioners.

2. Pneumatic Damper Position Indicator:  Potentiometer mounted in enclosure with adjustable crank-arm assembly connected to damper to transmit 0 to 100 percent valve/damper travel.

3. Pilot Positioners:

Retain one or more of first seven subparagraphs below.

a. Start Point:  Adjustable from 2 to 12 psig (14 to 83 kPa).

b. Operating Span:  Adjustable from 5 to 13 psig (35 to 90 kPa).

c. Linearity:  Plus or minus 10 percent of output signal span.

d. Hysteresis:  3 percent of span.

e. Response:  0.25-psig (1723-Pa) input change.

f. Maximum Pilot Signal Pressure:  20 psig (140 kPa).

g. Maximum Control Air-Supply Pressure:  60 psig (410 kPa).

4. Actuator Housing:  Molded or die-cast zinc or aluminum.[$ds~Terminal unit actuators may be high-impact plastic with ambient temperature rating of 50 to 140 deg F (10 to 60 deg C) unless located in return-air plenums.]

Operators in subparagraph below have superior torque but require at least 25 psig (172 kPa) of air.

5. Inlet-Vane Operators:  High pressure, with pilot positioners.

E. Zone Dampers:  Two single-blade, [galvanized-steel] [aluminum] [extruded-aluminum] dampers offset 90 degrees from each other on [cadmium-plated ]steel operating rod rotating in sintered bronze or nylon bearings mounted in a single [galvanized-steel] [aluminum] [extruded-aluminum] frame.  Provide blade gaskets and edge seals, and mechanically fasten blades to operating rod.

F. Face-and-Bypass Dampers:  Opposed-blade, [galvanized-steel] [aluminum] [extruded-aluminum] dampers with [cadmium-plated ]steel operating rods rotating in sintered bronze or nylon bearings mounted in a single [galvanized-steel] [aluminum] [extruded-aluminum] frame and with operating rods connected with a common linkage.  Provide blade gaskets and edge seals, and mechanically fasten blades to operating rod.

Mixing box in first paragraph below is standard quality.  Low-leakage dampers are available from some manufacturers and from manufacturers of temperature-control equipment.

G. Outdoor- and Return-Air Mixing Dampers:  Parallel-blade, [galvanized-steel] [aluminum] [extruded-aluminum] dampers mechanically fastened to [cadmium-plated ]steel operating rod in reinforced cabinet.  Connect operating rods with common linkage and interconnect linkages so dampers operate simultaneously.

H. Outdoor- and Return-Air Dampers:  Low-leakage, double-skin, airfoil-blade, [galvanized-steel] [aluminum] [extruded-aluminum] dampers with compressible jamb seals and extruded-vinyl blade edge seals in [opposed] [parallel]-blade arrangement with [cadmium-plated ]steel operating rods rotating in [stainless-steel sleeve] [sintered bronze or nylon] bearings mounted in a single [galvanized-steel] [aluminum] [extruded-aluminum] frame, and with operating rods connected with a common linkage.  Leakage rate shall not exceed 5 cfm/sq. ft. (0.22 L/s per sq. m) at 1-inch wg (250 Pa) and 9 cfm/sq. ft. (0.4 L/s per sq. m) at 4-inch wg (1.0 MPa).

I. Mixing Section:  Multiple-blade, air-mixer assembly located immediately downstream of mixing section.

J. Combination Filter and Mixing Section:

1. Cabinet support members shall hold 2-inch- (50-mm-) thick, pleated, flat, permanent or throwaway filters.

2. Multiple-blade, air-mixer assembly shall mix air to prevent stratification, located immediately downstream of mixing box.

2.7 HUMIDIFIERS

Retain this article to require that humidifiers be provided by air-handling unit manufacturer; delete if humidifiers are specified in Division 23 Section "Humidifiers."

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 5.13 - "Humidifiers and Water-Spray Systems" sets requirements for humidifiers and water-spray systems.  If applying for LEED certification, comply with requirements in ASHRAE 62.1-2004.  LEED-NC Credit EQ 7.1 requires humidity control.

A. Steam Grid Humidifier:

1. Manifold:

Retain one or more of first four subparagraphs below.

a. ASTM A 666, Type 304 stainless steel.

b. Steam jacketed.

c. Insulated with 1/2-inch (13-mm) fiberglass and stainless-steel jacket.

d. Manifold shall extend the full width of unit with mounting brackets at ends.

2. Steam Separator:  [Cast iron,] [ASTM A 666, Type 304 stainless steel,] with [separate ]humidifier control valve.

Retain one of first two subparagraphs below.

3. Humidifier Control Valve:  Actuator:  [Pneumatic] [Electric] modulating with spring return.

4. Humidifier Control Valve:  Actuator:  As specified in Division 23 Section "Instrumentation and Control for HVAC."

5. Steam Trap:  Inverted-bucket type, sized for a minimum of three times the maximum rated condensate flow of humidifier at 1/2-psig (3.4-kPa) inlet pressure.

6. Aquastat:  For separate mounting on steam condensate, return piping to prevent cold operation of humidifier.

7. Strainer:  In-line type.

8. Airflow Switch:  To prevent humidifier operation in the absence of airflow.

B. Wet Glass Cell Washer Section:

1. 3-inch- (75-mm-) deep cells with random packed, glass-fiber media in [galvanized] [stainless]-steel frames.

2. Access Door:  Watertight with brass fittings[, wire glass window,] and locking handles.

3. Spray Tree Assembly:  [Brass] [Stainless-steel] nozzles and [galvanized] [stainless]-steel piping.

4. Eliminator:  [Galvanized] [Stainless]-steel plates.

5. Tank:

a. Welded[ stainless] steel[, with interior and exterior surfaces blasted and painted with zinc-chromate paint].

b. Copper suction screen.

c. Drain, overflow, and suction connections.

d. Makeup connection with [brass ]float valve, and with quick-fill connection.

6. Insulate exterior with duct insulation and mount on 2-inch (-(50-mm-)) thick, rigid insulation board.

C. Evaporative Humidifier Section:

1. Access Door:  Watertight [cast iron ]with brass fittings, wire glass window, and locking handles.

2. Spray Tree Assembly:  Brass nozzles and galvanized piping, [galvanized eliminator plates with flooding nozzles and header, and galvanized antisplash baffles] [cross-fluted cellulose media].

3. Tank:

a. Welded steel tank with interior and exterior surfaces blasted and painted with zinc-chromate paint.

b. Copper suction screen, drain, overflow, and suction connections.

c. Makeup connection with [brass ]float valve, and with quick-fill connection.

4. Insulation:  Insulate with duct insulation on exterior and mount on 2-inch (-(50-mm-)) thick, rigid insulation board.

2.8 AIR-TO-AIR ENERGY RECOVERY

Retain this article to require that air-to-air energy recovery units be provided by air-handling unit manufacturer; delete if air-to-air energy recovery units are specified in Division 23 Section "Air-to-Air Energy Recovery Equipment."

A. Heat Wheels:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Airxchange.

b. American Energy Exchange, Inc.

c. Loren Cook Company.

d. SEMCO Incorporated.

e. Trane; American Standard Inc.

f. <Insert manufacturer's name>.

3. Casing:

a. Steel, with manufacturer's standard paint coating.

b. Integral purge section limiting carryover of exhaust air to between 0.05 percent at 1.6-inch wg and 0.20 percent at 4-inch wg (0.05 percent at 400-Pa and 0.20 percent at 1000-Pa) differential pressure.

c. Casing seals on periphery of rotor, on duct divider, and on purge section.

d. Support rotor on grease-lubricated ball bearings with extended grease fittings.  Mount horizontal wheels on tapered roller bearing.

Retain one of first two subparagraphs below.

4. Rotor:  Aluminum, segmented wheel, strengthened with radial spokes[, with nontoxic, noncorrosive, silica-gel desiccant coating].  Construct media for passing maximum [500] [800] [1200]-micrometer solids.

5. Rotor:  [Glass-fiber] [Polymer] segmented wheel, strengthened with radial spokes impregnated with nonmigrating, water-selective, molecular-sieve desiccant coating. Construct media for passing maximum [800] [1200]-micrometer solids.

6. Drive:  Fractional horsepower motor and gear reducer[, with speed changed by variable frequency controller,] and self-adjusting multilink belt around outside of rotor.

Retain subparagraph below to require that controls be an integral part of air-handling unit; delete if controls are specified in Division 23 Section "Instrumentation and Control for HVAC."

7. Controls:

a. Starting relay, factory mounted and wired, and manual motor starter for field wiring.

Retain one of first three subparagraphs below.

b. Variable frequency controller, factory mounted and wired, permitting input of field connected 4-20 mA or 1-10-V control signal.

c. Variable frequency controller, factory mounted and wired, with exhaust-air sensor to vary rotor speed and maintain exhaust temperature above freezing.

d. Variable frequency controller, factory mounted and wired, with exhaust- and outdoor-air sensors, automatic changeover thermostat and set-point adjuster, to vary rotor speed and maintain [exhaust temperature above freezing and] air differential temperature above set point.  Provide maximum rotor speed when exhaust-air temperature is less than outdoor-air temperature.

e. Pilot-Light Indicator:  Display rotor rotation and speed.

f. Speed Settings:  Adjustable settings for maximum and minimum rotor speed limits.

B. Fixed-Plate Sensible Heat Exchangers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Energy Exchange, Inc.

b. Des Champs Technologies.

c. Exothermics Inc.; a brand of Eclipse, Inc.

d. Nutech Brands Inc.

e. RenewAire LLC.

f. <Insert manufacturer's name>.

3. Casing:  [Aluminum] [Galvanized steel] [Enameled steel, with galvanized-steel liner] [Enameled steel].

4. Plates:  Evenly spaced and sealed and arranged for counter airflow.

5. Plate Material:  [Embossed aluminum] [Stainless steel] [Polypropylene copolymer (high-density plastic)].

Coatings are available for aluminum plates in corrosive atmospheres.

a. Plate Coating:  [Epoxy] [Air-dried phenolic].

6. Bypass:  Plenum within casing, with gasketed face-and-bypass dampers that have operating rods extended outside casing.

Water wash and detergent injection are available optional features.

7. Water Wash:  Automatic system, with spray manifold to individual spray tubes or traversing type with stainless-steel-screw operating mechanism and electric motor drive; activated by time clock[, with detergent injection].

8. Heat-Exchanger Prefilters:  [1 inch (25 mm) thick, disposable] [2 inches (50 mm) thick, disposable] [Medium efficiency] [Electrostatic].

2.9 CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of air-handling unit, delete this article and schedule air-handling units on Drawings.

A. Casing:

Retain one of first three subparagraphs below.

1. Outside Casing:  Galvanized steel, minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] <Insert value> thick.

2. Outside Casing:  Aluminum, minimum [0.050 inch (1.3 mm)] [0.063 inch (1.6 mm)] [0.080 inch (2.0 mm)] <Insert value> thick.

3. Outside Casing:  Stainless steel, minimum [0.050 inch (1.3 mm)] [0.0625 inch (1.6 mm)] [0.0781 inch (2.0 mm)] <Insert value> thick.

Retain one of first three subparagraphs below.

4. Inside Casing:  Galvanized steel, [solid] [perforated], minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] <Insert value> thick.

5. Inside Casing:  Aluminum, [solid] [perforated], minimum [0.050 inch (1.3 mm)] [0.063 inch (1.6 mm)] [0.080 inch (2.0 mm)] <Insert value> thick.

6. Inside Casing:  Stainless steel, [solid] [perforated], minimum [0.050 inch (1.3 mm)] [0.0625 inch (1.6 mm)] [0.0781 inch (2.0 mm)] <Insert value> thick.

Retain one of first three subparagraphs below.

7. Floor Plate:  Galvanized steel, minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] <Insert value> thick.

8. Floor Plate:  Aluminum, minimum [0.040 inch (1.0 mm)] [0.050 inch (1.3 mm)] [0.063 inch (1.6 mm)] [0.080 inch (2.0 mm)] <Insert value> thick.

9. Floor Plate:  Stainless steel, minimum [0.050 inch (1.3 mm)] [0.0625 inch (1.6 mm)] [0.0781 inch (2.0 mm)] <Insert value> thick.

10. Insulation Thickness:  [1 inch (25 mm)] [1-1/2 inches (40 mm)] [2 inches (50 mm)] <Insert value>.

11. Static-Pressure Classifications for Unit Sections before Fans:  [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] [6-inch wg (1500 Pa)] [8-inch wg (2000 Pa)] [9-inch wg (2250 Pa)] [10-inch wg (2500 Pa)] <Insert value>.

12. Static-Pressure Classifications for Unit Sections after Fans:  [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] [6-inch wg (1500 Pa)] [8-inch wg (2000 Pa)] [9-inch wg (2250 Pa)] [10-inch wg (2500 Pa)] <Insert value>.

B. Supply Fan:

1. [Class I] [Class II] [Class III]:  AMCA 99-2408.

2. Drive:  [V-belt] [Direct].

3. Type:  [Steel, backward-inclined centrifugal] [Aluminum, backward-inclined centrifugal] [Black-steel, forward-curved centrifugal] [Galvanized-steel, forward-curved centrifugal] [Steel, airfoil centrifugal] [Aluminum, airfoil centrifugal] [Cast-aluminum axial].

4. Number of Fan Wheels:  <Insert number>.

5. Fan Diameter :  <Insert inches (mm)>.

6. Fan Housing and Wheel Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name; trade name>.

7. Airflow:  <Insert cfm (L/s)>.

8. Total Static Pressure:  <Insert inches wg (kPa)>.

9. External Static Pressure:  <Insert inches wg (kPa)>.

10. Speed:  <Insert rpm>.

11. Maximum Outlet Velocity:  <Insert fpm (m/s)>.

12. Inlet vane controls.

13. Motor Size:  <Insert horsepower>.

14. Motor Speed:  <Insert rpm>.

15. Electrical Characteristics:

a. Volts:  [120] [208] [230] <Insert value>.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

16. Fan Discharge Sound Power:

a. 1st Octave:  <Insert value>.

b. 2nd Octave:  <Insert value>.

c. 3rd Octave:  <Insert value>.

d. 4th Octave:  <Insert value>.

e. 5th Octave:  <Insert value>.

f. 6th Octave:  <Insert value>.

g. 7th Octave:  <Insert value>.

h. 8th Octave:  <Insert value>.

C. [Exhaust] [Return] Fan:

1. [Class I] [Class II] [Class III]:  AMCA 99-2408.

2. Drive:  [V-belt] [Direct].

3. Type:  [Steel, backward-inclined centrifugal] [Aluminum, backward-inclined centrifugal] [Black-steel, forward-curved centrifugal] [Galvanized-steel, forward-curved centrifugal] [Steel, airfoil centrifugal] [Aluminum, airfoil centrifugal] [Cast-aluminum axial].

4. Number of Fan Wheels:  <Insert value>.

5. Fan Diameter:  <Insert inches (mm)>.

6. Fan Housing and Wheel Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name; trade name>.

7. Airflow:  <Insert cfm (L/s)>.

8. Total Static Pressure:  <Insert inches wg (kPa)>.

9. External Static Pressure:  <Insert inches wg (kPa)>.

10. Speed:  <Insert rpm>.

11. Maximum Outlet Velocity :  <Insert fpm (m/s)>.

12. Inlet vane controls.

13. Motor Size:  <Insert horsepower>.

14. Motor Speed:  <Insert rpm>.

15. Electrical Characteristics:

a. Volts:  [120] [208] [230] <Insert value>.

b. Phase:  [Single] [Three].

c. Hertz:  60.

d. Full-Load Amperes:  <Insert value>.

e. Minimum Circuit Ampacity:  <Insert value>.

f. Maximum Overcurrent Protection:  <Insert amperage>.

D. Preheat Coil:

1. Heat-Transfer Rate:  <Insert Btu/h (kW)>.

2. Entering-Air Temperature:  <Insert deg F (deg C)>.

3. Leaving-Air Temperature:  <Insert deg F (deg C)>.

4. Face Area:  <Insert sq. ft. (sq. m)>.

5. Maximum Face Velocity:  <Insert fpm (m/s)>.
6. Maximum Air-Side, Static-Pressure Drop:  <Insert inches wg (Pa)>.

Retain one of first two subparagraphs below.

7. Coil Type:  [Continuous circuit] [Self-draining] [Cleanable].

8. Coil Type:  [Steam distributed] [Single tube].

Retain third option in first subparagraph below for freeze protection.

9. Piping Connections:  [Threaded] [Flanged], [same end] [opposite ends] of coil.

10. Tube Material:  [Copper] <Insert material>.

11. Tube Thickness:  <Insert inches (mm)>.

12. Fin Type:  [Plate] [Spiral].

13. Fin Material:  [Aluminum] [Copper].

14. Fin Spacing:  [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.80 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.42 mm)] [0.0075 inch (0.19 mm)] <Insert fins per inch (mm)>.

15. Fin Thickness:  <Insert inches (mm)>.

16. Fin and Tube Joint:  [Mechanical bond] [Silver brazed].

17. Headers:

a. Cast iron with[ cleaning plugs and] drain and air vent tappings[ extended to exterior of unit].

b. Seamless copper tube with brazed joints, prime coated.

c. Fabricated steel, with brazed joints, prime coated.

d. Provide insulated cover to conceal headers exposed outside casings.

18. Frames:  Channel frame, [0.052-inch- (1.3-mm-) thick galvanized steel] [0.064-inch- (1.6-mm-) thick galvanized steel] [0.079-inch- (2.0-mm-) thick galvanized steel] [0.0625-inch- (1.58-mm-) thick galvanized steel] [0.0625-inch- (1.58-mm-) thick stainless steel].

19. Number of Rows:  <Insert number>.

Pressure and temperature ratings in first subparagraph below are standard for most copper tube coils.  Other materials have different ratings.

20. Coil Working-Pressure Ratings:  [200 psig (1380 kPa), 325 deg F (163 deg C)] <Insert value>.

21. Water:

a. Water Flow:  <Insert gpm (L/s)>.

b. Maximum Water Pressure Drop:  <Insert feet of head (kPa)>.

c. Entering-Water Temperature:  <Insert deg F (deg C)>.

d. Leaving-Water Temperature:  <Insert deg F (deg C)>.

e. Tube Velocity:  <Insert fpm (L/s)>.

22. Steam:

a. Steam Flow:  <Insert lb/h (g/s)>.

b. Inlet Steam Pressure:  <Insert psig (kPa)>.

c. Outer-Tube Diameter:  <Insert inches (mm)>.

23. Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name; trade name>.

Retain subparagraph below for integral face-and-bypass dampers on water or steam coils.

24. Integral Face-and-Bypass Dampers:  [Horizontal] [Vertical], opposed-blade, [galvanized-steel] [aluminum] [extruded-aluminum] dampers with [cadmium-plated ]steel operating rods rotating in sintered bronze or nylon bearings mounted in a single [galvanized-steel] [aluminum] [extruded-aluminum] frame, with operating rods connected with a common linkage.  Meeting edges of blades shall have gaskets and edge seals, and blades shall be mechanically fastened.

E. Heating Coil:

1. Heat-Transfer Rate:  <Insert Btu/h (kW)>.

2. Entering-Air Temperature:  <Insert deg F (deg C)>.

3. Leaving-Air Temperature:  <Insert deg F (deg C)>.

4. Face Area:  <Insert sq. ft. (sq. m)>.

5. Maximum Face Velocity:  <Insert fpm (m/s)>.

6. Maximum Air-Side, Static-Pressure Drop:  <Insert inches wg (Pa)>.

Retain one of first two subparagraphs below.

7. Coil Type:  [Continuous circuit] [Self-draining] [Cleanable].

8. Coil Type:  [Steam distributed] [Single tube].

Retain third option in first subparagraph below for freeze protection.

9. Piping Connections:  [Threaded] [Flanged], [same end] [opposite ends] of coil.

10. Tube Material:  [Copper] <Insert material>.

11. Tube Thickness:  <Insert inches (mm)>.

12. Fin Type:  [Plate] [Spiral].

13. Fin Material:  [Aluminum] [Copper].

14. Fin Spacing:  [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.80 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.42 mm)] [0.0075 inch (0.19 mm)] <Insert fins per inch (mm)>.

15. Fin Thickness:  <Insert inches (mm)>.

16. Fin and Tube Joint:  [Mechanical bond] [Silver brazed].

17. Headers:

a. Cast iron with [cleaning plugs and ]drain and air vent tappings[ extended to exterior of unit].

b. Seamless copper tube with brazed joints, prime coated.

c. Fabricated steel, with brazed joints, prime coated.

d. Provide insulated cover to conceal headers exposed outside casings.

18. Frames:  Channel frame, [0.052-inch- (1.3-mm-) thick galvanized steel] [0.064-inch- (1.6-mm-) thick galvanized steel] [0.079-inch- (2.0-mm-) thick galvanized steel] [0.0625-inch- (1.58-mm-) thick galvanized steel] [0.0625-inch- (1.58-mm-) thick stainless steel].

19. Number of Rows:  <Insert number>.

Pressure and temperature ratings in first subparagraph below are standard for most copper tube coils.  Other materials have different ratings.

20. Coil Working-Pressure Ratings:  [200 psig (1380 kPa), 325 deg F (163 deg C)] <Insert value>.

21. Water:

a. Water Flow:  <Insert gpm (L/s)>.

b. Maximum Water Pressure Drop:  <Insert feet of head (kPa)>.

c. Entering-Water Temperature:  <Insert deg F (deg C)>.

d. Leaving-Water Temperature:  <Insert deg F (deg C)>.

e. Tube Velocity:  <Insert fpm (L/s)>.

22. Steam:

a. Steam Flow:  <Insert lb/h (g/s)>.

b. Inlet Steam Pressure:  <Insert psig (kPa)>.

c. Outer-Tube Diameter:  <Insert inches (mm)>.

23. Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name; trade name>.

Retain subparagraph below for integral face-and-bypass dampers on water or steam coils.

24. Integral Face-and-Bypass Dampers:  [Horizontal] [Vertical], opposed-blade, [galvanized-steel] [aluminum] [extruded-aluminum] dampers with [cadmium-plated ]steel operating rods rotating in sintered bronze or nylon bearings mounted in a single [galvanized-steel] [aluminum] [extruded-aluminum] frame, with operating rods connected with a common linkage.  Meeting edges of blades shall have gaskets and edge seals, and blades shall be mechanically fastened.

F. Electric Heating Coil:

1. Heat-Transfer Rate:  <Insert Btu/h (kW)>.

2. Input:  <Insert kilowatts>.

3. Volts:  [120] [208] [230] <Insert value>.

4. Phase:  [Single] [Three].

5. Full-Load Amperes:  <Insert value>.

6. Number of Steps:  <Insert number>.

G. Cooling Coil:

1. Sensible Heat-Transfer Rate:  <Insert Btu/h (kW)>.

2. Total Heat-Transfer Rate:  <Insert Btu/h (kW)>.

3. Entering-Air, Dry-Bulb Temperature:  <Insert deg F (deg C)>.

4. Entering-Air, Wet-Bulb Temperature:  <Insert deg F (deg C)>.

5. Leaving-Air, Dry-Bulb Temperature:  <Insert deg F (deg C)>.

6. Leaving-Air, Wet-Bulb Temperature:  <Insert deg F (deg C)>.

7. Face Area:  <Insert sq. ft. (sq. m)>.

8. Maximum Face Velocity:  <Insert fpm (m/s)>.

9. Maximum Air-Side, Static-Pressure Drop:  <Insert inches wg (Pa)>.

Retain one of first two subparagraphs below.

10. Coil Type:  [Continuous circuit] [Self-draining] [Cleanable].

Retain third option in first subparagraph below for freeze protection.

11. Piping Connections:  [Threaded] [Flanged], [same end] [opposite ends] of coil.

12. Tube Material:  [Copper] <Insert material>.

13. Tube Thickness:  <Insert inches (mm)>.

14. Fin Type:  [Plate] [Spiral].

15. Fin Material:  [Aluminum] [Copper].

16. Fin Spacing:  [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.80 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.42 mm)] [0.0075 inch (0.19 mm)] <Insert fins per inch (mm)>.

17. Fin Thickness:  <Insert inches (mm)>.

18. Fin and Tube Joint:  [Mechanical bond] [Silver brazed].

19. Headers:

a. Cast iron with[ cleaning plugs and] drain and air vent tappings[ extended to exterior of unit].

b. Seamless copper tube with brazed joints, prime coated.

c. Fabricated steel, with brazed joints, prime coated.

d. Provide insulated cover to conceal headers exposed outside casings.

20. Frames:  Channel frame, [0.052-inch- (1.3-mm-) thick galvanized steel] [0.064-inch- (1.6-mm-) thick galvanized steel] [0.079-inch- (2.0-mm-) thick galvanized steel] [0.0625-inch- (1.58-mm-) thick galvanized steel] [0.0625-inch- (1.58-mm-) thick stainless steel].

21. Number of Rows:  <Insert number>.

Pressure and temperature ratings in first subparagraph below are standard for most copper tube coils.  Other materials have different ratings.

22. Coil Working-Pressure Ratings:  [200 psig (1380 kPa), 325 deg F (163 deg C)] <Insert value>.

23. Water:

a. Water Flow:  <Insert gpm (L/s)>.

b. Maximum Water Pressure Drop:  <Insert feet of head (kPa)>.

c. Entering-Water Temperature:  <Insert deg F (deg C)>.

d. Leaving-Water Temperature:  <Insert deg F (deg C)>.

e. Tube Velocity:  <Insert fpm (L/s)>.

LEED-NC Prerequisite EA 3 requires using CFC-free refrigerants in new HVAC&R systems.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.

24. Refrigerant Type:  <Insert type>.

25. Coating:  [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name; trade name>.

H. Prefilters:

1. Type:  <Insert type>.

2. Face Area:  <Insert sq. ft. (sq. m)>.

3. Surface Area:  <Insert sq. ft. (sq. m)>.

4. Thickness or Depth:  <Insert inches (mm)>.

5. Number of Filters:  <Insert number>.

6. Access Location:  [Front] [Back] [Side].

7. Maximum or Rated Face Velocity:  <Insert fpm (m/s)>.

I. Filters:

1. Type:  <Insert type>.

2. Face Area:  <Insert sq. ft. (sq. m)>.

3. Surface Area:  <Insert sq. ft. (sq. m)>.

4. Thickness or Depth:  <Insert inches (mm)>.

5. Number of Filters:  <Insert number>.

6. Access Location:  [Front] [Back] [Side].

7. Maximum or Rated Face Velocity:  <Insert fpm (m/s)>.

J. Dampers:  [Zone] [Mixing dampers] [Face and bypass].

K. Steam Grid Humidifier:

1. Humidification Rate:  <Insert lb/h (g/s)>.

2. Steam Supply Pressure:  <Insert psig (kPa)>.

3. Dry-Bulb Air Temperature at Discharge:  <Insert deg F (deg C)>.

4. Wet-Bulb Air Temperature at Discharge:  <Insert deg F (deg C)>.

5. Maximum Absorption Distance:  <Insert inches (mm)>.

6. Number of Manifolds:  <Insert number>.

L. Wet Glass Cell Washer:

1. Rated Capacity:  <Insert lb/h (kg/h)>.

2. Saturation Efficiency:  <Insert percent>.

M. Evaporative Humidifier:

1. Rated Capacity:  <Insert lb/h (kg/h)>.

2. Saturation Efficiency:  <Insert percent>.

N. Air-to-Air Energy Recovery:

1. Exhaust Air:

a. Airflow:  <Insert cfm (L/s)>.

b. Face Velocity:  <Insert fpm (m/s)>.

c. Summer:

1) Entering-Air Temperature, Dry Bulb:  <Insert deg F (deg C)>.

2) Entering-Air Temperature, Wet Bulb:  <Insert deg F (deg C)>.

3) Leaving-Air Temperature, Dry Bulb:  <Insert deg F (deg C)>.

4) Leaving-Air Temperature, Wet Bulb:  <Insert deg F (deg C)>.

d. Winter:

1) Entering-Air Temperature, Dry Bulb:  <Insert deg F (deg C)>.

2) Entering-Air Temperature, Wet Bulb:  <Insert deg F (deg C)>.

3) Leaving-Air Temperature, Dry Bulb:  <Insert deg F (deg C)>.

4) Leaving-Air Temperature, Wet Bulb:  <Insert deg F (deg C)>.

e. Air Pressure Drop:  <Insert inches wg (Pa)>.

2. Supply Air:

a. Airflow:  <Insert cfm (L/s)>.

b. Face Velocity:  <Insert fpm (m/s)>.

c. Summer:

1) Entering-Air Temperature, Dry Bulb:  <Insert deg F (deg C)>.

2) Entering-Air Temperature, Wet Bulb:  <Insert deg F (deg C)>.

3) Leaving-Air Temperature, Dry Bulb:  <Insert deg F (deg C)>.

4) Leaving-Air Temperature, Wet Bulb:  <Insert deg F (deg C)>.

d. Winter:

1) Entering-Air Temperature, Dry Bulb:  <Insert deg F (deg C)>.

2) Entering-Air Temperature, Wet Bulb:  <Insert deg F (deg C)>.

3) Leaving-Air Temperature, Dry Bulb:  <Insert deg F (deg C)>.

4) Leaving-Air Temperature, Wet Bulb:  <Insert deg F (deg C)>.

e. Air Pressure Drop:  <Insert inches wg (Pa)>.

Retain first subparagraph below for heat wheels.

3. Wheel Drive:

a. Motor Size:  <Insert horsepower>.

b. Motor Electrical Characteristics:

1) Volts:  [120] [208] [230] <Insert value>.

2) Phase:  [Single] [Three].

3) Hertz:  60.

4. Effectiveness:  <Insert percent>.

2.10 SOURCE QUALITY CONTROL

A. Fan Sound-Power Level Ratings:  Comply with AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data."  Test fans according to AMCA 300, "Reverberant Room Method for Sound Testing of Fans."  Fans shall bear AMCA-certified sound ratings seal.

B. Fan Performance Rating:  Factory test fan performance for airflow, pressure, power, air density, rotation speed, and efficiency.  Rate performance according to AMCA 210, "Laboratory Methods of Testing Fans for Aerodynamic Performance Rating."

C. Water Coils:  Factory tested to 300 psig (2070 kPa) according to ARI 410 and ASHRAE 33.

D. Steam Coils:  Factory tested to 300 psig (2070 kPa) and to 200 psig (1380 kPa) underwater according to ARI 410 and ASHRAE 33.

E. Refrigerant Coils:  Factory tested to 450 psig (3105 kPa) according to ARI 410 and ASHRAE 33.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

B. Examine casing insulation materials and filter media before air-handling unit installation.  Reject insulation materials and filter media that are wet, moisture damaged, or mold damaged.

C. Examine roughing-in for steam, hydronic, and condensate drainage piping systems and electrical services to verify actual locations of connections before installation.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain one of first two paragraphs below for floor-mounted units.  Refer to Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" for other types and applications of vibration-control devices.

Retain first paragraph for equipment supported on concrete base and vibration isolation devices.  Retain "without vibration isolation devices" option for units that have fans with internal vibration isolation and seismic restraints.

A. Equipment Mounting:  Install air-handling units on concrete bases [using elastomeric pads] [using elastomeric mounts] [using restrained spring isolators] [without vibration isolation devices] <Insert device>.  Secure units to anchor bolts installed in concrete bases.  Comply with requirements for concrete bases specified in Division 03 Section "[Cast-in-Place Concrete] [Miscellaneous Cast-in-Place Concrete]." Comply with requirements for vibration isolation devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection:  [1/2 inch (13 mm)] [1 inch (25 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension>.

Retain first subparagraph below if retaining "elastomeric pads" option in "Equipment Mounting" Paragraph above.

2. Install [galvanized] [stainless]-steel plate to equally distribute weight over elastomeric pad.

3. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

4. Install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

5. Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

6. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below for equipment supported on vibration isolation devices without a concrete base.  Retain "without vibration isolation devices" option for units that have fans with internal vibration isolation and seismic restraints.

B. Equipment Mounting:  Install air-handling unit [using elastomeric pads] [using elastomeric mounts] [using restrained spring isolators] [without vibration isolation devices] <Insert device>.  Comply with requirements for vibration isolation devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

1. Minimum Deflection:  [1/4 inch (6 mm)] [1/2 inch (13 mm)] [1 inch (25 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension>.

Retain subparagraph below if retaining "elastomeric pads" option in "Equipment Mounting" Paragraph above.

2. Install [galvanized] [stainless]-steel plate to equally distribute weight over elastomeric pad.

Retain first paragraph below for suspended units.  Retain option for projects in seismic areas.

C. Suspended Units:  Suspend[ and brace] units from structural-steel support frame using threaded steel rods and spring hangers.  Comply with requirements for vibration isolation devices specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

D. Arrange installation of units to provide access space around air-handling units for service and maintenance.

LEED-NC Credit EQ 3.1 requires filters with a minimum MERV 13 rating for the air delivered to the occupied space.  Air-handling units should not be used for temporary heating and ventilating unless expressly approved by Owner.  If used during construction, see SMACNA's "IAQ Guidelines for Occupied Buildings under Construction" for procedures to protect HVAC system.

E. Do not operate fan system until filters (temporary or permanent) are in place.  Replace temporary filters used during construction and testing, with new, clean filters.

F. Install filter-gage, static-pressure taps upstream and downstream of filters.  Mount filter gages on outside of filter housing or filter plenum in accessible position.  Provide filter gages on filter banks, installed with separate static-pressure taps upstream and downstream of filters.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Comply with requirements for piping specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to air-handling unit to allow service and maintenance.

C. Connect piping to air-handling units mounted on vibration isolators with flexible connectors.

D. Connect condensate drain pans using [NPS 1-1/4 (DN 32)] <Insert pipe size>, ASTM B 88, Type M (ASTM B 88M, Type C) copper tubing.  Extend to nearest equipment or floor drain.  Construct deep trap at connection to drain pan and install cleanouts at changes in direction.

E. Hot- and Chilled-Water Piping:  Comply with applicable requirements in Division 23 Section "Hydronic Piping." Install shutoff valve and union or flange at each coil supply connection.  Install balancing valve and union or flange at each coil return connection.

F. Steam and Condensate Piping:  Comply with applicable requirements in Division 23 Section "Steam and Condensate Heating Piping." Install shutoff valve at steam supply connections, float and thermostatic trap, and union or flange at each coil return connection.  Install gate valve and inlet strainer at supply connection of dry steam humidifiers, and inverted bucket steam trap to condensate return connection.

G. Refrigerant Piping:  Comply with applicable requirements in Division 23 Section "Refrigerant Piping." Install shutoff valve and union or flange at each supply and return connection.

Coordinate duct installations and specialty arrangements with schematics on Drawings and with requirements specified in Division 23 Sections "Metal Ducts" and "Air Duct Accessories."

H. Connect duct to air-handling units with flexible connections.  Comply with requirements in Division 23 Section "Air Duct Accessories."

3.4 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

C. Tests and Inspections:

1. Leak Test:  After installation, fill water and steam coils with water, and test coils and connections for leaks.

2. Charge refrigerant coils with refrigerant and test for leaks.

3. Fan Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Retain first subparagraph below for units with automatic roll filters.

4. Automatic-Roll-Filter Operational Test:  Operate filters to demonstrate compliance with requirements.  Test for leakage of unfiltered air while system is operating.

5. HEPA-Filter Operational Test:  Pressurize housing to a minimum of 3-inch wg (750 Pa) or to designed operating pressure, whichever is higher; test housing joints, door seals, and sealing edges of filter with soapy water to check for air leaks.

Retain last subparagraph above or two subparagraphs below for units with HEPA filters.  Retain subparagraphs below in critical applications per ASME N510.

6. HEPA-Filter Operational Test:  Pressurize housing to a minimum of 3-inch wg (750 Pa) or to designed operating pressure, whichever is higher; test housing joints, door seals, and sealing edges of filter for air leaks according to ASME N510, pressure-decay method.

7. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

D. Air-handling unit or components will be considered defective if unit or components do not pass tests and inspections.

E. Prepare test and inspection reports.

3.5 STARTUP SERVICE

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Verify that shipping, blocking, and bracing are removed.

3. Verify that unit is secure on mountings and supporting devices and that connections to piping, ducts, and electrical systems are complete.  Verify that proper thermal-overload protection is installed in motors, controllers, and switches.

4. Verify proper motor rotation direction, free fan wheel rotation, and smooth bearing operations.  Reconnect fan drive system, align belts, and install belt guards.

5. Verify that bearings, pulleys, belts, and other moving parts are lubricated with factory-recommended lubricants.

6. Verify that zone dampers fully open and close for each zone.

7. Verify that face-and-bypass dampers provide full face flow.

8. Verify that outdoor- and return-air mixing dampers open and close, and maintain minimum outdoor-air setting.

9. Comb coil fins for parallel orientation.

10. Verify that proper thermal-overload protection is installed for electric coils.

11. Install new, clean filters.

12. Verify that manual and automatic volume control and fire and smoke dampers in connected duct systems are in fully open position.

B. Starting procedures for air-handling units include the following:

1. Energize motor; verify proper operation of motor, drive system, and fan wheel.  Adjust fan to indicated rpm.[$ds~Replace fan and motor pulleys as required to achieve design conditions.]

2. Measure and record motor electrical values for voltage and amperage.

3. Manually operate dampers from fully closed to fully open position and record fan performance.

3.6 ADJUSTING

A. Adjust damper linkages for proper damper operation.

B. Comply with requirements in Division 23 Section "Testing, Adjusting, and Balancing for HVAC" for air-handling system testing, adjusting, and balancing.

3.7 CLEANING

A. After completing system installation and testing, adjusting, and balancing air-handling unit and air-distribution systems and after completing startup service, clean air-handling units internally to remove foreign material and construction dirt and dust.  Clean fan wheels, cabinets, dampers, coils, and filter housings, and install new, clean filters.

3.8 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain air-handling units.

END OF SECTION 237313

	MODULAR INDOOR CENTRAL-STATION AIR-HANDLING UNITS
	237313 - 1



