Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
03/03 (R 06/06)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238146 - WATER-SOURCE UNITARY HEAT PUMPS
This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include water-source unitary heat pumps may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following types of water-source heat pumps:

Adjust list below to suit Project.

1. Concealed horizontal or vertical units, 6 tons (21 kW) and smaller.

2. Concealed horizontal or vertical units, larger than 6 tons (21 kW).

3. Vertical stack units.

4. Rooftop units.

5. Exposed, floor-mounted console units.

6. Unit ventilators.

1.3 SUBMITTALS

First three paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  Include rated capacities, furnished specialties, and accessories for each model.

B. LEED Submittals:

Retain first subparagraph below for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

1. Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment and refrigerants comply.

2. Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

C. Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal, and control wiring.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Floor plans, reflected ceiling plans, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Revise subparagraphs and associated subparagraphs below to suit Project.

1. Suspended ceiling components.

2. Structural members to which heat pumps will be attached.

3. Method of attaching hangers to building structure.

4. Size and location of initial access modules for acoustical tile.

5. Items penetrating finished ceiling, including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. <Insert item.>

E. Samples for Initial Selection:  For units with factory-applied color finishes.

Delete paragraph above if colors are preselected and specified or scheduled.  Retain first paragraph below with or without above.

F. Samples for Verification:  For each type of unit indicated.

G. Product Certificates:  For each type of water-source heat pump, signed by product manufacturer.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Seismic certification may be required for large units.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

H. Manufacturer Seismic Qualification Certification:  Submit certification that water-source heat pumps, accessories, and components will withstand seismic forces defined in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment." Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

I. Field quality-control test reports.

J. Operation and Maintenance Data:  For water-source heat pumps to include in emergency, operation, and maintenance manuals.

K. Warranty:  Special warranty specified in this Section.

1.4 QUALITY ASSURANCE

Retain first paragraph and subparagraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Division 01 requirements.

A. Product Options:  Drawings indicate size, profiles, and dimensional requirements of water-source heat pumps and are based on the specific system indicated.  Refer to Division 01 Section "Product Requirements."

1. Do not modify intended aesthetic effects, as judged solely by Architect, except with Architect's approval.  If modifications are proposed, submit comprehensive explanatory data to Architect for review.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

C. ASHRAE Compliance:

1. ASHRAE 15.

2. Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EQ 1 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

D. ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

E. Comply with NFPA 70.

F. Comply with safety requirements in UL 484 for assembly of free-delivery water-source heat pumps.

G. Comply with safety requirements in UL 1995 for duct-system connections.

1.5 COORDINATION

A. Coordinate layout and installation of water-source heat pumps and suspension components with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system components, and partition assemblies.

B. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

A. Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of water-source heat pumps that fail in materials or workmanship within specified warranty period.

1. Failures include, but are not limited to, refrigeration components.

Verify available warranties for refrigerant components and insert number below.

2. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. [One] <Insert number>set(s) of matched fan belts for each belt-driven fan.

2. [One] <Insert number>set(s) of filters for each unit.

3. [One] <Insert number> spare heat-pump unit(s) of each size and model furnished.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 CONCEALED WATER-SOURCE HEAT PUMPS, 6 TONS (21 kW) AND SMALLER

Concealed water-source heat pumps, 6 tons (21 kW) and smaller, are characterized by direct-drive fan, domestic water preheat heat-exchanger, and absence of mixing box including outdoor-air dampers.

Many optional features are available for this product and some are mutually exclusive.  Specify all those required for Project.  Identify optional features for specific units in the schedule or on Drawings.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Addison Products Company.

2. Bard Manufacturing Company.

3. Carrier Corporation.

4. ClimateMaster, Inc.

5. FHP Manufacturing Inc.

6. Hydro-Temp Corporation, Inc.

7. Mammoth Inc.

8. McQuay International.

9. Trane.

10. WaterFurnace International, Inc.

11. <Insert manufacturer's name.>

B. Description:  Packaged water-source heat pump with temperature controls; factory assembled, tested, and rated according to ARI-ISO-13256-1.

C. Cabinet and Chassis:  Galvanized-steel casing with the following features:

1. Access panel for access and maintenance of internal components.

2. Knockouts for electrical and piping connections.

3. Flanged duct connections.

4. Cabinet Insulation:  Glass-fiber liner, minimum 1/2 inch (13 mm) thick, complying with UL 181.

Retain option in subparagraph below to comply with LEED-NC Prerequisite EQ 1.

5. Condensate Drainage:  Plastic or stainless-steel drain pan with condensate drain piping projecting through unit cabinet[ and complying with ASHRAE 62.1-2004].

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

6. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain subparagraph and associated subparagraphs below for sound attenuation package.  Verify availability of method selected with specified manufacturer.

7. Sound Attenuation Package:

a. Minimum 0.598-inch- (1.5-mm-) thick compressor enclosure and front panel.  Minimum 0.0937-inch- (2.38-mm-) thick foam gasket around the compressor and perimeter of end panel.

b. Sound attenuating blanket over compressor.

c. Hot-gas muffler.

d. <Insert method.>

D. Fan:  Direct driven, centrifugal, with multispeed motor resiliently mounted in fan inlet.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

2. Motor:  Multispeed, permanently lubricated, [permanent split capacitor] [ECM] motor.

E. Water Circuit:

1. Refrigerant-to-Water Heat Exchangers:

a. Coaxial heat exchangers with [copper] [cupronickel] water tube with enhanced heat-transfer surfaces inside a steel shell; both shell and tube leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side.  Factory mount heat exchanger in unit on resilient rubber vibration isolators.

Retain subparagraph above or below.

b. Stainless-steel, brazed-plate heat exchanger leak tested to 450 psig (3102 kPa) for refrigerant side and 400 psig (2758 kPa) for water side.  Factory mount heat exchanger in unit on resilient rubber vibration isolators.

Verify availability of heat exchanger with manufacturer.

2. Domestic Water Heat Exchanger:  Refrigerant-to-domestic water heat exchanger shall be double-wall-vented type with factory-mounted pump and controls.  Energize pump when domestic-water temperature in heat exchanger is more than [145 deg F (63 deg C)] <Insert temperature>, and temperature in water heater is less than [125 deg F (52 deg C)] <Insert temperature>.

Verify availability of water-side economizer with manufacturer.  Water-side economizer may be field installed on this type of water-source heat pump.  Partial free cooling is available at 55 deg F (13 deg C).

3. Water-Side Economizer:  Copper tube and aluminum fin coil with three-way valve and entering-water temperature sensor and controller.  Valve diverts water to water-side economizer coil ahead of refrigerant-to-water heat exchanger when entering-water temperature falls to [55 deg F (13 deg C)] <Insert temperature>.

Verify availability of water regulating valves and motorized water valves.

4. Water Regulating Valves:  Limit water flow through refrigerant-to-water heat exchanger, and control head pressure on compressor during cooling and heating.  Valves shall close when heat-pump compressor is not running.

5. Motorized Water Valve:  Stop water flow through the unit when compressor is off.

First paragraph below describes both heating/cooling and reheat coils.

F. Refrigerant-to-Air Coils:  Copper tubes with aluminum fins, leak tested to 450 psig (3102 kPa).

G. Refrigerant Circuit Components:

Retain one of first two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second or third option in first subparagraph or retain second subparagraph to comply with Credit EA 4.

1. Sealed Refrigerant Circuit:  Charge with [R-22] [R-407C] [R-410A] refrigerant.

2. Sealed Refrigerant Circuit:  Charge with R-407C or R-410A refrigerant.

Filter-dryer is not available from some manufacturers.

3. Filter-Dryer:  Factory installed to clean and dehydrate the refrigerant circuit.

4. Charging Connections:  Service fittings on suction and liquid for charging and testing.

5. Reversing Valve:  Pilot-operated sliding-type valve designed to be fail-safe in heating position with replaceable magnetic coil.

Options in first subparagraph below depend on unit size.  Verify with manufacturers.  Delete if these features are not specific selection criteria.

6. Compressor:  Hermetic [rotary] [reciprocating] [scroll] compressor installed on vibration isolators and housed in an acoustically treated enclosure with factory-installed safeties as follows:

a. Antirecycle timer.

b. High-pressure cutout.

c. Low-pressure cutout or loss of charge switch.

d. Internal thermal-overload protection.

Retain first two subparagraphs below for compressor safety switches.

e. Freezestat to stop compressor if water-loop temperature in refrigerant-to-water heat exchanger falls below [35 deg F (2 deg C)] <Insert temperature>.

f. Condensate overflow switch to stop compressor with high condensate level in condensate drain pan.

7. Refrigerant Piping Materials:  ASTM B 743 copper tube with wrought-copper fittings and brazed joints.

8. Pipe Insulation:  Refrigerant minimum 3/8-inch- (10-mm-) thick, flexible elastomeric insulation on piping exposed to airflow through the unit.  Maximum 25/50 flame-spread/smoke-development indexes according to ASTM E 84.

9. Refrigerant Metering Device:  Capillary tube.

Retain subparagraph above or below.

10. Refrigerant Metering Device:  Thermal expansion valve to allow specified operation with entering-water temperatures from [25 to 125 deg F (minus 4 to plus 52 deg C)] <Insert temperature>.

Retain subparagraph below for hot-gas reheat.

11. Hot-Gas Reheat Valve:  Pilot-operated sliding-type valve with replaceable magnetic coil.

Electric heating coil is an optional feature for "boilerless" system.  Some features are mutually exclusive.  Verify availability with manufacturer.  Temperature set point is adjustable and will vary with system type.

H. Electric Heating Coil:  Helix-wound, nickel-chromium wire-heating elements in ceramic insulators mounted on steel supports.  Energize on call for heating when entering-water-loop temperature is less than [25 deg F (minus 4 deg C)] [40 deg F (5 deg C)] [60 deg F (15deg C)] <Insert temperature>.

Retain paragraph below for hot-gas reheat for humidity control; water regulating valves may be required.

I. Hot-Gas Reheat:  Reheat valve diverts refrigerant hot gas to reheat coil when remote humidistat calls for dehumidification.

Retain one of first two paragraphs below.  Verify availability of filter options in first paragraph with manufacturers.  Retain second paragraph if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

J. Filters:  Disposable, glass-fiber, flat type, [1 inch (25 mm)] <Insert thickness> thick, treated with adhesive, and having a minimum of 80 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 5 according to ASHRAE 52.2.

K. Filters:  Disposable, pleated type, [1 inch (25 mm)] <Insert thickness> thick and with a minimum of 90 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 7 according to ASHRAE 52.2.

L. Control equipment and sequence of operation are specified in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

Retain paragraph above and delete paragraph and subparagraphs below if controls are part of overall temperature-control system.

M. Controls:

1. Basic Unit Controls:

a. Low- and high-voltage protection.

b. Overcurrent protection for compressor and fan motor.

c. Random time delay, three to ten seconds, start on power up.

d. Time delay override for servicing.

e. Control voltage transformer.

Retain subparagraphs and associated subparagraphs below to suit Project; delete those not required.  Verify availability with manufacturers.

2. Thermostat:

a. Wall-Mounted Thermostat:

1) Heat-cool-off switch.

2) Fan on-auto switch.

3) [Manual] [Automatic] changeover.

4) [Concealed] [Exposed] temperature set point.

5) [Concealed] [Exposed] temperature indication.

6) Deg [F] [C] indication.

b. Wall-Mounted Humidistat:  [Concealed] [Exposed].

1) Temperature set point.

2) Temperature indication.

c. Wall-mounted temperature sensor.

d. Unoccupied period override push button.

e. LED to indicate fault condition at heat pump.

f. Data entry and access port.

1) Input data include room temperature and humidity set points for occupied and unoccupied periods.

2) Output data include room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

3. Terminal Controller:

a. Scheduled operation for occupied and unoccupied periods on [7] [365]-day clock with minimum 4 programmable periods per day.

b. [Two] <Insert number>-hour unoccupied period override period.

c. Remote control panel to contain programmable timer and LED for fault condition.

d. Compressor disable relay to stop compressor operation for demand limiting or switch to unoccupied operation.

e. Automatic restart after five minutes if fault clears.  Lockout after three attempts to restart following fault.  Indicate fault for service technician.

f. Return-air temperature high-limit (firestat).  Stop unit on high temperature.

g. Backup for volatile memory.

h. Differential pressure switch to indicate fan status.  Fan failure alarm.

i. Differential pressure switch to indicate filter status.  Dirty filter alarm.

4. BAS interface requirements as further described in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

a. Interface relay for scheduled operation.

b. Interface relay to provide indication of fault at central workstation.

c. Provide [BAC-net] [or] [Lonworks] interface for central BAS workstation for the following functions:

1) Set-point adjustment for set points identified in this Section.

2) Start/stop and operating status of heat-pump unit.

3) Data inquiry to include supply air, room air temperature and humidity, and entering-water temperature.

4) Occupied and unoccupied schedules.

N. Electrical Connection:  Single electrical connection[ with fused disconnect].

If Project has more than one of this type of heat pump, delete paragraph and subparagraphs below and schedule heat pumps on Drawings.

O. Capacities and Characteristics:

1. Fan:

a. Airflow:  <Insert cfm (L/s).>

b. External Static Pressure:  <Insert inches wg (kPa).>

c. Fan Speed:  <Insert rpm.>

d. Maximum Brake Horsepower for Fan:  <Insert value.>

e. Motor Speed:  <Insert rpm.>

f. Motor Horsepower:  <Insert value.>

2. Water Supply:

a. Water Flow:  <Insert gpm (L/s).>

b. Pressure Loss:  <Insert feet wg (kPa).>

c. Entering-Water Temperature (Cooling):  <Insert deg F (deg C).>

d. Entering-Water Temperature (Heating):  <Insert deg F (deg C).>

e. Antifreeze Protection Chemical:  <Insert chemical name.>

f. Antifreeze Concentration:  <Insert percent.>

3. Cooling:

a. Total Capacity:  <Insert Btu/h (kW).>

b. Sensible Capacity:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

c. Minimum Energy-Efficiency Ratio (EER):  <Insert value.>

d. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

e. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

4. Heating:

a. Capacity:  <Insert Btu/h (kW).>

b. Entering-Air Temperature:  <Insert deg F (deg C).>

c. Air Temperature Rise:  <Insert deg F (deg C).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

d. Minimum Coefficient of Performance (COP):  <Insert value.>

5. Electric Heating Coil (Optional Feature):

a. Capacity:  <Insert Btu/h (kW).>

b. Number of Steps:  <Insert number.>

6. Water-Side Economizer (Optional Feature):

a. Total Cooling Capacity:  <Insert Btu/h (kW).>

b. Sensible Cooling Capacity:  <Insert Btu/h (kW).>

c. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

d. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

e. Entering-Water Temperature:  <Insert deg F (deg C).>

f. Water Flow:  <Insert gpm (L/s).>

g. Pressure Loss:  <Insert feet wg (kPa).>

7. Domestic Water Heat Exchanger (Optional Feature)

a. Heating Capacity:  <Insert Btu/h (kW).>

b. Entering-Domestic Water Temperature:  <Insert deg F (deg C).>

c. Domestic Water Flow:  <Insert gpm (L/s).>

d. Pressure Loss:  <Insert feet wg (kPa).>

8. Filters:

a. Face Area:  <Insert sq. ft. (sq. m).>

b. Maximum Face Velocity:  <Insert fpm (m/s).>

9. Electrical Characteristics for Single Connection:

a. Volts/Phase/Hertz:  <Insert values.>

b. FLA (Full-Load Amperes):  <Insert value.>

c. MCA (Maximum Circuit Amperes):  <Insert value.>

d. MOCP (Maximum Overcurrent Protection):  <Insert value.>

2.3 CONCEALED WATER-SOURCE HEAT PUMPS, LARGER THAN 6 TONS (21 kW)
Concealed water-source heat pumps larger than 6 tons (21 kW) are characterized by belt-drive fan and absence of mixing box including outdoor-air dampers.

Many optional features are available for this product and some are mutually exclusive.  Specify all those required for Project.  Identify optional features for specific units in the schedule or on Drawings.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Addison Products Company.

2. Bard Manufacturing Company.

3. Carrier Corporation.

4. ClimateMaster, Inc.

5. FHP Manufacturing Inc.

6. Hydro-Temp Corporation, Inc.

7. Mammoth Inc.

8. McQuay International.

9. Trane.

10. WaterFurnace International, Inc.

11. <Insert manufacturer's name.>

B. Description:  Packaged water-source heat pump with temperature controls; factory assembled, tested, and rated according to ARI-ISO-13256-1.

C. Cabinet and Chassis:  Galvanized-steel casing with the following features:

1. Access panel for access and maintenance of internal components.

2. Knockouts for electrical and piping connections.

3. Flanged duct connections.

4. Cabinet Insulation:  Glass-fiber liner, 1 inch (25 mm) thick, complying with UL 181.

Retain option in subparagraph below to comply with LEED-NC Prerequisite EQ 1.

5. Condensate Drainage:  Plastic or stainless-steel drain pan with condensate drain piping projecting through unit cabinet[ and complying with ASHRAE 62.1-2004].

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

6. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain subparagraph and associated subparagraphs below for sound attenuation package.  Verify availability of method selected with specified manufacturer.

7. Sound Attenuation Package:

a. Minimum 0.598-inch- (1.5-mm-) thick compressor enclosure and front panel.  Minimum 0.0937-inch- (2.38-mm-) thick foam gasket around the compressor and perimeter of end panel.

b. Sound attenuating blanket over compressor.

c. Hot-gas muffler.

d. <Insert method.>

D. Fan:  Belt driven, centrifugal, with single-speed motor installed on an adjustable fan base resiliently mounted in cabinet.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.  Permanently lubricated ball bearings are available for motors up to and including 5 hp.  Larger motors have grease-lubricated ball bearings.

1. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

E. Water Circuit:

1. Refrigerant-to-Water Heat Exchanger:

Retain one or more of first three options in subparagraph below.  Retain more than one to allow more than one component, or delete all to allow any of the three.

a. [Coaxial] [Coil-in-shell] [Shell-and-tube] heat exchanger with [copper] [cupronickel] water tube with enhanced heat-transfer surfaces inside a steel shell; both shell and tube leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side.  Factory mount heat exchanger in unit on resilient rubber vibration isolators.

Retain subparagraph above or below; retain both to allow either component.

b. Stainless-steel brazed plate heat exchanger leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side.  Factory mount heat exchanger in unit on resilient rubber vibration isolators.

Verify availability of water-side economizer with manufacturer.  Water-side economizer may be field installed on this type of water-source heat pump.  Partial free cooling is available at 55 deg F (13 deg C).

2. Water-Side Economizer:  Copper tube and aluminum fin coil leak tested at 400 psig (2758 kPa) with 3-way valve and entering-water temperature sensor and controller.  Valve diverts water to water-side economizer coil ahead of refrigerant-to-water heat exchanger when entering-water temperature falls to [55 deg F (13 deg C)] <Insert temperature>.

Verify availability of water regulating valves and motorized water valves.

3. Water Regulating Valves:  Limit water flow through refrigerant-to-water heat exchanger, and control head pressure on compressor during cooling and heating.  Valves shall close when heat-pump compressor is not running.

4. Motorized Water Valve:  Stop water flow through the unit when compressor is off.

First paragraph below describes both heating/cooling and reheat coils.

F. Refrigerant-to-Air Coils:  Copper tubes with aluminum fins, leak tested to 450 psig (3102 kPa).

G. Refrigerant Circuit Components:

1. Sealed Refrigerant Circuit:  Minimum of 2 circuits required for units [10 tons (35 kW)] <Insert nominal capacity> and larger.  Intertwine circuits in refrigerant to air coil.

Retain one of two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second or third option in first subparagraph or retain second subparagraph to comply with Credit EA 4.

a. Charge with [R-22] [R-407C] [R-410A] refrigerant.

b. Charge with R-407C or R-410A refrigerant.

Filter-dryer is not available from some manufacturers.

2. Filter-Dryer:  Factory installed to clean and dehydrate each refrigerant circuit.

3. Charging Connections:  Service fittings on suction and liquid for charging and testing on each circuit.

4. Reversing Valve:  Pilot-operated sliding-type valve designed to be fail-safe in heating position with replaceable magnetic coil.

Options in first subparagraph below depend on unit size.  Verify with manufacturers.  Delete if these features are not specific selection criteria.

5. Compressor:  [Hermetic reciprocating] [Hermetic scroll] [Semihermetic reciprocating] compressor installed on vibration isolators housed in an acoustically treated enclosure with factory-installed safeties as follows:

a. Antirecycle timer.

b. High-pressure cutout.

c. Low-pressure cutout or loss of charge switch.

d. Internal thermal-overload protection.

Retain first subparagraph below for compressor safety switches.

e. Freezestat to stop compressor if water-loop temperature in refrigerant-to-water heat exchanger falls below [35 deg F (2 deg C)] <Insert temperature>.

f. Condensate overflow switch to stop compressor with high condensate level in condensate drain pan.

6. Refrigerant Piping Materials:  ASTM B 743 copper tube with wrought-copper fittings and brazed joints.

7. Pipe Insulation:  Refrigerant minimum 3/8-inch- (10-mm-) thick, flexible elastomeric insulation on piping exposed to airflow through the unit.  Maximum 25/50 flame-spread/smoke-development indexes per ASTM E 84.

8. Refrigerant Metering Device:  Capillary tube.

Retain subparagraph above or below.

9. Refrigerant Metering Device:  Thermal expansion valve to allow specified operation with entering-water temperatures from 25 to 125 deg F (minus 4 to plus 52 deg C).

Retain subparagraph below for hot-gas reheat.

10. Hot-Gas Reheat Valve:  Pilot-operated sliding-type valve with replaceable magnetic coil.

Electric heating coil is an optional feature for "boilerless" system.  Some features are mutually exclusive.  Verify availability with manufacturer.  Temperature set point is adjustable and will vary with system type.

H. Electric Heating Coil:  Helix-wound, nickel-chromium wire-heating elements in ceramic insulators mounted on steel supports.  Energize on call for heating when entering-water-loop temperature is less than [25 deg F (minus 4 deg C)] [40 deg F (5 deg C)] [60 deg F (15deg C)] <Insert temperature>.

Retain paragraph below for hot-gas reheat for humidity control; water regulating valves may be required.

I. Hot-Gas Reheat:  Reheat valve diverts refrigerant hot gas to reheat coil when remote humidistat calls for dehumidification.

Retain paragraph below for hot-gas bypass for capacity control; water regulating valves may be required.

J. Hot-Gas Bypass:  Include constant pressure expansion valve, solenoid valve, and controls to maintain continuous refrigeration system operation at 10 percent of full load on lead compressor.

Retain one of first two paragraphs below.  Verify availability of filter options in first paragraph with manufacturers.  Retain second paragraph if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

K. Filters:  Disposable, glass-fiber, flat type, [1 inch (25 mm)] [2 inches (50 mm)] [4 inches (100 mm)] <Insert thickness> thick, treated with adhesive, and having a minimum of 80 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 5 according to ASHRAE 52.2.

L. Filters:  Disposable, pleated type, [1 inch (25 mm)] [2 inches (50 mm)] [4 inches (100 mm)] <Insert thickness> thick and with a minimum of 90 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 7 according to ASHRAE 52.2.

M. Control equipment and sequence of operation are specified in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

Retain paragraph above and delete paragraph and subparagraphs below if controls are part of overall temperature-control system.

N. Controls:

1. Basic Unit Controls:

a. Low- and high-voltage protection.

b. Overcurrent protection for compressor and fan motor.

c. Random time delay, three to ten seconds, start on power-up.

d. Time delay override for servicing.

e. Control voltage transformer.

Retain subparagraphs and associated subparagraphs below to suit Project; delete those not required.  Verify availability with manufacturer.

2. Thermostat:

a. Wall-Mounted Thermostat:

1) Heat-cool-off switch.

2) Fan on-auto switch.

3) [Manual] [Automatic] changeover.

4) [Concealed] [Exposed] temperature set point.

5) [Concealed] [Exposed] temperature indication.

6) Deg [F] [C] indication.

7) [One] [Two]-stage heating.

8) [One] [Two]-stage cooling.

b. Wall-Mounted Humidistat:  [Concealed] [Exposed].

1) Temperature set point.

2) Temperature indication.

c. Wall-mounted temperature sensor.

d. Unoccupied period override push button.

e. LED to indicate fault condition at heat pump.

f. Data entry and access port.

1) Input data include room temperature and humidity set points for occupied and unoccupied periods.

2) Output data include room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

3. Terminal Controller:

a. Scheduled operation for occupied and unoccupied periods on [7] [365]-day clock with minimum 4 programmable periods per day.

b. [Two] <Insert number>-hour unoccupied period override period.

c. Remote control panel to contain programmable timer and LED for fault condition.

d. Compressor disable relay to stop compressor operation for demand limiting or switch to unoccupied operation.

e. Automatic restart after five minutes if fault clears.  Lockout after three attempts to restart following fault.  Indicate fault for service technician.

f. Return-air temperature high-limit (firestat).  Stop unit on high temperature.

g. Smoke alarm with smoke detector installed in [supply] [return] [supply and return] air.  Stop unit on smoke detection.

h. Backup for volatile memory.

i. Differential pressure switch to indicate fan status.  Fan failure alarm.

j. Differential pressure switch to indicate filter status.  Dirty filter alarm.

4. BAS interface requirements as further described in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

a. Interface relay for scheduled operation.

b. Interface relay to provide indication of fault at central workstation.

c. Provide [BAC-net] [or] [Lonworks] interface for central BAS workstation for the following functions:

1) Set-point adjustment for set points identified in this Section.

2) Start/stop and operating status of heat-pump unit.

3) Data inquiry to include supply air, room air temperature and humidity, and entering-water temperature.

4) Occupied and unoccupied schedules.

O. Electrical Connection:  Single electrical connection[ with fused disconnect].

If Project has more than one of this type of heat pump, delete paragraph and subparagraphs below and schedule heat pumps on Drawings.

P. Capacities and Characteristics:

1. Fan:

a. Airflow:  <Insert cfm (L/s).>

b. External Static Pressure:  <Insert inches wg (kPa).>

c. Fan Speed:  <Insert rpm.>

d. Maximum Brake Horsepower for Fan:  <Insert value.>

e. Motor Speed:  <Insert rpm.>

f. Motor Horsepower:  <Insert value.>

2. Water Supply:

a. Water Flow:  <Insert gpm (L/s).>

b. Pressure Loss:  <Insert feet wg (kPa).>

c. Entering-Water Temperature (Cooling):  <Insert deg F (deg C).>

d. Entering-Water Temperature (Heating):  <Insert deg F (deg C).>

e. Antifreeze Protection Chemical:  <Insert chemical name.>

f. Antifreeze Concentration:  <Insert percent.>

3. Cooling:

a. Total Capacity:  <Insert Btu/h (kW).>

b. Sensible Capacity:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

c. Minimum Energy-Efficiency Ratio (EER):  <Insert value.>

d. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

e. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

4. Heating:

a. Capacity:  <Insert Btu/h (kW).>

b. Entering-Air Temperature:  <Insert deg F (deg C).>

c. Air Temperature Rise:  <Insert deg F (deg C).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

d. Minimum Coefficient of Performance (COP):  <Insert value.>

5. Electric Heating Coil (Optional Feature):

a. Capacity:  <Insert Btu/h (kW).>

b. Number of Steps:  <Insert number.>

6. Water-Side Economizer (Optional Feature):

a. Total Cooling Capacity:  <Insert Btu/h (kW).>

b. Sensible Cooling Capacity:  <Insert Btu/h (kW).>

c. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

d. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

e. Entering-Water Temperature:  <Insert deg F (deg C).>

f. Water Flow:  <Insert gpm (L/s).>

g. Pressure Loss:  <Insert feet wg (kPa).>

7. Filters:

a. Face Area:  <Insert sq. ft. (sq. m).>

b. Maximum Face Velocity:  <Insert fpm (m/s).>

8. Electrical Characteristics for Single Connection:

a. Volts/Phase/Hertz:  <Insert values.>

b. FLA (Full-Load Amperes):  <Insert value.>

c. MCA (Maximum Circuit Amperes):  <Insert value.>

d. MOCP (Maximum Overcurrent Protection):  <Insert value.>

2.4 VERTICAL-STACK WATER-SOURCE HEAT PUMPS

Vertical-stack water-source heat pumps are distinguished from other types by their approximate cooling capacity of from 1/2 to 3 tons (1.7 to 10.5 kW), direct-drive fans, unfinished cabinet concealed in the occupied space, and absence of outdoor-air dampers.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. ClimateMaster, Inc.

2. Trane.

3. <Insert manufacturer's name.>

B. Description:  Packaged water-source heat pump with temperature controls; factory assembled, tested, and rated according to ARI-ISO-13256-1.

C. Cabinet and Chassis:  Manufacturer's standard galvanized-steel casing with the following features:

1. Return-air opening with access panel for access to internal components.

2. Knockouts for electrical and piping connections.

3. Cabinet Insulation:  Glass-fiber liner, 1/2 inch (13 mm) thick, complying with UL 181.

Retain option in first subparagraph below to comply with LEED-NC Prerequisite EQ 1.

4. Condensate Drainage:  Plastic or stainless-steel drain pan with condensate drain piping projecting to unit exterior[ and complying with ASHRAE 62.1-2004].

5. Discharge Grille:  Double deflection grille for adjustable discharge air pattern.

6. Discharge and Return Grille Color:  Selected by Architect from manufacturer's [standard] [custom] color selection.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

7. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

D. Fan:  Direct driven, centrifugal, with multispeed motor mounted on a removable fan-motor board.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

2. Motor:  Multispeed, permanently lubricated, [permanent split capacitor] [ECM].

E. Water Circuit:

1. Refrigerant-to-Water Heat Exchanger:  [Coaxial] [Coil-in-shell] heat exchanger with [copper] [cupronickel] water tube with enhanced heat-transfer surfaces inside a steel shell; both shell and tube leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side.  Mount heat exchanger in unit on resilient rubber vibration isolators.

2. Risers:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 88, Type M (ASTM B 88M Type C)] copper pipe with hose and ball valve for system flushing.

F. Refrigerant-to-Air Coil:  Copper tubes with aluminum fins, leak tested to 450 psig (3102 kPa).

G. Refrigerant Circuit Components:

LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Obtaining the credit is not possible with R-22.

1. Sealed Refrigerant Circuit:  Charge with R-22 refrigerant.

Filter-dryer is not available from some manufacturers.

2. Filter-Dryer:  Factory installed to clean and dehydrate the refrigerant circuit.

3. Charging Connections:  Service fittings on suction and liquid for charging and testing.

4. Reversing Valve:  Pilot-operated sliding-type valve designed to be fail-safe in heating position with replaceable magnetic coil.

Options in first subparagraph below depend on unit size.  Verify with manufacturers.  Delete if these features are not specific selection criteria.

5. Compressor:  Hermetic [rotary] [scroll] compressor installed on vibration isolators housed in an acoustically treated enclosure with factory-installed safeties as follows:

a. Antirecycle timer.

b. High-pressure cutout.

c. Low-pressure cutout or loss of charge switch.

d. Internal thermal-overload protection.

6. Refrigerant Piping Materials:  ASTM B 743 copper tube with wrought-copper fittings and brazed joints.

7. Pipe Insulation:  Refrigerant minimum 3/8-inch- (10-mm-) thick, flexible elastomeric insulation on piping exposed to airflow through the unit.  Maximum 25/50 flame-spread/smoke-development indexes per ASTM E 84.

8. Refrigerant Metering Device:  Thermal expansion valve to allow specified operation with entering-water temperatures from [65 to 100 deg F (minus 18 to plus 38 deg C)] <Insert temperature range>.

Retain one of first two paragraphs below.  Verify availability of filter options in first paragraph with manufacturers.  Retain second paragraph if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

H. Filters:  Disposable, glass-fiber, flat type, [1 inch (25 mm)] <Insert thickness> thick, treated with adhesive, and having a minimum of 80 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 5 according to ASHRAE 52.2.

I. Filters:  Disposable, pleated type, [1 inch (25 mm)] <Insert thickness> thick and with a minimum of 90 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 7 according to ASHRAE 52.2.

J. Control equipment and sequence of operation are specified in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

Retain paragraph above and delete paragraph and subparagraphs below if controls are part of overall temperature-control system.

K. Controls:

1. Basic Unit Controls:

a. Low- and high-voltage protection.

b. Overcurrent protection for compressor and fan motor.

c. Random time delay, three to ten seconds, start on power up.

d. Time delay override for servicing.

e. Control voltage transformer.

Retain subparagraphs and associated subparagraphs below to suit Project; delete those not required.  Verify availability with manufacturer.

2. Thermostat:

a. Wall-Mounted Thermostat:

1) Heat-cool-off switch.

2) Fan on-auto switch.

3) [Manual] [Automatic] changeover.

4) [Concealed] [Exposed] temperature set point.

5) [Concealed] [Exposed] temperature indication.

6) Deg [F] [C] indication.

3. Terminal Controller:

a. Scheduled operation for occupied and unoccupied periods on seven-day clock with minimum four periods per day.

b. [Two] <Insert number>-hour unoccupied period override period.

c. Backup for volatile memory.

L. Electrical Connection:  Single electrical connection[ with fused disconnect].

If Project has more than one of this type of heat pump, delete paragraph and subparagraphs below and schedule heat pumps on Drawings.

M. Capacities and Characteristics:

1. Fan:

a. Airflow:  <Insert cfm (L/s).>

b. External Static Pressure:  <Insert inches wg (kPa).>

c. Fan Speed:  <Insert rpm.>

d. Maximum Brake Horsepower for Fan:  <Insert value.>

e. Motor Speed:  <Insert rpm.>

f. Motor Horsepower:  <Insert value.>

2. Water Supply:

a. Water Flow:  <Insert gpm (L/s).>

b. Pressure Loss:  <Insert feet wg (kPa).>

c. Entering-Water Temperature (Cooling):  <Insert deg F (deg C).>

d. Entering-Water Temperature (Heating):  <Insert deg F (deg C).>

e. Antifreeze Protection Chemical:  <Insert chemical name.>

f. Antifreeze Concentration:  <Insert percent.>

3. Cooling:

a. Total Capacity:  <Insert Btu/h (kW).>

b. Sensible Capacity:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

c. Minimum Energy-Efficiency Ratio (EER):  <Insert value.>

d. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

e. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

4. Heating:

a. Capacity:  <Insert Btu/h (kW).>

b. Entering-Air Temperature:  <Insert deg F (deg C).>

c. Air Temperature Rise:  <Insert deg F (deg C).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

d. Minimum Coefficient of Performance (COP):  <Insert value.>

5. Filters:

a. Face Area:  <Insert sq. ft. (sq. m).>

b. Maximum Face Velocity:  <Insert fpm (m/s).>

6. Electrical Characteristics for Single Connection:

a. Volts/Phase/Hertz:  <Insert values.>

b. FLA (Full-Load Amperes):  <Insert value.>

c. MCA (Maximum Circuit Amperes):  <Insert value.>

d. MOCP (Maximum Overcurrent Protection):  <Insert value.>

2.5 ROOFTOP WATER-SOURCE HEAT PUMPS

Rooftop water-source heat pumps are characterized by their approximate cooling capacity of from 3 to 35 tons (10.5 to 123 kW), direct- or belt-drive fan, and factory-installed mixing box including outdoor-air dampers and barometric or fan-assisted relief air modules.

Many optional features are available for this product and some are mutually exclusive.  Specify all those required for Project. Identify optional features for specific units in the schedule or on Drawings.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Addison Products Company.

2. Carrier Corporation.

3. ClimateMaster, Inc.

4. FHP Manufacturing Inc.

5. Mammoth Inc.

6. McQuay International.

7. Trane.

8. WaterFurnace International, Inc.

9. <Insert manufacturer's name.>

B. Description:  Packaged water-source heat pump with temperature controls; factory assembled, tested, and rated according to ARI-ISO-13256-1.

C. Cabinet and Chassis:  Galvanized-steel casing with the following features:

1. Water- and air-tight access panels for access and maintenance of internal components.

2. Knockouts for electrical and piping connections.

3. Flanged duct connections.

4. Cabinet Insulation:  Glass-fiber liner, 1 inch (25 mm) thick, complying with UL 181.

Retain option in first subparagraph below to comply with LEED-NC Prerequisite EQ 1.

5. Condensate Drainage:  [Plastic] [Galvanized-steel] [Stainless-steel] drain pan with condensate drain piping projecting to unit exterior[ and complying with ASHRAE 62.1-2004].

6. Exterior Finish:  Color selected by Architect from manufacturer's [standard] [custom] color selection.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

7. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain option for direct-drive or belt-drive fan in paragraph below, or retain all options if required and schedule on Drawings.

D. Indoor Fan:  Forward curved centrifugal, with [direct-drive, multispeed motor resiliently mounted in fan inlet] [or] [belt-drive, single-speed motor with adjustable motor sheave installed on an adjustable fan base resiliently mounted in cabinet].

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

2. Direct-Drive Fan Motor:  Multispeed, permanently lubricated, [permanent split capacitor] [ECM] motor.

E. Water Circuit:

1. Refrigerant-to-Water Heat Exchanger:

Retain one or more of first three options in subparagraph below.  Retain more than one to allow more than one component, or delete all to allow any of the three.

a. [Coaxial] [Coil-in-shell] [Shell-and-tube] heat exchanger with [copper] [cupronickel] water tube with enhanced heat-transfer surfaces inside a steel shell; both shell and tube leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side.  Factory mount heat exchanger in unit on resilient rubber vibration isolators.

Retain subparagraph above or below; retain both to allow either component.

b. Stainless-steel brazed plate heat exchanger leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side.  Factory mount heat exchanger in unit on resilient rubber vibration isolators.

Verify availability of water regulating valves and motorized water valves.

2. Water Regulating Valves:  Limit water flow through refrigerant-to-water heat exchanger, and control head pressure on compressor during cooling and heating.  Valves shall close when heat-pump compressor is not running.

3. Motorized Water Valve:  Stop water flow through the unit when compressor is off.

First paragraph below describes both heating/cooling and reheat coils.

F. Refrigerant-to-Air Coils:  Copper tubes with aluminum fins, leak tested to 450 psig (3102 kPa).

G. Refrigerant Circuit Components:

1. Sealed Refrigerant Circuit:  .  Minimum of 2 circuits required for units [10 tons (35 kW)] <Insert nominal capacity> and larger.  Intertwine circuits in refrigerant to air coil.

Retain one of two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second or third option in first subparagraph or retain second subparagraph to comply with Credit EA 4.

a. Charge with [R-22] [R-407C] [R-410A] refrigerant.

b. Charge with R-407C or R-410A refrigerant.

Filter-dryer is not available from some manufacturers.

2. Filter-Dryer:  Factory installed to clean and dehydrate each refrigerant circuit.

3. Charging Connections:  Service fittings on suction and liquid for charging and testing on each circuit.

4. Reversing Valve:  Pilot-operated sliding-type valve designed to be fail-safe in heating position with replaceable magnetic coil.

Options in first subparagraph below depend on unit size.  Verify with manufacturers.  Delete if these features are not specific selection criteria.

5. Compressor:  [Hermetic reciprocating] [Hermetic scroll] [Semihermetic reciprocating] compressor installed on vibration isolators housed in an acoustically treated enclosure with factory-installed safeties as follows:

a. Antirecycle timer.

b. High-pressure cutout.

c. Low-pressure cutout or loss of charge switch.

d. Internal thermal-overload protection.

Retain first subparagraph below for compressor safety switches.

e. Freezestat to stop compressor if water-loop temperature in refrigerant-to-water heat exchanger falls below [35 deg F (2 deg C)] <Insert temperature>.

f. Condensate overflow switch to stop compressor with high condensate level in condensate drain pan.

6. Refrigerant Piping Materials:  ASTM B 743 copper tube with wrought-copper fittings and brazed joints.

7. Pipe Insulation:  Refrigerant minimum 3/8-inch- (10-mm-) thick, flexible elastomeric insulation on piping exposed to airflow through the unit.  Maximum 25/50 flame-spread/smoke-development indexes per ASTM E 84.

8. Refrigerant Metering Device:  Capillary tube.

Retain subparagraph above or below.

9. Refrigerant Metering Device:  Thermal expansion valve to allow specified operation with entering-water temperatures from 25 to 125 deg F (minus 4 to plus 52 deg C).

Retain subparagraph below for hot-gas reheat.

10. Hot-Gas Reheat Valve:  Pilot-operated sliding-type valve with replaceable magnetic coil.

Electric heating coil is an optional feature for "boilerless" system.  Some features are mutually exclusive.  Verify availability with manufacturer.  Temperature set point is adjustable and will vary with system type.

H. Electric Heating Coil:  Helix-wound, nickel-chromium wire-heating elements in ceramic insulators mounted on steel supports.  Energize on call for heating when entering-water-loop temperature is less than [25 deg F (minus 4 deg C)] [40 deg F (5 deg C)] [60 deg F (15 deg C)] <Insert temperature>.

Retain paragraph below for hot-gas reheat for humidity control; water regulating valves may be required.

I. Hot-Gas Reheat:  Reheat valve diverts refrigerant hot gas to reheat coil when remote humidistat calls for dehumidification.

Retain first paragraph below for hot-gas bypass for capacity control; water regulating valves may be required.

J. Hot-Gas Bypass:  Include constant pressure expansion valve, solenoid valve, and controls to maintain continuous refrigeration system operation at 10 percent of full load on lead compressor.

ASHRAE/IESNA 90.1-2004 sets requirements for dampers.  If applying for LEED certification, retain second option in paragraph below to comply with ASHRAE/IESNA 90.1-2004.

K. Outdoor-Air Damper:  Linked damper blades, for minimum 25 percent outdoor air, with [manual slide and] [fully modulating, spring-return damper motor and] hood.

Retain paragraph above for limited outdoor air or paragraph and subparagraphs below for air-side economizer.

L. Air-Side Economizer:  Return-, relief-, and outdoor-air dampers with neoprene seals and with weather-resistant hood.

1. Damper Motors:  Fully modulating spring return with adjustable minimum position potentiometer.

2. Temperature Control:  Microprocessor-based controller using [outdoor-air, mixed-air and outdoor-air temperature] [outdoor-air, mixed-air temperature and selects between outdoor-air and return-air enthalpy] to adjust mixing dampers with water-loop entering temperature greater than [70 deg F (21 deg C)] <Insert temperature>.  Delay opening outdoor-air damper to minimum position until room thermostat is satisfied at room set-point temperature.

Retain first subparagraph below for carbon dioxide sensor to reset minimum outdoor-air intake rate.

3. Ventilation Control:  Provide carbon dioxide sensor to reset minimum outdoor-air intake rate to minimum [10 percent] <Insert percent> to maintain maximum [800 ppm] <Insert concentration> concentration of carbon dioxide in return air.

4. Relief Damper:  Gravity-actuated damper with bird screen and hood.

Retain subparagraph above or below for optional air-side economizer relief.

5. Powered Relief:  Direct-drive propeller fan with PSC motor, normally closed motorized damper, and hood.  Operate fan with building pressure greater than [0.05-inch wg (12.4 Pa)] <Insert pressure>.

Retain one of two paragraphs below.  Verify availability of filter options in first paragraph with manufacturers.  Retain second paragraph if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

M. Filters:  Disposable, glass-fiber, flat type, [1 inch (25 mm)] [2 inches (50 mm)] <Insert thickness> thick, treated with adhesive, and having a minimum of 80 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 5 according to ASHRAE 52.2.

N. Filters:  Disposable, pleated type, [1 inch (25 mm)] [2 inches (50 mm)] <Insert thickness> thick and with a minimum of 90 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 7 according to ASHRAE 52.2.

Revise curb height in paragraph below to manufacturer's standard or to required height for units specified.

O. Roof Curb:  Steel, with corrosion-protection coating, gasketing, and factory-installed wood nailer; complying with NRCA standards; minimum height of [14 inches (355 mm)] [24 inches (600 mm)] <Insert height>.

Revise curb height in paragraph below to manufacturer's standard or to required height for units specified.

P. Horizontal Discharge Roof Curb:  Steel, with corrosion-protection coating, gasketing, and factory-installed wood nailer, and configured to convert from downflow to horizontal airflow; complying with NRCA standards; minimum height of [26 inches (660 mm)] [30 inches (760 mm)] [37 inches (940 mm)] [41 inches (1040 mm)] <Insert height>.

Revise static deflection in first paragraph below to suit Project.

Q. Isolation Curb:  Rigid upper and lower steel structure with vibration isolation springs having [2-inch (50-mm)] <Insert deflection> static deflection and vertical and horizontal restraints; with elastomeric waterproof membrane.

R. Control equipment and sequence of operation are specified in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

Retain paragraph above and delete paragraph and subparagraphs below if controls are part of overall temperature-control system.

S. Controls:

1. Basic Unit Controls:

a. Low- and high-voltage protection.

b. Overcurrent protection for compressor and fan motor.

c. Random time delay, three to ten seconds, start on power-up.

d. Time delay override for servicing.

e. Control voltage transformer.

Retain subparagraphs and associated subparagraphs below to suit Project; delete those not required.  Verify availability with manufacturer.

2. Thermostat:

a. Wall-Mounted Thermostat:

1) Heat-cool-off switch.

2) Fan on-auto switch.

3) [Manual] [Automatic] changeover.

4) [Concealed] [Exposed] temperature set point.

5) [Concealed] [Exposed] temperature indication.

6) Deg [F] [C] indication.

7) [One] [Two]-stage heating.

8) [One] [Two]-stage cooling.

b. Wall-Mounted Humidistat:  [Concealed] [Exposed].

1) Temperature set point.

2) Temperature indication.

c. Wall-mounted temperature sensor.

d. Unoccupied period override push button.

e. LED to indicate fault condition at heat pump.

f. Data entry and access port.

1) Input data include room temperature and humidity set points for occupied and unoccupied periods.

2) Output data include room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

3. Terminal Controller:

a. Scheduled operation for occupied and unoccupied periods on [7] [365]-day clock with minimum 4 programmable periods per day.

b. [Two] <Insert number>-hour unoccupied period override period.

c. Remote control panel to contain programmable timer and LED for fault condition.

d. Compressor disable relay to stop compressor operation for demand limiting or switch to unoccupied operation.

e. Automatic restart after five minutes if fault clears.  Lockout after three attempts to restart following fault.  Indicate fault for service technician.

f. Return-air temperature high-limit (firestat).  Stop unit on high temperature.

g. Smoke alarm with smoke detector installed in [supply] [return] [supply and return] air.  Stop unit on smoke detection.

h. Backup for volatile memory.

i. Differential pressure switch to indicate fan status.  Fan failure alarm.

j. Differential pressure switch to indicate filter status.  Dirty filter alarm.

4. BAS interface requirements as further described in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

a. Interface relay for scheduled operation.

b. Interface relay to provide indication of fault at central workstation.

c. Provide [BAC-net] [or] [Lonworks] interface for central BAS workstation for the following functions:

1) Set-point adjustment for set points identified in this Section.

2) Start/stop and operating status of heat-pump unit.

3) Data inquiry to include supply air, room air temperature and humidity, and entering-water temperature.

4) Occupied and unoccupied schedules.

T. Electrical Connection:  Single electrical connection[ with fused disconnect].

If Project has more than one of this type of heat pump, delete paragraph and subparagraphs below and schedule heat pumps on Drawings.

U. Capacities and Characteristics:

1. Fan:

a. Airflow:  <Insert cfm (L/s).>

b. External Static Pressure:  <Insert inches wg (kPa).>

c. Fan Speed:  <Insert rpm.>

d. Maximum Brake Horsepower for Fan:  <Insert value.>

e. Motor Speed:  <Insert rpm.>

f. Motor Horsepower:  <Insert value.>

2. Water Supply:

a. Water Flow:  <Insert gpm (L/s).>

b. Pressure Loss:  <Insert feet wg (kPa).>

c. Entering-Water Temperature (Cooling):  <Insert deg F (deg C).>

d. Entering-Water Temperature (Heating):  <Insert deg F (deg C).>

e. Antifreeze Protection Chemical:  <Insert chemical name.>

f. Antifreeze Concentration:  <Insert percent.>

3. Cooling:

a. Total Capacity:  <Insert Btu/h (kW).>

b. Sensible Capacity:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

c. Minimum Energy-Efficiency Ratio (EER):  <Insert value.>

d. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

e. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

4. Heating:

a. Capacity:  <Insert Btu/h (kW).>

b. Entering-Air Temperature:  <Insert deg F (deg C).>

c. Air Temperature Rise:  <Insert deg F (deg C).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

d. Minimum Coefficient of Performance (COP):  <Insert value.>

5. Electric Heating Coil (Optional Feature):

a. Capacity:  <Insert Btu/h (kW).>

b. Number of Steps:  <Insert number.>

6. Water-Side Economizer (Optional Feature):

a. Total Cooling Capacity:  <Insert Btu/h (kW).>

b. Sensible Cooling Capacity:  <Insert Btu/h (kW).>

c. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

d. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

e. Entering-Water Temperature:  <Insert deg F (deg C).>

f. Water Flow:  <Insert gpm (L/s).>

g. Pressure Loss:  <Insert feet wg (kPa).>

7. Filters:

a. Face Area:  <Insert sq. ft. (sq. m).>

b. Maximum Face Velocity:  <Insert fpm (m/s).>

8. Electrical Characteristics for Single Connection:

a. Volts/Phase/Hertz:  <Insert values.>

b. FLA (Full-Load Amperes):  <Insert value.>

c. MCA (Maximum Circuit Amperes):  <Insert value.>

d. MOCP (Maximum Overcurrent Protection):  <Insert value.>

2.6 EXPOSED, CONSOLE WATER-SOURCE HEAT PUMPS

Exposed, console water-source heat pumps are distinguished from other types by their approximate cooling capacity of from 1/2 to 2 tons (1.7 to 7 kW), finished cabinet exposed in the occupied space, hot-gas bypass for capacity control, optional motorized outdoor-air damper or economizer cycle, and direct-drive fans.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Carrier Corporation.

2. ClimateMaster, Inc.

3. FHP Manufacturing Inc.

4. Hydro-Temp Corporation, Inc.

5. Mammoth Inc.

6. McQuay International.

7. Trane.

8. WaterFurnace International, Inc.

9. <Insert manufacturer's name.>

B. Description:  Packaged water-source heat pump with temperature controls; factory assembled, tested, and rated according to ARI-ISO-13256-1.

C. Cabinet and Chassis:  Manufacturer's [standard] [low] [standard- and low]-height, [flat] [sloped]-top, [extended ]galvanized-steel casing with the following features:

1. Access panel for access and maintenance of internal components.

2. Knockouts for electrical and piping connections.

3. Cabinet Insulation:  Glass-fiber liner, 1/2 inch (13 mm) thick, complying with UL 181.

Retain option in first subparagraph below to comply with LEED-NC Prerequisite EQ 1.

4. Condensate Drainage:  Plastic or stainless-steel drain pan with condensate drain piping projecting to unit exterior[ and complying with ASHRAE 62.1-2004].

5. Discharge Grille:  Steel, aluminum, or plastic grille for adjustable discharge air pattern.

6. Color:  Selected by Architect from manufacturer's [standard] [custom] color selection.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

7. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Retain subparagraph and associated subparagraphs below for sound attenuation package.  Verify availability of method selected with specified manufacturer.

8. Sound Attenuation Package:  Provide one or more of the following.

a. Minimum 0.598-inch- (1.5-mm-) thick compressor enclosure and front panel.  Minimum 0.0937-inch (2.38-mm) thick foam gasket around the compressor and perimeter of end panel.

b. <Insert method.>

D. Fan:  Direct driven, centrifugal, with multispeed motor mounted on a removable fan-motor board.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

2. Motor:  Multispeed, permanently lubricated, [permanent split capacitor] [ECM].

E. Water Circuit:

1. Refrigerant-to-Water Heat Exchanger:  Coaxial heat exchanger with [copper] [cupronickel] water tube with enhanced heat-transfer surfaces inside a steel shell; both shell and tube leak tested to 450 psig (3102 kPa) for refrigerant side and 400 psig (2758 kPa) for water side.  Mount heat exchanger in unit on resilient rubber vibration isolators.

Subparagraph below is a feature with some manufacturers.

2. Water Regulating Valves:  Limit water flow through refrigerant-to-water heat exchanger and control head pressure on compressor during cooling and heating.  Valves shall close when heat-pump compressor is not running.

First paragraph below describes both heating/cooling and hot-gas reheat coils.

F. Refrigerant-to-Air Coils:  Copper tubes with aluminum fins, leak tested to 450 psig (3102 kPa).

G. Refrigerant Circuit Components:

Retain one of two subparagraphs below to require a specific refrigerant type; delete both if any refrigerant type is acceptable.  LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Retain second or third option in first subparagraph or retain second subparagraph to comply with Credit EA 4.

1. Sealed Refrigerant Circuit:  Charge with [R-22] [R-407C] [R-410A] refrigerant.

2. Sealed Refrigerant Circuit:  Charge with R-407C or R-410A refrigerant.

Filter-dryer is not available from some manufacturers.

3. Filter-Dryer:  Factory installed to clean and dehydrate the refrigerant circuit.

4. Charging Connections:  Service fittings on suction and liquid for charging and testing.

5. Reversing Valve:  Pilot-operated sliding-type valve designed to be fail-safe in heating position with replaceable magnetic coil.

6. Compressor:  Hermetic rotary compressor installed on vibration isolators housed in an acoustically treated enclosure with factory-installed safeties as follows:

a. Antirecycle timer.

b. High-pressure cutout.

c. Low-pressure cutout or loss of charge switch.

d. Internal thermal-overload protection.

Retain first subparagraph below for compressor safety switches.

e. Freezestat to stop compressor if water-loop temperature in refrigerant-to-water heat exchanger falls below [35 deg F (2 deg C)] <Insert temperature>.

f. Condensate overflow switch to stop compressor with high condensate level in condensate drain pan.

7. Refrigerant Piping Materials:  ASTM B 743 copper tube with wrought-copper fittings and brazed joints.

8. Pipe Insulation:  Refrigerant minimum 3/8-inch- (10-mm-) thick, flexible elastomeric insulation on piping exposed to airflow through the unit.  Maximum 25/50 flame-spread/smoke-development indexes per ASTM E 84.

9. Refrigerant Metering Device:

a. Capillary tube.

Retain subparagraph above or below.

b. Thermal expansion valve to allow specified operation with entering-water temperatures from [25 to 125 deg F (minus 4 to 52 deg C)] <Insert temperature range>.

Retain subparagraph below for hot-gas reheat.

10. Hot-Gas Reheat Valve:  Pilot-operated sliding-type valve with replaceable magnetic coil.

Electric heating coil is an optional feature for "boilerless" system.  Some features are mutually exclusive.  Verify availability with manufacturer.

H. Electric Heating Coil:  Energized on call for heating when entering-water-loop temperature is less than [60 deg F (15deg C)] <Insert temperature>.

Retain paragraph below for hot-gas reheat for humidity control; water regulating valves may be required.

I. Hot-Gas Reheat:  Reheat valve diverts refrigerant hot gas to reheat coil when [remote] [unit-mounted] humidistat calls for dehumidification.

Retain paragraph below for outdoor-air damper.

ASHRAE/IESNA 90.1-2004 sets requirements for dampers.  If applying for LEED certification, retain second option in paragraph below to comply with ASHRAE/IESNA 90.1-2004.

J. Outdoor-Air Damper:  Two-position, [manual] [motorized] outdoor-air damper for fixed minimum intake up to 25 percent of fan capacity.

Retain one of first two paragraphs below.  Verify availability of filter options in first paragraph with manufacturers.  Retain second paragraph if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

K. Filters:  Disposable, glass-fiber, flat type, [1 inch (25 mm)] <Insert thickness> thick, treated with adhesive, and having a minimum of 80 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 5 according to ASHRAE 52.2.

L. Filters:  Disposable, pleated type, [1 inch (25 mm)] <Insert thickness> thick and with a minimum of 90 percent arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value of 7 according to ASHRAE 52.2.

M. Control equipment and sequence of operation are specified in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

Retain paragraph above and delete paragraph and subparagraphs below if controls are part of overall temperature-control system.

N. Controls:

1. Basic Unit Controls:

a. Low- and high-voltage protection.

b. Overcurrent protection for compressor and fan motor.

c. Random time delay, three to ten seconds, start on power up.

d. Time delay override for servicing.

e. Control voltage transformer.

Retain subparagraphs and associated subparagraphs below to suit Project; delete those not required.  Verify availability with manufacturers.

2. Thermostat:

a. [Wall] [Unit]-Mounted Thermostat:

1) Heat-cool-off switch.

2) Fan on-auto switch.

3) [Manual] [Automatic] changeover.

4) [Concealed] [Exposed] temperature set point.

5) [Concealed] [Exposed] temperature indication.

6) Deg [F] [C] indication.

b. [Wall] [Unit]-Mounted Humidistat:  [Concealed] [Exposed].

1) Temperature set point.

2) Temperature indication.

c. [Wall] [Unit]-mounted temperature sensor.

d. Unoccupied period override push button.

e. LED to indicate fault condition at heat pump.

f. Data entry and access port.

1) Input data include room temperature and humidity set points for occupied and unoccupied periods.

2) Output data include room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

3. Terminal Controller:

a. Scheduled operation for occupied and unoccupied periods on [7] [365]-day clock with minimum 4 programmable periods per day.

b. [Two] <Insert number>-hour unoccupied period override period.

c. Compressor disable relay to stop compressor operation for demand limiting or switch to unoccupied operation.

d. Automatic restart after five minutes if fault clears.  Lockout after three attempts to restart following fault.  Indicate fault for service technician.

e. Backup for volatile memory.

Differential pressure switches for statuses of fan and filter are not available from some manufacturers.

f. Differential pressure switch to indicate fan status.  Fan failure alarm.

g. Differential pressure switch to indicate filter status.  Dirty filter alarm.

4. BAS interface requirements as further described in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

a. Interface relay for scheduled operation.

b. Interface relay to provide indication of fault at central workstation.

c. Provide [BAC-net] [or] [Lonworks] interface for central BAS workstation for the following functions:

1) Set-point adjustment for set points identified in this Section.

2) Start/stop and operating status of heat-pump unit.

3) Data inquiry to include supply air, room air temperature and humidity, and entering-water temperature.

4) Occupied and unoccupied schedules.

O. Electrical Connection:  Single electrical connection[ with fused disconnect].

If Project has more than one of this type of heat pump, delete paragraph and subparagraphs below and schedule heat pumps on Drawings.

P. Capacities and Characteristics:

1. Fan:

a. Airflow:  <Insert cfm (L/s).>

b. External Static Pressure:  <Insert inches wg (kPa).>

c. Fan Speed:  <Insert rpm.>

d. Maximum Brake Horsepower for Fan:  <Insert value.>

e. Motor Speed:  <Insert rpm.>

f. Motor Horsepower:  <Insert value.>

2. Water Supply:

a. Water Flow:  <Insert gpm (L/s).>

b. Pressure Loss:  <Insert feet wg (kPa).>

c. Entering-Water Temperature (Cooling):  <Insert deg F (deg C).>

d. Entering-Water Temperature (Heating):  <Insert deg F (deg C).>

e. Antifreeze Protection Chemical:  <Insert chemical name.>

f. Antifreeze Concentration:  <Insert percent.>

3. Cooling:

a. Total Capacity:  <Insert Btu/h (kW).>

b. Sensible Capacity:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

c. Minimum Energy-Efficiency Ratio (EER):  <Insert value.>

d. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

e. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

4. Heating:

a. Capacity:  <Insert Btu/h (kW).>

b. Entering-Air Temperature:  <Insert deg F (deg C).>

c. Air Temperature Rise:  <Insert deg F (deg C).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

d. Minimum Coefficient of Performance (COP):  <Insert value.>

5. Electric Heating Coil (Optional Feature):

a. Capacity:  <Insert Btu/h (kW).>

b. Number of Steps:  <Insert number.>

6. Filters:

a. Face Area:  <Insert sq. ft. (sq. m).>

b. Maximum Face Velocity:  <Insert fpm (m/s).>

7. Electrical Characteristics for Single Connection:

a. Volts/Phase/Hertz:  <Insert values.>

b. FLA (Full-Load Amperes):  <Insert value.>

c. MCA (Maximum Circuit Amperes):  <Insert value.>

d. MOCP (Maximum Overcurrent Protection):  <Insert value.>

2.7 UNIT VENTILATOR WATER-SOURCE HEAT PUMPS

Unit ventilator water-source heat pumps are distinguished from other types by their approximate cooling capacity of from 2 to 3.75 tons (7 to 13.2 kW); finished cabinet exposed in the occupied space; motorized outdoor-air damper controlled according to Cycle II (as defined in the "Control" Article of ASHRAE's "HVAC Systems and Equipment" handbook, Ch. 31), or economizer cycle; and direct-drive fans.

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

A. [Available ]Manufacturers:

1. Trane.

2. <Insert manufacturer's name.>

B. Description:  Packaged water-source heat pump with temperature controls; factory assembled, tested, and rated according to ARI-ISO-13256-1.

C. Cabinet and Chassis:  Manufacturer's standard-height, [flat] [sloped]-top, [extended] galvanized-steel casing with the following features:

1. Access panel for access and maintenance of internal components.

2. Knockouts for electrical and piping connections.

3. Cabinet Insulation:  Glass-fiber liner, 1 inch (25 mm) thick, complying with UL 181.

Retain option in first subparagraph below to comply with LEED-NC Prerequisite EQ 1.

4. Condensate Drainage:  Plastic or stainless-steel drain pan with condensate drain piping projecting to unit exterior[ and complying with ASHRAE 62.1-2004].

5. Discharge Grille:  Extruded-aluminum grille for adjustable discharge air pattern.

6. Wall Sleeve:  Galvanized steel, painted same as cabinet.

7. Color:  Selected by Architect from manufacturer's [standard] [custom] color selection.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

8. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

D. Fan:  Direct driven, centrifugal, with multispeed motor mounted on a removable fan-motor board.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

E. Water Circuit:

1. Refrigerant-to-Water Heat Exchanger:  Coil-in-shell type heat exchanger with [copper] [cupronickel] water tube with enhanced heat-transfer surfaces inside a steel shell; both shell and tube leak tested to 450 psig (3102 kPa) on refrigerant side and 400 psig (2758 kPa) on water side.  Mount heat exchanger in unit on resilient rubber vibration isolators.

F. Refrigerant-to-Air Coil:  Copper tubes with aluminum fins, leak tested to 450 psig (3102 kPa).

G. Refrigerant Circuit Components:

LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.  Obtaining the credit is not possible with R-22.

1. Sealed Refrigerant Circuit:  Charge with R-22 refrigerant.

Filter-dryer is not available from some manufacturers.

2. Filter-Dryer:  Factory installed to clean and dehydrate the refrigerant circuit.

3. Charging Connections:  Service fittings on suction and liquid for charging and testing.

4. Reversing Valve:  Pilot-operated sliding-type valve designed to be fail-safe in heating position with replaceable magnetic coil.

5. Compressor:  Hermetic scroll compressor installed on vibration isolators housed in an acoustically treated enclosure with factory-installed safeties as follows:

a. Antirecycle timer.

b. High-pressure cutout.

c. Low-pressure cutout or loss of charge switch.

d. Internal thermal-overload protection.

6. Refrigerant Piping Materials:  ASTM B 743 copper tube with wrought-copper fittings and brazed joints.

7. Pipe Insulation:  Refrigerant minimum 3/8-inch- (10-mm-) thick, flexible elastomeric insulation on piping exposed to airflow through the unit.  Maximum 25/50 flame-spread/smoke-development indexes per ASTM E 84.

8. Refrigerant Metering Device:  Thermal expansion valve to allow specified operation with entering-water temperatures from [65 to 100 deg F (minus 18 to 38 deg C)] <Insert temperature range>.

H. Outdoor-Air Damper:  Motorized outdoor-air damper for fixed minimum intake, and maximum 100 percent of fan capacity.  Provide electronic damper actuators with microprocessor controller to permit air-side economizer operation with minimum 70 deg F (21 deg C) water-loop inlet temperature.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

I. Filters:  Disposable glass-fiber type, 1 inch (25 mm) thick.  Glass-fiber filter treated with adhesive shall have minimum 80 percent arrestance according to ASHRAE 52.1, and a minimum efficiency reporting value (MERV) of 6 according to ASHRAE 52.2.

J. Control equipment and sequence of operation are specified in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

Retain paragraph above and delete paragraph and subparagraphs below if controls are part of overall temperature-control system.

K. Controls:

1. Basic Unit Controls:

a. Low- and high-voltage protection.

b. Overcurrent protection for compressor and fan motor.

c. Random time delay, three to ten seconds, start on power up.

d. Time delay override for servicing.

e. Control voltage transformer.

Retain subparagraphs and associated subparagraphs below to suit Project; delete those not required.  Verify availability with manufacturers.

2. Thermostat:

a. [Wall] [Unit]-Mounted Thermostat:

1) Heat-cool-off switch.

2) Fan on-auto switch.

3) [Manual] [Automatic] changeover.

4) [Concealed] [Exposed] temperature set point.

5) [Concealed] [Exposed] temperature indication.

6) Deg [F] [C] indication.

b. [Wall] [Unit]-mounted temperature sensor.

c. Unoccupied period override push button.

d. LED to indicate fault condition at heat pump.

e. Data entry and access port.

1) Input data include room temperature and humidity set points for occupied and unoccupied periods.

2) Output data include room temperature and humidity, supply-air temperature, entering-water temperature, operating mode, and status.

3. Terminal Controller:

a. Scheduled operation for occupied and unoccupied periods on seven-day clock with minimum four programmable periods per day.

b. [Two] <Insert number>-hour unoccupied period override period.

c. Compressor disable relay to stop compressor operation for demand limiting or switch to unoccupied operation.

d. Automatic restart after five minutes if fault clears.  Lockout after three attempts to restart following fault.  Indicate fault for service technician.

e. Backup for volatile memory.

f. Differential pressure switch to indicate fan status.  Fan failure alarm.

g. Differential pressure switch to indicate filter status.  Dirty filter alarm.

4. BAS interface requirements as further described in Division 23 Sections "Instrumentation and Controls for HVAC" and "Sequence of Operations for HVAC Controls."

a. Interface relay for scheduled operation.

b. Interface relay to provide indication of fault at central workstation.

c. Provide [BAC-net] [or] [Lonworks] interface for central BAS workstation for the following functions:

1) Set-point adjustment for set points identified in this Section.

2) Start/stop and operating status of heat-pump unit.

3) Data inquiry to include supply air, room air temperature and humidity, and entering-water temperature.

4) Occupied and unoccupied schedules.

L. Electrical Connection:  Single electrical connection[ with fused disconnect].

If Project has more than one of this type of heat pump, delete paragraph and subparagraphs below and schedule heat pumps on Drawings.

M. Capacities and Characteristics:

1. Fan:

a. Airflow:  <Insert cfm (L/s).>

b. External Static Pressure:  <Insert inches wg (kPa).>

c. Fan Speed:  <Insert rpm.>

d. Maximum Brake Horsepower for Fan:  <Insert value.>

e. Motor Speed:  <Insert rpm.>

f. Motor Horsepower:  <Insert value.>

2. Water Supply:

a. Water Flow:  <Insert gpm (L/s).>

b. Pressure Loss:  <Insert feet wg (kPa).>

c. Entering-Water Temperature (Cooling):  <Insert deg F (deg C).>

d. Entering-Water Temperature (Heating):  <Insert deg F (deg C).>

e. Antifreeze Protection Chemical:  <Insert chemical name.>

f. Antifreeze Concentration:  <Insert percent.>

3. Cooling:

a. Total Capacity:  <Insert Btu/h (kW).>

b. Sensible Capacity:  <Insert Btu/h (kW).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

c. Minimum Energy-Efficiency Ratio (EER):  <Insert value.>

d. Entering-Air Temperature Dry Bulb:  <Insert deg F (deg C).>

e. Entering-Air Temperature Wet Bulb:  <Insert deg F (deg C).>

4. Heating:

a. Capacity:  <Insert Btu/h (kW).>

b. Entering-Air Temperature:  <Insert deg F (deg C).>

c. Air Temperature Rise:  <Insert deg F (deg C).>

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004, Table 6.8.1B, "Electrically Operated Unitary and Applied Heat Pumps ? Minimum Efficiency Requirements."

d. Minimum Coefficient of Performance (COP):  <Insert value.>

5. Filters:

a. Face Area:  <Insert sq. ft. (sq. m).>

b. Maximum Face Velocity:  <Insert fpm (m/s).>

6. Electrical Characteristics for Single Connection:

a. Volts/Phase/Hertz:  <Insert values.>

b. FLA (Full-Load Amperes):  <Insert value.>

c. MCA (Maximum Circuit Amperes):  <Insert value.>

d. MOCP (Maximum Overcurrent Protection):  <Insert value.>

2.8 HOSE KITS

Retain this Article for hose kits furnished with each water-source heat pump.  Edit for size and components.

A. General:  Hose kits shall be designed for minimum 400 psig (2758 kPa) working pressure, and operating temperatures from 33 to 211 deg F (0.5 to 99 deg C).  Tag hose kits to equipment designations.

B. Hose:  Length [24 inches (600 mm)] [36 inches (900 mm)] <Insert dimension>.  Minimum diameter, equal to water-source heat-pump connection size.

C. Isolation Valves:  Two-piece bronze-body ball valves with stainless-steel ball and stem and galvanized-steel lever handle.  Provide valve for supply and return.  If balancing device is combination shutoff type with memory stop, the isolation valve may be omitted on the return.

D. Strainer:  Y-type with blowdown valve in supply connection.

E. Balancing Device:  Mount in return connection.  Include meter ports to allow flow measurement with differential pressure gage.

Retain one of three subparagraphs below.  Retain more than one if different balancing valves are used on different types of heat-pumps.

1. Automatic balancing valve, factory set to operate within 10 percent of design flow rate over a 40:1 differential pressure range of 2 to 80 psig (13.8 to 552 kPa).

2. Manual, calibrated-orifice balancing valve.

3. Manual, venturi-type balancing valve.

2.9 PUMP MODULE

Retain this Article for individual heat pumps that stand alone from a central circulating water loop.  Values in paragraph below are examples only; verify actual values with specified manufacturer.

A. Minimum [1/6-hp] <Insert value>, 230-V, single-phase pump rated to move at least [16 gpm (1 L/s)] <Insert flow> at [20-feet wg (59-kPa)] <Insert head> head pressure.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

1. General requirements for motors are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

B. Include pump module hose kit with thread to barb fittings, hose, and hose clamps.

C. Three-way brass shut-off/flushing/purging valve.

D. Include controls to operate pump as required to maintain room temperature and ventilation set points.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of water-source heat pumps.

B. Examine roughing-in for piping and electric installations for water-source heat pumps to verify actual locations of piping connections and electrical conduit before installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain two paragraphs and associated subparagraphs below for floor-mounted, water-source heat pumps.

A. Concrete Bases:  Install floor mounting units on 4-inch- (100-mm-) high concrete bases.  See Division 23 Section "Common Work Results for HVAC" for concrete base materials and fabrication requirements.

B. Mount water-source heat pumps on concrete base with vibration isolators[ and seismic restraints].[ Vibration isolators are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."]

Retain one of two subparagraphs below or revise to suit Project and equipment requirements.  Refer to Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" for other types and applications of vibration-control devices.

1. Units with Internally Isolated Fans and Compressors:  Support on concrete bases using neoprene pads with minimum 0.125-inch (3.17-mm) static deflection.  Secure units to anchor bolts installed in concrete bases.

2. Floor-Mounted Units:  Support on concrete bases using housed-spring isolators with minimum [1-inch (25-mm)] <Insert deflection> static deflection.  Secure units to anchor bolts installed in concrete bases.

Retain paragraph below for suspended water-source heat pumps.

C. Suspend water-source heat pumps from structure with threaded steel rods and[ minimum 0.25-inch (6.35-mm) static deflection rubber-in-shear] vibration isolators[ and seismic restraints].[ Vibration isolators are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."]

Retain paragraph below if curbs are furnished with rooftop water-source heat pump; delete if unit is installed on field-fabricated curbs or pilings.

D. Curb Support:  Install roof curb on roof structure, level and secure, according to [NRCA's "Low-Slope Membrane Roofing Construction Details Manual," Illustration "Raised Curb Detail for Rooftop Air Handling Units and Ducts."] [ARI Guideline B.] Install and secure rooftop water-source heat pumps on curbs and coordinate roof penetrations and flashing with roof construction.[ Secure units to curb support with anchor bolts.]

Retain paragraph above or below for appropriate mounting method and edit to suit Project.  Anchor bolts may be required for seismic restraint.

E. Unit Support:  Install unit level on structural [curbs] [pilings].  Coordinate wall penetrations and flashing with wall construction.[ Secure units to structural support with anchor bolts.]

Retain paragraph below for units mounted on isolation curbs.

F. Isolation Curb Support:  Install units on isolation curbs according to [NRCA's "Low-Slope Membrane Roofing Construction Details Manual," Illustration "Raised Curb Detail for Rooftop Air Handling Units and Ducts."] [ARI Guideline B.]

Retain first paragraph below for units mounted on restrained isolation roof-curb rails specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" instead of vibration isolation curb specified in Part 2.

G. Install restrained vibration isolation roof-curb rails on roof structure according to [NRCA's "Low-Slope Membrane Roofing Construction Details Manual," Illustration "Raised Curb Detail for Rooftop Air Handling Units and Ducts."] [ARI Guideline B.] Install and secure rooftop water-source heat pumps on rails and coordinate roof penetrations and flashing with roof construction.  Restrained isolation roof-curb rails are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

H. Install wall-mounting thermostats, humidistats, and switch controls in electrical outlet boxes at heights to match lighting controls or as required in Division 23 Section "Instrumentation and Control for HVAC."

3.3 CONNECTIONS

Coordinate requirements for piping installation and specialty arrangements with schematics on Drawings and with requirements specified in hydronic piping and steam and condensate piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of piping, fittings, and specialties.  Specific connection requirements are as follows:

1. Connect supply and return hydronic piping to heat pump with [unions and shutoff valves] [hose kits].

2. Connect heat-pump condensate drain pan to indirect waste connection with condensate trap of adequate depth to seal against the pressure of fan.  Install cleanouts in piping at changes of direction.

Coordinate duct installation requirements with schematics on Drawings and with requirements specified for duct systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

B. Duct installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of ducts.  Specific connection requirements are as follows:

1. Connect supply and return ducts to water-source heat pumps with flexible duct connectors specified in Division 23 Section "Air Duct Accessories."

Retain subparagraphs below for rooftop water-source heat pumps.  Edit to describe required Project conditions.

2. Install ducts to termination in roof curb.

3. Remove roof decking only as required for passage of ducts.  Do not cut out decking under entire roof curb.

4. Terminate return-air duct through roof structure and insulate space between roof and bottom of unit with 2-inch- (50-mm-) thick, acoustic duct liner.

5. Install normal-weight, 3000 psi (20.7 MPa), compressive-strength (28-day) concrete mix inside roof curb, [4 inches (100 mm)] <Insert thickness> thick.  Concrete, formwork, and reinforcement are specified in Division 03.

C. Install electrical devices furnished by manufacturer but not specified to be factory mounted.

D. Install piping adjacent to machine to allow service and maintenance.

E. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

F. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

A. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

B. Perform the following field tests and inspections and prepare test reports:

1. After installing water-source heat pumps and after electrical circuitry has been energized, test units for compliance with requirements.

2. Inspect for and remove shipping bolts, blocks, and tie-down straps.

3. Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

C. Remove and replace malfunctioning units and retest as specified above.

3.5 STARTUP SERVICE

Delete first paragraph below if factory-authorized service representative is not required.

A. Engage a factory-authorized service representative to perform startup service.

B. Complete installation and startup checks according to manufacturer's written instructions and do the following:

1. Inspect for visible damage to unit casing.

2. Inspect for visible damage to compressor, coils, and fans.

3. Inspect internal insulation.

4. Verify that labels are clearly visible.

5. Verify that clearances have been provided for servicing.

6. Verify that controls are connected and operable.

7. Verify that filters are installed.

8. Adjust vibration isolators.

9. Inspect operation of barometric dampers.

10. Verify bearing lubrication on fan.

11. Inspect fan-wheel rotation for movement in correct direction without vibration and binding.

12. Adjust fan belts to proper alignment and tension.

13. Start unit according to manufacturer's written instructions.

14. Complete startup sheets and attach copy with Contractor's startup report.

15. Inspect and record performance of interlocks and protective devices; verify sequences.

16. Operate unit for an initial period as recommended or required by manufacturer.

17. Verify thermostat and humidistat calibration.

18. Inspect outdoor-air dampers for proper stroke and interlock with return-air dampers.

19. Inspect controls for correct sequencing of heating, mixing dampers, refrigeration, and normal and emergency shutdown.

Retain testing requirements if not using Division 23 Section "Testing, Adjusting, and Balancing for HVAC."

20. Start refrigeration system and measure and record the following:

a. Coil leaving-air, dry- and wet-bulb temperatures.

b. Coil entering-air, dry- and wet-bulb temperatures.

c. Outdoor-air, dry-bulb temperature.

d. Outdoor-air-coil, discharge-air, dry-bulb temperature.

21. Measure and record the following minimum and maximum airflows.  Plot fan volumes on fan curve.

a. Supply-air volume.

b. Return-air volume.

c. Relief-air volume.

d. Outdoor-air intake volume.

3.6 ADJUSTING

A. Adjust initial temperature and humidity set points.

B. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

3.7 CLEANING

A. Replace filters used during construction prior to air balance or substantial completion.

B. After completing installation of exposed, factory-finished water-source heat pumps, inspect exposed finishes and repair damaged finishes.

3.8 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain water-source heat pumps.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 238146

WATER-SOURCE UNITARY HEAT PUMPS
238146 - 1

