Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
12/03 (R 06/06)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238216 - AIR COILS
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following types of air coils that are not an integral part of air-handling units:

Adjust list below to suit Project.

1. Hot-water.

2. Chilled-water.

3. Steam.

4. Refrigerant.

5. Electric.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 23 Sections for air coils that are integral to air-handling units.

1.3 SUBMITTALS

A. Product Data:  For each type of product indicated.  Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for each air coil.  Include rated capacity and pressure drop for each air coil.

Retain paragraph below for electric coils.

B. Shop Drawings:  Diagram power, signal, and control wiring.

Retain paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which coil location and ceiling-mounted access panels are shown and coordinated with each other.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For air coils to include in operation and maintenance manuals.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

B. ASHRAE Compliance:

1. Comply with ASHRAE 15 for refrigeration system safety.

2. Comply with ASHRAE 33 for methods of testing cooling and heating coils.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

3. Comply with applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

1.5 PROJECT CONDITIONS

A. Altitude above Mean Sea Level:  <Insert feet (m).>

PART 2 -  PRODUCTS

2.1 WATER COILS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Aerofin Corporation.

2. Carrier Corporation.

3. Coil Company, LLC.

4. Dunham-Bush, Inc.

5. Heatcraft Refrigeration Products LLC; Heat Transfer Division.

6. Super Radiator Coils.

7. Trane.

8. USA Coil & Air.

9. <Insert manufacturer's name.>

D. Performance Ratings:  Tested and rated according to ARI 410 and ASHRAE 33.

Pressure/temperature ratings in first paragraph below are common.  Some manufacturers may vary ratings.

E. Minimum Working-Pressure/Temperature Ratings:  200 psig (1380 kPa), 325 deg F (163 deg C).

F. Source Quality Control:  Factory tested to 300 psig (2070 kPa).

G. Tubes:  ASTM B 743 copper, minimum [0.020 inch (0.508 mm)] [0.035 inch (0.889 mm)] [0.049 inch (1.245 mm)] <Insert size> thick.

H. Fins:  [Aluminum] [Copper], minimum [0.006 inch (0.152 mm)] [0.010 inch (0.254 mm)] <Insert size> thick.

I. Headers:  [Cast iron with drain and air vent tappings] [Cast iron with cleaning plugs, and drain and air vent tappings] [Seamless copper tube with brazed joints, prime coated] [Steel with brazed joints, prime coated].

Retain one of two paragraphs below.

J. Frames:  Galvanized-steel channel frame, minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] [0.0625 inch (1.6 mm)] thick for [slip-in] [flanged] mounting.

K. Frames:  ASTM A 666, Type [304] [316] stainless steel, minimum 0.0625 inch (1.6 mm) thick for [slip-in] [flanged] mounting.

Retain paragraph and subparagraphs below for face-and-bypass heating coils.

L. Hot-Water Coil and Steam Coil, Face-and-Bypass Dampers:  Alternating arrangement of coil segments and dampers.

1. Coil Configuration:  [Horizontal] [Vertical] tubes.

2. Dampers:  [Extruded-aluminum] [Galvanized-steel] blades with edge and end seals; full-length drive rod and mount for actuator [in] [outside] the airstream.

If Project has more than one type or size of hot-water coil, delete paragraph and subparagraphs below and schedule coils on Drawings.

M. Hot-Water Coil Capacities and Characteristics:

1. Coil Face Dimensions:

a. Finned Length:  <Insert inches (mm).>

b. Finned Width:  <Insert inches (mm).>

2. Minimum Fin Spacing:  [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.81 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.41 mm)] [0.0075 inch (0.19 mm)] <Insert spacing>.

3. Tube Diameter:  [0.625 inch (15.9 mm)] [0.50 inch (12.7 mm)] [0.375 inch (9.5 mm)] [0.75 inch (19.0 mm)] [1.0 inch (25.4 mm)] <Insert diameter>.

4. Number of Rows:  <Insert number.>

5. Serpentine:  [Single] [Half] [Full].

6. Mounting:  [Slip in] [Flanged].

7. Coating:  [Baked phenolic] [Cathodic epoxy e-coat].

8. Air Side:

a. Flow Rate:  <Insert cfm (L/s).>

b. Finned Area Face Velocity:  <Insert fpm (m/s).>

c. Static Pressure Drop:  <Insert inches wg (Pa).>

d. Total Capacity:  <Insert Btu/h (kW).>

e. Entering Temperature:  <Insert deg F (deg C).>

f. Leaving Temperature:  <Insert deg F (deg C).>

9. Water Side:

a. Flow Rate:  <Insert gpm (L/s).>

b. Tube Velocity:  <Insert fpm (m/s).>

c. Glycol Type:  [Ethylene] [Propylene].

d. Aqueous Glycol Solution Concentration:  <Insert percentage.>

e. Pressure Drop:  <Insert feet (kPa).>

f. Entering Temperature:  <Insert deg F (deg C).>

g. Leaving Temperature:  <Insert deg F (deg C).>

If Project has more than one type or size of chilled-water coil, delete paragraph and subparagraphs below and schedule coils on Drawings.

N. Chilled-Water Coil Capacities and Characteristics:

1. Coil Face Dimensions:

a. Finned Length:  <Insert inches (mm).>

b. Finned Width:  <Insert inches (mm).>

2. Minimum Fin Spacing:  [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.81 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.41 mm)] [0.0075 inch (0.19 mm)] <Insert spacing>.

3. Tube Diameter:  [0.625 inch (15.9 mm)] [0.50 inch (12.7 mm)] [0.375 inch (9.5 mm)] [0.75 inch (19.0 mm)] [1.0 inch (25.4 mm)] <Insert diameter>.

4. Number of Rows:  <Insert number.>

5. Serpentine:  [Half] [Single] [Double].

6. Mounting:  [Slip in] [Flanged].

7. Coating:  [Baked phenolic] [Cathodic epoxy e-coat].

8. Air Side:

a. Flow Rate:  <Insert cfm (L/s).>

b. Finned Area Face Velocity:  <Insert fpm (m/s).>

c. Static Pressure Drop:  <Insert inches wg (Pa).>

d. Total Capacity:  <Insert Btu/h (kW).>

e. Sensible Capacity:  <Insert Btu/h (kW).>

f. Entering Dry-Bulb Temperature:  <Insert deg F (deg C).>

g. Entering Wet-Bulb Temperature:  <Insert deg F (deg C).>

h. Leaving Dry-Bulb Temperature:  <Insert deg F (deg C).>

i. Leaving Wet-Bulb Temperature:  <Insert deg F (deg C).>

9. Water Side:

a. Flow Rate:  <Insert gpm (L/s).>

b. Tube Velocity:  <Insert fpm (m/s).>

c. Glycol Type:  [Ethylene] [Propylene].

d. Aqueous Glycol Solution Concentration:  <Insert percentage.>

e. Pressure Drop:  <Insert feet (Pa).>

f. Entering Temperature:  <Insert deg F (deg C).>

g. Leaving Temperature:  <Insert deg F (deg C).>

2.2 STEAM COILS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Aerofin Corporation.

2. Carrier Corporation.

3. Coil Company, LLC.

4. Dunham-Bush, Inc.

5. Heatcraft Refrigeration Products LLC; Heat Transfer Division.

6. Super Radiator Coils.

7. Trane.

8. USA Coil & Air.

9. <Insert manufacturer's name.>

D. Performance Ratings:  Tested and rated according to ARI 410 and ASHRAE 33.

Pressure/temperature ratings in first paragraph below are common.  Some manufacturers may vary ratings.

E. Minimum Working-Pressure/Temperature Ratings:  100 psig (690 kPa), 400 deg F (204 deg C).

F. Source Quality Control:  Factory tested to 300 psig (2070 kPa).

G. Tubes:  ASTM B 743 copper, minimum [0.025 inch (0.635 mm)] [0.035 inch (0.889 mm)] [0.049 inch (1.245 mm)] <Insert size> thick.

H. Fins:  [Aluminum] [Copper], minimum [0.006 inch (0.152 mm)] [0.010 inch (0.254 mm)] <Insert size> thick.

I. Headers:  [Cast iron with drain and air vent tappings] [Cast iron with cleaning plugs, and drain and air vent tappings] [Seamless copper tube with brazed joints, prime coated] [Steel with brazed joints, prime coated].

Indicate single- or distributing-tube type in "Capacities and Characteristics" Paragraph or in schedule on Drawings.

J. Tube Type:  Single or distributing as indicated.

Retain one of two paragraphs below.

K. Frames:  Galvanized-steel channel frame, minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] [0.0625 inch (1.6 mm)] thick for [slip-in] [flanged] mounting.

L. Frames:  ASTM A 666, Type [304] [316] stainless steel, minimum 0.0625 inch (1.6 mm) thick for [slip-in] [flanged] mounting.

Retain paragraph and subparagraphs below for face-and-bypass coils.

M. Face-and-Bypass Dampers:  Alternating arrangement of coil segments and dampers.

1. Coil Configuration:  [Horizontal] [Vertical] tubes.

2. Dampers:  [Extruded-aluminum] [Galvanized-steel] blades with edge and end seals; full-length drive rod and mount for actuator [in] [outside] the airstream.

If Project has more than one type or size of steam coil, delete paragraph and subparagraphs below and schedule coils on Drawings.

N. Capacities and Characteristics:

1. Coil Face Dimensions:

a. Finned Length:  <Insert inches (mm).>

b. Finned Width:  <Insert inches (mm).>

2. Minimum Fin Spacing:  [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.81 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.41 mm)] [0.0075 inch (0.19 mm)] <Insert spacing>.

3. Tube Diameter:  [0.625 inch (15.9 mm)] [0.50 inch (12.7 mm)] [0.375 inch (9.5 mm)] [0.75 inch (19.0 mm)] [1.0 inch (25.4 mm)] <Insert diameter>.

4. Number of Rows:  <Insert number.>

5. Mounting:  [Slip in] [Flanged].

6. Air Side:

a. Flow Rate:  <Insert cfm (L/s).>

b. Finned Area Face Velocity:  <Insert fpm (m/s).>

c. Static Pressure Drop:  <Insert inches wg (Pa).>

d. Total Capacity:  <Insert Btu/h (kW).>

e. Entering Temperature:  <Insert deg F (deg C).>

f. Leaving Temperature:  <Insert deg F (deg C).>

7. Steam Side:

a. Inlet Pressure:  <Insert psig (kPa).>

b. Tube Type:  [Single] [Distributing].

c. Condensing Capacity:  <Insert lb/h (g/s).>

2.3 REFRIGERANT COILS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Aerofin Corporation.

2. Carrier Corporation.

3. Coil Company, LLC.

4. Dunham-Bush, Inc.

5. Heatcraft Refrigeration Products LLC; Heat Transfer Division.

6. Lennox Industries Inc.

7. Super Radiator Coils.

8. Trane.

9. USA Coil & Air.

10. <Insert manufacturer's name.>

D. Performance Ratings:  Tested and rated according to ARI 410 and ASHRAE 33.

Pressure rating in first paragraph below is common.  Some manufacturers may vary rating.

E. Minimum Working-Pressure Rating:  300 psig (2070 kPa).

F. Source Quality Control:  Factory tested to 450 psig (3105 kPa).

G. Tubes:  ASTM B 743 copper, minimum [0.020 inch (0.508 mm)] [0.035 inch (0.889 mm)] [0.049 inch (1.245 mm)] <Insert size> thick.

H. Fins:  [Aluminum] [Copper], minimum [0.006 inch (0.152 mm)] [0.010 inch (0.254 mm)] <Insert size> thick.

I. Suction and Distributor Piping:  ASTM B 88, Type L (ASTM B 88M, Type B) copper tube with brazed joints.

Retain one of two paragraphs below.

J. Frames:  Galvanized-steel channel frame, minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] [0.0625 inch (1.6 mm)] thick for [slip-in] [flanged] mounting.

K. Frames:  ASTM A 666, Type [304] [316] stainless steel, minimum 0.0625 inch (1.6 mm) thick for [slip-in] [flanged] mounting.

If Project has more than one type or size of refrigerant coil, delete paragraph and subparagraphs below and schedule coils on Drawings.

L. Capacities and Characteristics:

1. Coil Face Dimensions:

a. Finned Length:  <Insert inches (mm).>

b. Finned Width:  <Insert inches (mm).>

2. Minimum Fin Spacing:  [0.125 inch (3.18 mm)] [0.091 inch (2.31 mm)] [0.071 inch (1.81 mm)] [0.067 inch (1.70 mm)] [0.056 inch (1.41 mm)] [0.0075 inch (0.19 mm)] <Insert spacing>.

3. Tube Diameter:  [0.625 inch (15.9 mm)] [0.50 inch (12.7 mm)] [0.375 inch (9.5 mm)] [0.75 inch (19.0 mm)] [1.0 inch (25.4 mm)] <Insert diameter>.

4. Number of Rows:  <Insert number.>

5. Coil Split:  [Row] [Face] [Interlaced].

6. Mounting:  [Slip in] [Flanged].

7. Coating:  [Baked phenolic] [Cathodic epoxy e-coat].

8. Air Side:

a. Flow Rate:  <Insert cfm (L/s).>

b. Finned Area Face Velocity:  <Insert fpm (m/s).>

c. Static Pressure Drop:  <Insert inches wg (Pa).>

d. Total Capacity:  <Insert Btu/h (kW).>

e. Sensible Capacity:  <Insert Btu/h (kW).>

f. Entering Dry-Bulb Temperature:  <Insert deg F (deg C).>

g. Entering Wet-Bulb Temperature:  <Insert deg F (deg C).>

h. Leaving Dry-Bulb Temperature:  <Insert deg F (deg C).>

i. Leaving Wet-Bulb Temperature:  <Insert deg F (deg C).>

9. Refrigerant Side:

LEED-NC Credit EA 4 awards a single point if all HVAC&R equipment meets requirements for enhanced refrigerant management.

a. Refrigerant Type:  <Insert type.>

b. Saturated Suction Temperature:  <Insert deg F (deg C).>

2.4 ELECTRIC COILS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Brasch Manufacturing Co., Inc.

2. Chromalox, Inc., Wiegand Industrial Division; Emerson Electric Company.

3. Dunham-Bush, Inc.

4. INDEECO.

5. Trane.

6. <Insert manufacturer's name.>

D. Coil Assembly:  Comply with UL 1995.

Retain one of first two paragraphs below.

E. Heating Elements:  Coiled resistance wire of 80 percent nickel and 20 percent chromium; surrounded by compacted magnesium-oxide powder in tubular-steel sheath; with spiral-wound, copper-plated, steel fins continuously brazed to sheath.

F. Heating Elements:  Open-coil resistance wire of 80 percent nickel and 20 percent chromium, supported and insulated by floating ceramic bushings recessed into casing openings, and fastened to supporting brackets.

G. High-Temperature Coil Protection:  Disk-type, automatically reset, thermal-cutout, safety device; serviceable through terminal box without removing heater from duct or casing.

1. Secondary Protection:  Load-carrying, manually reset or manually replaceable, thermal cutouts; factory wired in series with each heater stage.

H. Frames:  Galvanized-steel channel frame, minimum [0.052 inch (1.3 mm)] [0.064 inch (1.6 mm)] [0.079 inch (2.0 mm)] [0.0625 inch (1.6 mm)] thick for [slip-in] [flanged] mounting.

I. Control Panel:  [Unit] [Remote] mounted with disconnecting means and overcurrent protection.  Include the following controls:

1. Magnetic contactor.

2. Mercury contactor.

3. Toggle switches; one per step.

4. Step controller.

5. Time-delay relay.

6. Pilot lights; one per step.

7. Airflow proving switch.

Retain one of two paragraphs below.

J. Refer to Division 23 Section "Instrumentation and Control for HVAC" for thermostat.

K. Thermostats:  Wall-mounted thermostats, with temperature range from 50 to 90 deg F (10 to plus 32 deg C), and 2.5 deg F (1.4 deg C) throttling range.

If Project has more than one type or size of electric coil, delete paragraph and subparagraphs below and schedule coils on Drawings.

L. Capacities and Characteristics:

1. Coil Face Dimensions:

a. Length:  <Insert inches (mm).>

b. Height:  <Insert inches (mm).>

2. Mounting:  [Slip in] [Flanged].

3. Air Side:

a. Flow Rate:  <Insert cfm (L/s).>

b. Face Velocity:  <Insert fpm (m/s).>

c. Static Pressure Drop:  <Insert inches wg (Pa).>

d. Total Capacity:  <Insert Btu/h (kW).>

e. Entering Temperature:  <Insert deg F (deg C).>

f. Leaving Temperature:  <Insert deg F (deg C).>

4. Electrical Characteristics:

a. Capacity:  <Insert kW.>

b. Number of Steps:  <Insert number.>

c. Volts:  <Insert value.>

d. Phase:  <Insert value.>

e. Hertz:  <Insert value.>

f. Full-Load Amperes:  <Insert value.>

g. Minimum Circuit Ampacity:  <Insert value.>

h. Maximum Overcurrent Protection:  <Insert amperage.>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine ducts, plenums, and casings to receive air coils for compliance with requirements for installation tolerances and other conditions affecting coil performance.

Retain first paragraph below for hot-water, chilled-water, steam, and refrigerant coils.

B. Examine roughing-in for piping systems to verify actual locations of piping connections before coil installation.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install coils level and plumb.

B. Install coils in metal ducts and casings constructed according to SMACNA's "HVAC Duct Construction Standards, Metal and Flexible."

C. Install [galvanized] [stainless]-steel drain pan under each cooling coil.

Retain option in first subparagraph below to comply with LEED-NC Prerequisite EQ 1.

1. Construct drain pans with connection for drain; insulated[and complying with ASHRAE 62.1-2004].

2. Construct drain pans to extend beyond coil length and width and to connect to condensate trap and drainage.

3. Extend drain pan upstream and downstream from coil face.

4. Extend drain pan under coil headers and exposed supply piping.

D. Install moisture eliminators for cooling coils.  Extend drain pan under moisture eliminator.

Retain paragraphs below for water, steam, and refrigerant coils.

E. Straighten bent fins on air coils.

F. Clean coils using materials and methods recommended in writing by manufacturers, and clean inside of casings and enclosures to remove dust and debris.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in hydronic, steam and condensate, and refrigerant piping systems.

A. Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

B. Install piping adjacent to coils to allow service and maintenance.

Retain paragraph below for water coils.

C. Connect water piping with unions and shutoff valves to allow coils to be disconnected without draining piping.  Control valves are specified in Division 23 Section "Instrumentation and Control for HVAC," and other piping specialties are specified in Division 23 Section "Hydronic Piping."

Retain paragraph below for steam coils.

D. Connect steam piping with gate valve and union and steam condensate piping with union, strainer, trap, and gate valve to allow coils to be disconnected without draining piping.  Control valves are specified in Division 23 Section "Instrumentation and Control for HVAC," and other piping specialties are specified in Division 23 Section "Steam and Condensate Heating Piping."

Retain paragraph below for refrigerant coils.

E. Connect refrigerant piping according to Division 23 Section "Refrigerant Piping."

Retain paragraphs below for electric coils.

F. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

G. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

Retain this Article for electric coils.

A. Perform the following field tests and inspections and prepare test reports:

1. Operational Test:  After electrical circuitry has been energized, operate electric coils to confirm proper unit operation.

2. Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

END OF SECTION 238216

AIR COILS
238216 - 1

