Copyright 2005 AIA
MASTERSPEC Full Length
06/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238323 - RADIANT-HEATING ELECTRIC PANELS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes prefabricated radiant-heating electric panels.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 23 Section "Valance Heating and Cooling Units" for factory-fabricated electric heating panels for ceiling and wall applications.

2. Division 23 Section "Radiant-Heating Electric Cables."

1.3 SUBMITTALS

A. Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories for each type of product indicated.

B. Shop Drawings:  For electric heating panels.  Include plans, sections, details, and attachments to other work.

1. Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

C. Coordination Drawings:  Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

1. Ceiling suspension assembly members.

2. Method of attaching hangers to building structure.

3. Structural members to which heating panels and suspension systems will be attached.

4. Size and location of initial access modules for acoustical tile.

5. Items installed in finished ceiling, including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. Perimeter moldings.

g. <Insert item.>

D. Samples for Initial Selection:  For units with factory-applied color finishes.

Delete paragraph above if colors are preselected and specified or scheduled.  Retain first paragraph below with or without above.

E. Samples for Verification for Radiant Panel Finishes:  [12 by 12 inches (300 by 300 mm)] <Insert size>.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For electric heating panels to include in operation and maintenance manuals.

1.4 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.5 COORDINATION

Edit this Article to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of radiant panels and suspension system components with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, and partition assemblies.

PART 2 -  PRODUCTS

2.1 PREFABRICATED RADIANT-HEATING ELECTRIC PANELS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Berko Electric Heating; a division of Marley Engineered Products.

2. Markel Products; a division of TPI Corporation.

3. QMark Electric Heating; a division of Marley Engineered Products.

4. SSHC, Inc.; Solid State Heating Division.

5. <Insert manufacturer's name.>

D. Description:  Sheet-metal-enclosed panel with heating element suitable for [lay-in installation flush with T-bar ceiling grid] [surface mounting] [recessed mounting].  Comply with UL 2021.

1. Panel:  Minimum 0.0276-inch- (0.7-mm-) thick, galvanized-steel sheet back panel riveted to minimum 0.0396-inch- (1.0-mm-) thick, galvanized-steel sheet front panel with fused-on crystalline surface.

Retain one of first two subparagraphs below.

2. Heating Element:  Powdered graphite sandwiched between sheets of electric insulation.

3. Heating Element:  Insulated resistive wires.

4. Electrical Connections:  Nonheating, high-temperature, insulated-copper leads, factory connected to heating element.

Retain one of three subparagraphs below.  If more than one type of finish is required, indicate each type in a schedule on Drawings.

5. Exposed-Side Panel Finish:  Apply silk-screened finish to match appearance of Architect-selected acoustical ceiling tiles.

6. Exposed-Side Panel Finish:  Factory prime coated, ready for field painting.

7. Exposed-Side Panel Finish:  Baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

Retain subparagraph below for surface-mounting panels.

8. Surface-Mounting Trim:  Sheet metal with baked-enamel finish in manufacturer's [standard] [custom] paint color as selected by Architect.

E. Wall Thermostat:  Bimetal, sensing elements calibrated from 55 to 90 deg F (13 to 32 deg C); with contacts suitable for [low] [line]-voltage circuit, and manually operated on-off switch with contactors, relays, and control transformers.

If Project has more than one type or size of prefabricated radiant-heating electric panel, delete paragraph and subparagraphs below and schedule heating panels on Drawings.

F. Capacities and Characteristics:

1. Nominal Panel Size:  [24 by 24 inches (600 by 600 mm)] [24 by 36 inches (600 by 900 mm)] [24 by 48 inches (600 by 1200 mm)] [24 by 60 inches (600 by 1500 mm)] <Insert custom size>.

2. Heating Capacity:  [250] [375] [500] [570] [625] [750] [950] <Insert value> kW.

3. Electrical Characteristics for Single-Point Connection:

a. Volts:  <Insert value.>

b. Phase:  <Insert value.>

c. Hertz:  <Insert value.>

d. Full-Load Amperes:  <Insert value.>

e. Minimum Circuit Ampacity:  <Insert value.>

f. Maximum Overcurrent Protection:  <Insert value.>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine surfaces and substrates to receive electric heating panels for compliance with requirements for installation tolerances and other conditions affecting performance.

1. Ensure surfaces in contact with electric heating panels are free of burrs and sharp protrusions.

2. Ensure surfaces and substrates are level and plumb.

3. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install radiant-heating panels level and plumb.

B. Support for Radiant-Heating Panels in or on Grid-Type Suspended Ceilings:  Use grid as a support element.

1. Install a minimum of four ceiling support system rods or wires for each panel.  Locate not more than 6 inches (150 mm) from panel corners.

2. Support Clips:  Fasten to panel and to ceiling grid members at or near each panel corner with clips designed for the application.

3. Panels of Sizes Less Than Ceiling Grid:  Install as indicated on reflected ceiling plans or center in acoustical panel, and support panels independently with at least two 3/4-inch (19-mm) metal channels spanning and secured to ceiling tees.

Retain subparagraph below if Project is in a seismic area.

4. Install at least one independent support rod or wire from structure to a tab on panel.  Wire or rod shall have breaking strength of the weight of panel at a safety factor of 3.

To comply with requirements of the Americans with Disabilities Act, verify mounting height in paragraph below with authorities having jurisdiction.

C. Verify locations of thermostats with Drawings and room details before installation.  Install devices [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension> above finished floor.

3.3 CONNECTIONS

A. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

B. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.4 FIELD QUALITY CONTROL

A. Testing:  Perform the following field tests and inspections and prepare test reports:

1. Operate electric heating elements through each stage to verify proper operation and electrical connections.

2. Test and adjust controls and safeties.

B. Remove and replace malfunctioning units and retest as specified above.

END OF SECTION 238323

	RADIANT-HEATING ELECTRIC PANELS
	238323 - 1



