Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
09/04 (R 06/06)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260923 - LIGHTING CONTROL DEVICES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004.  ASHRAE/IESNA 90.1-2004, Section 9, "Lighting," sets minimum interior and exterior lighting power densities and minimum requirements for lighting controls.

Local switches, occupancy sensors, and daylight-harvesting controls can be used to meet the requirements of LEED-NC Credit EQ 6.1.  However, the use of task lighting may also be required, depending on the type of lighting system used on the Project.

Occupancy sensors and daylight-harvesting controls can be combined with other energy-conserving measures to meet the requirements of LEED-NC Credit EA 1.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following lighting control devices:

Adjust list below to suit Project.

1. Time switches.

2. [Outdoor] [Indoor] [Outdoor and indoor] photoelectric switches.

3. Indoor occupancy sensors.

4. Outdoor motion sensors.

5. Lighting contactors.

6. Emergency shunt relays.

B. Related Sections include the following:

List below only products that the reader might expect to find in this Section but are specified elsewhere.

1. Division 26 Sections "[Central Dimming Controls] [Modular Dimming Controls]" for architectural dimming system equipment.

2. Division 26 Section "Network Lighting Controls" for low-voltage, manual and programmable lighting control systems.

3. Division 26 Section "Wiring Devices" for wall-box dimmers, wall-switch occupancy sensors, and manual light switches.

4. Division 26 Section "Theatrical Lighting" for theatrical lighting controls.

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. LED:  Light-emitting diode.

B. PIR:  Passive infrared.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  Show installation details for occupancy and light-level sensors.

Delete subparagraph below if control connections are indicated on Drawings.

1. Interconnection diagrams showing field-installed wiring.

C. Field quality-control test reports.

D. Operation and Maintenance Data:  For each type of product to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

1.6 COORDINATION

A. Coordinate layout and installation of ceiling-mounted devices with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, smoke detectors, fire-suppression system, and partition assemblies.

PART 2 -  PRODUCTS

2.1 TIME SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Area Lighting Research, Inc.; Tyco Electronics.

2. Grasslin Controls Corporation; a GE Industrial Systems Company.

3. Intermatic, Inc.

4. Leviton Mfg. Company Inc.

5. Lightolier Controls; a Genlyte Company.

6. Lithonia Lighting; Acuity Lighting Group, Inc.

7. Paragon Electric Co.; Invensys Climate Controls.

8. Square D; Schneider Electric.

9. TORK.

10. Touch-Plate, Inc.

11. Watt Stopper (The).

12. <Insert manufacturer's name.>

Retain one of two paragraphs and associated subparagraphs below.

D. Electronic Time Switches:  Electronic, solid-state programmable units with alphanumeric display; complying with UL 917.

Delete first subparagraph below if configuration is indicated on Drawings.

1. Contact Configuration:  [SPST] [DPST] [DPDT] <Insert configuration>.

2. Contact Rating:  [30-A inductive or resistive, 240-V ac] [20-A ballast load, 120/240-V ac] <Insert rating>.

Retain one of first eight subparagraphs below.

3. Program:  8 on-off set points on a 24-hour schedule[ and an annual holiday schedule that overrides the weekly operation on holidays].

4. Program:  2 on-off set points on a 24-hour schedule, allowing different set points for each day of the week[ and an annual holiday schedule that overrides the weekly operation on holidays].

5. Programs:  <Insert number> channels; each channel shall be individually programmable with 8 on-off set points on a 24-hour schedule.

6. Programs:  <Insert number> channels; each channel shall be individually programmable with 2 on-off set points on a 24-hour schedule with skip-a-day weekly schedule.

7. Programs:  <Insert number> channels; each channel shall be individually programmable with 2 on-off set points on a 24-hour schedule, allowing different set points for each day of the week.

8. Programs:  <Insert number> channels; each channel shall be individually programmable with 40 on-off operations per week and an annual holiday schedule that overrides the weekly operation on holidays.

9. Programs:  <Insert number> channels; each channel shall be individually programmable with 40 on-off operations per week, plus 4 seasonal schedules that modify the basic program, and an annual holiday schedule that overrides the weekly operation on holidays.

10. Program:  <Insert configuration>[ and an annual holiday schedule that overrides the weekly operation on holidays].

11. Circuitry:  Allow connection of a photoelectric relay as substitute for on-off function of a program[ on selected channels].

12. Astronomic Time:  [All] [Selected] channels.

13. Battery Backup:  For schedules and time clock.

E. Electromechanical-Dial Time Switches:  Type complying with UL 917.

Delete first subparagraph below if configuration is indicated on Drawings.

1. Contact Configuration:  [SPST] [DPST] [SPDT] [DPDT] <Insert configuration>.

2. Contact Rating:  [30-A inductive or resistive, 240-V ac] [20-A ballast load, 120/240-V ac] <Insert rating>.

Five subparagraphs below describe optional features.

3. Circuitry:  Allow connection of a photoelectric relay as substitute for on-off function of a program.

Astronomic dial in first subparagraph below makes the time switch self-adjusting for seasonal changes and automatically adjusts on-off times as days grow shorter or longer.

4. Astronomic time dial.

5. Eight-Day Program:  Uniquely programmable for each weekday and holidays.

6. Skip-a-day mode.

7. Wound-spring reserve carryover mechanism to keep time during power failures, minimum of [16] <Insert number> hours.

2.2 OUTDOOR PHOTOELECTRIC SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Area Lighting Research, Inc.; Tyco Electronics.

2. Grasslin Controls Corporation; a GE Industrial Systems Company.

3. Intermatic, Inc.

4. Lithonia Lighting; Acuity Lighting Group, Inc.

5. Novitas, Inc.

6. Paragon Electric Co.; Invensys Climate Controls.

7. Square D; Schneider Electric.

8. TORK.

9. Touch-Plate, Inc.

10. Watt Stopper (The).

11. <Insert manufacturer's name.>

Retain one of two paragraphs and associated subparagraphs below.  Light-level range is typical for dusk-to-dawn lighting applications.  Inductive rating for a switch means it is UL tested at 50 percent power factor.

First paragraph describes a device with built-in, metal-oxide-varistor surge protection, selection of contact ratings, and range of adjustments to orient the photocell.  These features allow flexibility in making device suitable for a wide range of mounting and control situations.

Second paragraph describes a device with less-effective surge protection, having a fixed load-breaking contact capacity, and that may be considered for control of a single lighting fixture designed for mounting on fixture.

D. Description:  Solid state, with [SPST] [DPST] dry contacts rated for [1800-VA tungsten or 1000-VA inductive] <Insert value>, to operate connected relay, contactor coils, or microprocessor input; complying with UL 773A.

1. Light-Level Monitoring Range:  1.5 to 10 fc (16.14 to 108 lx), with an adjustment for turn-on and turn-off levels within that range[, and a directional lens in front of photocell to prevent fixed light sources from causing turn-off].

2. Time Delay:  15-second minimum, to prevent false operation.

3. Surge Protection:  Metal-oxide varistor, complying with IEEE C62.41.1, IEEE C62.41.2, and IEEE 62.45 for Category A1 locations.

4. Mounting:  Twist lock complying with IEEE C136.10, with base-and-stem mounting or stem-and-swivel mounting accessories as required to direct sensor to the north sky exposure.

E. Description:  Solid state, with [SPST] [DPST] dry contacts rated for 1800 VA to operate connected load, relay, or contactor coils; complying with UL 773.

1. Light-Level Monitoring Range:  1.5 to 10 fc (16.14 to 108 lx), with an adjustment for turn-on and turn-off levels within that range.

2. Time Delay:  30-second minimum, to prevent false operation.

3. Lightning Arrester:  Air-gap type.

4. Mounting:  Twist lock complying with IEEE C136.10, with base.

2.3 INDOOR PHOTOELECTRIC SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Allen-Bradley/Rockwell Automation.

2. Area Lighting Research, Inc.; Tyco Electronics.

3. Eaton Electrical Inc; Cutler-Hammer Products.

4. Grasslin Controls Corporation; a GE Industrial Systems Company.

5. Intermatic, Inc.

6. Lithonia Lighting; Acuity Lighting Group, Inc.

7. MicroLite Lighting Control Systems.

8. Novitas, Inc.

9. Paragon Electric Co.; Invensys Climate Controls.

10. Square D; Schneider Electric.

11. TORK.

12. Touch-Plate, Inc.

13. Watt Stopper (The).

14. <Insert manufacturer's name.>

Photoelectric switch in paragraph and subparagraphs below is used to turn lighting on and off, depending on amount of daylight reaching the work plane.  Switch described is for lighting control of interior spaces.  Switching range should correspond to typical interior lighting levels for the space in which it is mounted.

Paragraph below is suitable for general indoor daylight harvesting applications.  Sensors and accessories are for switching ballasts or lamps.  Dimming controls are specified in Division 26 Sections "Central Dimming Controls" and "Modular Dimming Controls."

D. Ceiling-Mounted Photoelectric Switch:  Solid-state, light-level sensor unit, with separate relay unit[ mounted on luminaire], to detect changes in lighting levels that are perceived by the eye.  Cadmium sulfide photoresistors are not acceptable.

1. Sensor Output:  Contacts rated to operate the associated relay, complying with UL 773A.  Sensor shall be powered from the relay unit.

Relay unit in subparagraph below is suitable for controlling a single lighting circuit, provided the circuit load does not exceed the listed aggregate load.

2. Relay Unit:  Dry contacts rated for [20] <Insert amperage>-A ballast load at 120- and 277-V ac, for [13] <Insert amperage>-A tungsten at 120-V ac, and for [1] <Insert value> hp at 120-V ac.  Power supply to sensor shall be 24-V dc, 150-mA, Class 2 power source as defined by NFPA 70.

Retain second option in first subparagraph below for lighting control of interior spaces with large window areas, including atriums and corridors; otherwise, retain first option.

3. Light-Level Monitoring Range:  [10 to 200 fc (108 to 2152 lx)] [100 to 1000 fc (1080 to 10 800 lx)], with an adjustment for turn-on and turn-off levels within that range.

4. Time Delay:  Adjustable from 5 to 300 seconds to prevent cycling, with deadband adjustment.

5. Indicator:  Two LEDs to indicate the beginning of on-off cycles.

Paragraph and subparagraphs below are suitable for specialized application of controlling lighting units in an area where one or more skylights are the source of illumination, and lighting level is controlled in direct relation to brightness of the sky.

E. Skylight Photoelectric Sensors:  Solid-state, light-level sensor; housed in a threaded, plastic fitting for mounting under skylight, facing up at skylight; with separate relay unit[ mounted on luminaire], to detect changes in lighting levels that are perceived by the eye.  Cadmium sulfide photoresistors are not acceptable.

1. Sensor Output:  Contacts rated to operate the associated relay, complying with UL 773A.  Sensor shall be powered from the relay unit.

Relay unit in first subparagraph below is suitable for controlling a single lighting circuit, provided the circuit load does not exceed the listed aggregate load.

2. Relay Unit:  Dry contacts rated for [20] <Insert amperage>-A ballast load at 120- and 277-V ac, for [13] <Insert amperage>-A tungsten at 120-V ac, and for [1] <Insert value> hp at 120-V ac.  Power supply to sensor shall be 24-V dc, 150-mA, Class 2 power source as defined by NFPA 70.

3. Light-Level Monitoring Range:  1000 to 10,000 fc (10 800 to 108 000 lx), with an adjustment for turn-on and turn-off levels within that range.

4. Time Delay:  Adjustable from 5 to 300 seconds to prevent cycling, with deadband adjustment.

5. Indicator:  Two LEDs to indicate the beginning of on-off cycles.

2.4 INDOOR OCCUPANCY SENSORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Hubbell Lighting.

2. Leviton Mfg. Company Inc.

3. Lithonia Lighting; Acuity Lighting Group, Inc.

4. Novitas, Inc.

5. RAB Lighting, Inc.

6. Sensor Switch, Inc.

7. TORK.

8. Watt Stopper (The).

9. <Insert manufacturer's name.>

D. General Description:  Wall- or ceiling-mounting, solid-state units with a separate relay unit.

Retain subparagraphs and associated subparagraphs below to specify various types of units required for Project.

1. Operation:  Unless otherwise indicated, turn lights on when covered area is occupied and off when unoccupied; with a time delay for turning lights off, adjustable over a minimum range of 1 to 15 minutes.

2. Sensor Output:  Contacts rated to operate the connected relay, complying with UL 773A.  Sensor shall be powered from the relay unit.

3. Relay Unit:  Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac.  Power supply to sensor shall be 24-V dc, 150-mA, Class 2 power source as defined by NFPA 70.

4. Mounting:

a. Sensor:  Suitable for mounting in any position on a standard outlet box.

b. Relay:  Externally mounted through a 1/2-inch (13-mm) knockout in a standard electrical enclosure.

c. Time-Delay and Sensitivity Adjustments:  Recessed and concealed behind hinged door.

5. Indicator:  LED, to show when motion is being detected during testing and normal operation of the sensor.

6. Bypass Switch:  Override the on function in case of sensor failure.

7. Automatic Light-Level Sensor:  Adjustable from 2 to 200 fc (21.5 to 2152 lx); keep lighting off when selected lighting level is present.

Retain one or more of three paragraphs and associated subparagraphs below.  Revise coverage area of detectors and add detectors with different coverage patterns and features to suit Project.

E. PIR Type:  Ceiling mounting; detect occupancy by sensing a combination of heat and movement in area of coverage.

1. Detector Sensitivity:  Detect occurrences of 6-inch- (150-mm-) minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. (232 sq. cm).

2. Detection Coverage (Room):  Detect occupancy anywhere in a circular area of 1000 sq. ft. (93 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

3. Detection Coverage (Corridor):  Detect occupancy within 90 feet (27.4 m) when mounted on a 10-foot- (3-m-) high ceiling.

F. Ultrasonic Type:  Ceiling mounting; detect occupancy by sensing a change in pattern of reflected ultrasonic energy in area of coverage.

1. Detector Sensitivity:  Detect a person of average size and weight moving not less than 12 inches (305 mm) in either a horizontal or a vertical manner at an approximate speed of 12 inches/s (305 mm/s).

Coverage areas listed in four subparagraphs below are typical.

2. Detection Coverage (Small Room):  Detect occupancy anywhere within a circular area of 600 sq. ft. (56 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

3. Detection Coverage (Standard Room):  Detect occupancy anywhere within a circular area of 1000 sq. ft. (93 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

4. Detection Coverage (Large Room):  Detect occupancy anywhere within a circular area of 2000 sq. ft. (186 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

5. Detection Coverage (Corridor):  Detect occupancy anywhere within 90 feet (27.4 m) when mounted on a 10-foot- (3-m-) high ceiling in a corridor not wider than 14 feet (4.3 m).

G. Dual-Technology Type:  Ceiling mounting; detect occupancy by using a combination of PIR and ultrasonic detection methods in area of coverage.  Particular technology or combination of technologies that controls on-off functions shall be selectable in the field by operating controls on unit.

1. Sensitivity Adjustment:  Separate for each sensing technology.

2. Detector Sensitivity:  Detect occurrences of 6-inch- (150-mm-) minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. (232 sq. cm), and detect a person of average size and weight moving not less than 12 inches (305 mm) in either a horizontal or a vertical manner at an approximate speed of 12 inches/s (305 mm/s).

3. Detection Coverage (Standard Room):  Detect occupancy anywhere within a circular area of 1000 sq. ft. (93 sq. m) when mounted on a 96-inch- (2440-mm-) high ceiling.

2.5 OUTDOOR MOTION SENSORS (PIR)

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Bryant Electric; a Hubbell Company.

2. Hubbell Lighting.

3. Lithonia Lighting; Acuity Lighting Group, Inc.

4. Paragon Electric Co.; Invensys Climate Controls.

5. RAB Lighting, Inc.

6. TORK.

7. Watt Stopper (The).

8. <Insert manufacturer's name.>

Retain features in paragraph and subparagraphs below applicable to motion sensors for Project.

D. Performance Requirements:  Suitable for operation in ambient temperatures ranging from minus 40 to plus 130 deg F (minus 40 to plus 54 deg C), rated as raintight according to UL 773A.

1. Operation:  Turn lights on when sensing infrared energy changes between background and moving body in area of coverage; with a time delay for turning lights off, adjustable over a minimum range of 1 to 15 minutes.

2. Mounting:

a. Sensor:  Suitable for mounting in any position on a standard outdoor junction box.

b. Relay:  Internally mounted in a standard weatherproof electrical enclosure.

c. Time-Delay and Sensitivity Adjustments:  Recessed and concealed behind hinged door.

3. Bypass Switch:  Override the on function in case of sensor failure.

4. Automatic Light-Level Sensor:  Adjustable from 1 to 20 fc (11 to 215 lx); keep lighting off during daylight hours.

Retain one or both paragraphs below.  Revise coverage area of detectors and add detectors with different coverage patterns and features to suit Project.

E. Detector Sensitivity:  Detect occurrences of 6-inch- (150-mm-) minimum movement of any portion of a human body that presents a target of not less than 36 sq. in. (232 sq. cm).

F. Detection Coverage:  [Up to 35 feet (11 m), with a field of view of 90 degrees] [Up to 100 feet (30 m), with a field of view of 60 degrees] [Up to 35 feet (11 m), with a field of view of 180 degrees] [Up to 52.5 feet (16 m), with a field of view of 270 degrees] <Insert coverage area>.

Retain paragraph below for sensor with a built-in switch suitable for operating one or two lamps.  Standard unit for this purpose is typically limited to switching 300 W, such as two 150-PAR lamps.

G. Lighting Fixture Mounted Sensor:  Suitable for switching 300 W of tungsten load at 120- or 277-V ac.

Retain paragraph and subparagraphs below for split unit with wiring between relay and sensor and to specify relay suitable for contactor operation.

H. Individually Mounted Sensor:  Contacts rated to operate the connected relay, complying with UL 773A.  Sensor shall be powered from the relay unit.

1. Relay Unit:  Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac.  Power supply to sensor shall be 24-V dc, 150-mA, Class 2 power source as defined by NFPA 70.

2. Indicator:  LED, to show when motion is being detected during testing and normal operation of the sensor.

2.6 LIGHTING CONTACTORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Allen-Bradley/Rockwell Automation.

2. ASCO Power Technologies, LP; a division of Emerson Electric Co.

3. Eaton Electrical Inc.; Cutler-Hammer Products.

4. GE Industrial Systems; Total Lighting Control.

5. Grasslin Controls Corporation; a GE Industrial Systems Company.

6. Hubbell Lighting.

7. Lithonia Lighting; Acuity Lighting Group, Inc.

8. MicroLite Lighting Control Systems.

9. Square D; Schneider Electric.

10. TORK.

11. Touch-Plate, Inc.

12. Watt Stopper (The).

13. <Insert manufacturer's name.>

D. Description:  Electrically operated and [mechanically] [electrically] held, combination type with [fusible switch] [nonfused disconnect], complying with NEMA ICS 2 and UL 508.

Revise subparagraphs below, if required, for specific ratings or indicate on Drawings.  Coordinate control voltage with lighting control system if used.  See Evaluations for suggested options to be indicated on Drawings.

1. Current Rating for Switching:  Listing or rating consistent with type of load served, including tungsten filament, inductive, and high-inrush ballast (ballast with 15 percent or less total harmonic distortion of normal load current).

2. Fault Current Withstand Rating:  Equal to or exceeding the available fault current at the point of installation.

3. Enclosure:  Comply with NEMA 250.

4. Provide with control and pilot devices as [indicated on Drawings] [scheduled], matching the NEMA type specified for the enclosure.

Retain paragraph and associated subparagraphs below for interface with the BAS.  Coordinate with Division 23 Section "Instrumentation and Control for HVAC."

E. BAS Interface:  Provide hardware interface to enable the BAS to monitor and control lighting contactors.

1. Monitoring:  On-off status, <Insert monitoring point>.

2. Control:  On-off operation, <Insert control point>.

2.7 EMERGENCY SHUNT RELAY

Retain this Article for emergency lighting switched by manual, photoelectric, or other automatic switching devices.  Emergency shunt relay will bypass or shunt the manual switch or other control device and turn connected lights on when there is an outage of normal power.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product:  Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Lighting Control and Design, Inc.

2. <Insert manufacturer's name.>

D. Description:  Normally closed, electrically held relay, arranged for wiring in parallel with manual [or automatic ]switching contacts; complying with UL 924.

1. Coil Rating:  [120] [277] V.

2.8 CONDUCTORS AND CABLES

A. Power Wiring to Supply Side of Remote-Control Power Sources:  Not smaller than No. 12 AWG.  Comply with requirements in Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

B. Classes 2 and 3 Control Cable:  Multiconductor cable with stranded-copper conductors not smaller than No. [18] [22] [24] AWG.  Comply with requirements in Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

C. Class 1 Control Cable:  Multiconductor cable with stranded-copper conductors not smaller than No. [14] [16] [18] AWG.  Comply with requirements in Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

PART 3 -  EXECUTION

3.1 SENSOR INSTALLATION

A. Install and aim sensors in locations to achieve not less than 90 percent coverage of areas indicated.  Do not exceed coverage limits specified in manufacturer's written instructions.

3.2 CONTACTOR INSTALLATION

A. Mount electrically held lighting contactors with elastomeric isolator pads, to eliminate structure-borne vibration, unless contactors are installed in an enclosure with factory-installed vibration isolators.

3.3 WIRING INSTALLATION

Coordinate this Article with Drawings.

A. Wiring Method:  Comply with Division 26 Section "Low-Voltage Electrical Power Conductors and Cables." Minimum conduit size shall be 1/2 inch (13 mm).

B. Wiring within Enclosures:  Comply with NECA 1.  Separate power-limited and nonpower-limited conductors according to conductor manufacturer's written instructions.

C. Size conductors according to lighting control device manufacturer's written instructions, unless otherwise indicated.

D. Splices, Taps, and Terminations:  Make connections only on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

3.4 IDENTIFICATION

A. Identify components and power and control wiring according to Division 26 Section "Identification for Electrical Systems."

1. Identify controlled circuits in lighting contactors.

2. Identify circuits or luminaries controlled by photoelectric and occupancy sensors at each sensor.

B. Label time switches and contactors with a unique designation.

3.5 FIELD QUALITY CONTROL

A. Perform the following field tests and inspections and prepare test reports:

1. After installing time switches and sensors, and after electrical circuitry has been energized, adjust and test for compliance with requirements.

2. Operational Test:  Verify operation of each lighting control device, and adjust time delays.

B. Lighting control devices that fail tests and inspections are defective work.

3.6 ADJUSTING

A. Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting sensors to suit occupied conditions.  Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

3.7 DEMONSTRATION

This Article covers optional services; retain if Project warrants.  Coordinate with Division 01 training requirements.  If Project includes programmable lighting controls, coordinate with testing of that system.

A. Coordinate demonstration of products specified in this Section with demonstration requirements for low-voltage, programmable lighting control system specified in Division 26 Section "Network Lighting Controls."

B. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain lighting control devices.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 260923

LIGHTING CONTROL DEVICES
260923 - 1

