Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
09/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262500 - ENCLOSED BUS ASSEMBLIES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Feeder-bus assemblies.

2. Plug-in bus assemblies.

3. Bus plug-in devices.

1.3 DEFINITIONS

Retain abbreviation that remains after this Section has been edited.

A. TVSS:  Transient voltage surge suppressor.

1.4 SUBMITTALS

A. Shop Drawings:  For each type of [bus assembly] [and plug-in device].

1. Show fabrication and installation details for enclosed bus assemblies.  Include plans, elevations, and sections of components.  Designate components and accessories, including clamps, brackets, hanger rods, connectors, straight lengths, and fittings.

Retain first subparagraph below if Project requires fire-stop or weather barriers.

2. Show fittings, materials, fabrication, and installation methods for [listed fire-stop barriers] [and] [weather barriers].

3. Indicate required clearances, method of field assembly, and location and size of each field connection.

4. Detail connections to switchgear, switchboards, transformers, and panelboards.

5. Wiring Diagrams:  Power[ and signal] [ and control] [, signal, and control] wiring.

Retain subparagraph and associated subparagraphs below if products are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify products' compliance with performance requirements.  Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

6. Seismic-Restraint Details:  Signed and sealed by a qualified professional engineer.

a. Design Calculations:  Calculate requirements for selecting seismic restraints.

b. Detail fabrication, including anchorages and attachments to structure and to supported equipment.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

B. Coordination Drawings:  Floor plans and sections, drawn to scale.  Include scaled bus-assembly layouts and relationships between components and adjacent structural, mechanical, and electrical elements.  Show the following:

Revise subparagraphs below to suit Project.

1. Vertical and horizontal enclosed bus-assembly runs, offsets, and transitions.

2. Clearances for access above and to the side of enclosed bus assemblies.

3. Vertical elevation of enclosed bus assemblies above the floor or bottom of structure.

4. Support locations, type of support, and weight on each support.

C. Location of adjacent construction elements including light fixtures, HVAC and plumbing equipment, fire sprinklers and piping, signal and control devices, and other equipment.

D. Product Certificates:  For each type of enclosed bus assembly, signed by product manufacturer.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

E. Manufacturer Seismic Qualification Certification:  Submit certification that enclosed bus assemblies,[ plug-in devices,] accessories, and components will withstand seismic forces defined in Division 26 Section "Vibration and Seismic Controls for Electrical Systems."  Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

F. Qualification Data:  For [professional engineer] [and] [testing agency].

Retain first paragraph below if Contractor is responsible for field quality-control testing.

G. Field quality-control test reports.

H. Operation and Maintenance Data:  For enclosed bus assemblies to include in emergency, operation, and maintenance manuals.

1.5 QUALITY ASSURANCE

If an independent testing agency is required, see Division 01 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, retain one of first two paragraphs below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and subparagraph below if Contractor selects testing agency.

A. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

B. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

C. Source Limitations:  Obtain enclosed bus assemblies[ and plug-in devices] through one source from a single manufacturer.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with NEMA BU 1, "Busways."

F. Comply with NFPA 70.

1.6 DELIVERY, STORAGE, AND HANDLING

A. Deliver, store, and handle enclosed bus assemblies according to NEMA BU 1.1, "General Instructions for Proper Handling, Installation, Operation and Maintenance of Busway Rated 600 Volts or Less."

1.7 PROJECT CONDITIONS

A. Derate enclosed bus assemblies for continuous operation at indicated ampere ratings for ambient temperature not exceeding [122 deg F (50 deg C)] [140 deg F (60 deg C)] <Insert ambient temperature>.

1.8 COORDINATION

Revise paragraph below to delete or add types of construction that penetrate or are supported by ceilings.

A. Coordinate layout and installation of enclosed bus assemblies and suspension system with other construction that penetrates ceilings or floors or is supported by them, including light fixtures, HVAC equipment, fire-suppression system, and partition assemblies.

Retain paragraph below if required for concrete curbs around vertical floor penetrations.

B. Coordinate size and location of concrete curbs around openings for vertical bus.  Concrete, reinforcement, and formwork requirements are specified in Division 03.

1.9 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraph below to suit Project.

1. Plug-in Units:  [10] <Insert number> percent of amount installed[ for each size indicated], but no fewer than <Insert number> unit(s).

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers in this Article.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Calvert Company (The).

2. Eaton Electrical Inc.; Cutler-Hammer Products.

3. General Electric Company; Electrical Distribution & Control Division.

4. Siemens Energy & Automation, Inc.

5. Square D; Schneider Electric.

6. <Insert manufacturer's name.>

2.2 ENCLOSED BUS ASSEMBLIES

A. Feeder-Bus Assemblies:  NEMA BU 1, low-impedance bus assemblies in nonventilated housing; single-bolt joints; ratings as indicated.

Retain subparagraph below for projects in seismic areas.  Coordinate with "Submittals" Article for submittal of manufacturer's seismic qualification certification.

1. Seismic Fabrication Requirements:  Fabricate mounting provisions and attachments for feeder-bus assemblies with reinforcement strong enough to withstand seismic forces defined in Division 26 Section "Vibration and Seismic Controls for Electrical Systems" when mounting provisions and attachments are anchored to building structure

Select from options in first subparagraph below and revise to suit Project.  Consider 200 percent neutral on 4-wire systems if a significant portion of load is nonlinear (e.g., computers, fluorescent or high-intensity-discharge lighting, variable-frequency drives, etc.) and harmonic cancellation on the neutral conductor is unlikely.  If busways with different voltages and neutral capacities are required, delete subparagraph and include a schedule on Drawings.  See sample schedule in the Evaluations.

2. Voltage:  [120/208] [240] [480] [277/480] V; 3 phase; [100] [200] [percent neutral capacity].

3. Temperature Rise:  55 deg C above 40 deg C ambient maximum for continuous rated current.

4. Bus Materials:  Current-carrying [copper] [aluminum] conductors, fully insulated with Class 130C insulation except at joints; plated surface at joints.

5. Ground:

Retain one or more of three subparagraphs below.

a. 50 percent capacity integral with housing.

b. 50 percent capacity internal bus bars of material matching bus material.

c. 50 percent capacity isolated, internal bus bar of material matching bus material.

If subways with different ground or enclosure types are required, delete "Ground" Subparagraph and associated subparagraphs above or "Enclosure" Subparagraph below, or both, and include a schedule on Drawings.  See sample schedule in the Evaluations.

6. Enclosure:  [Steel with manufacturer's standard finish] [Aluminum with manufacturer's standard finish] [Weatherproof, steel or aluminum with manufacturer's standard finish, sealed seams, drains, and removable closures].

7. Fittings and Accessories:  Manufacturer's standard.

8. Mounting:  Arranged flat, edgewise, or vertically without derating.

B. Plug-in Bus Assemblies:  NEMA BU 1, low-impedance bus assemblies in nonventilated housing; single-bolt joints; ratings as indicated.

Retain subparagraph below for projects in seismic areas.  Coordinate with "Submittals" Article for submittal of manufacturer's seismic qualification certification.

1. Seismic Fabrication Requirements:  Fabricate mounting provisions and attachments for switchboards with reinforcement strong enough to withstand seismic forces defined in Division 26 Section "Vibration and Seismic Controls for Electrical Systems" when mounting provisions and attachments are anchored to building structure.

Select from options in first subparagraph below and revise to suit Project.  Consider 200 percent neutral on 4-wire systems if a significant portion of load is nonlinear (e.g., computers, fluorescent or high-intensity-discharge lighting, variable-frequency drives, etc.) and harmonic cancellation on the neutral conductor is unlikely.  If busways with different voltages and neutral capacities are required, delete subparagraph and include a schedule on Drawings.  See sample schedule in the Evaluations.

2. Voltage:  [120/208] [240] [480] [277/480] V; 3 phase; [100] [200] [percent neutral capacity].

3. Temperature Rise:  55 deg C above 40 deg C ambient maximum for continuous rated current.

4. Bus Materials:  Current-carrying [copper] [aluminum] conductors, fully insulated with Class 130C insulation except at stabs and joints; plated surface at stabs and joints.

5. Ground:

Retain one or more of three subparagraphs below.

a. 50 percent capacity integral with housing.

b. 50 percent capacity internal bus bar of material matching bus material.

c. 50 percent capacity isolated, internal bus bar of material matching bus material.

If subways with different ground or enclosure types are required, delete "Ground" Subparagraph and associated subparagraphs above or "Enclosure" Subparagraph below, or both, and include a schedule on Drawings.  See sample schedule in the Evaluations.

6. Enclosure:  [Steel, with manufacturer's standard finish, plug-in openings 24 inches (610 mm) o.c., and hinged covers over unused openings] [Aluminum, with manufacturer's standard finish, plug-in openings 24 inches (610 mm) o.c., and hinged covers over unused openings].

7. Fittings and Accessories:  Manufacturer's standard.

8. Mounting:  Arranged flat, edgewise, or vertically without derating.

2.3 PLUG-IN DEVICES

Chain-operable handles are available for plug-in devices.

For fusible-switch plug-in devices, R-type rejection fuse clips and J-type fuse clips are available in sizes from 30 to 600 A, rated 600 V.  L-type, bolt-on fuse clips are available in 800 to 1600 A, 600-V fusible switches.  Coordinate options selected in paragraph below with Division 26 Section "Fuses."

A. Fusible Switches:  NEMA KS 1, heavy duty; with [R-type rejection] [J-type] [L-type] fuse clips to accommodate specified fuses; hookstick-operated handle, lockable with two padlocks, and interlocked with cover in closed position.  See Division 26 Section "Fuses" for fuses and fuse installation requirements.

Indicate in schedule or diagrams on Drawings the frame size, trip rating, number of poles, interrupting-capacity rating, and auxiliary devices.

B. Molded-Case Circuit Breakers:  NEMA AB 1; hookstick-operated handle, lockable with two padlocks, and interlocked with cover in closed position.

C. TVSS:  NEMA 250, Type 1 enclosure with NEMA KS 1, fusible, disconnect switch and external handle to isolate TVSS from busway.  TVSS product and installation requirements are specified in Division 26 Section "Transient-Voltage Suppression for Low-Voltage Electrical Power Circuits."

D. Motor Controllers:  NEMA ICS 2, Class A, full voltage, nonreversing, across the line, unless otherwise indicated.

1. Control Circuit:  120 V; obtained from [integral control power transformer] <Insert source of control power> with a control power [transformer] [source] of enough capacity to operate connected pilot, indicating and control devices, plus 100 percent spare capacity.

2. Combination Controller:  Factory-assembled combination controller and disconnect switch with or without overcurrent protection as indicated.

Retain one of first three subparagraphs below if required.

a. Fusible Disconnecting Means:  NEMA KS 1, heavy-duty, fusible switch with [R-type rejection] [J-type] fuse clips rated for fuses.  Select and size fuses to provide Type 2 protection according to IEC 947-4-1, as certified by a nationally recognized testing laboratory (NRTL) acceptable to authorities having jurisdiction.  See Division 26 Section "Fuses" for fuses and fuse installation requirements.

b. Nonfusible Disconnecting Means:  NEMA KS 1, heavy-duty, nonfusible switch.

c. Circuit-Breaker Disconnecting Means:  NEMA AB 1, motor-circuit protector with field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

3. Overload Relay:  Ambient-compensated type with inverse-time-current characteristic and NEMA ICS 2, [Class 10] [Class 20] [Class 30] tripping characteristic.  Overload relays shall have heaters or sensors in each phase matched to nameplate full-load current of specific motor to which they connect and with appropriate adjustment for duty cycle.

Retain subparagraph above or below.

4. Adjustable Overload Relay:  Dipswitch selected for motor running overload protection with NEMA ICS 2, [Class 10] [Class 20] [Class 30] tripping characteristic, and selected to protect motor against voltage and current unbalance and single phasing.  Adjustable overload relays shall have Class II ground-fault protection with start and run delays to prevent nuisance trip on starting.

Coordinate paragraph and subparagraphs below with Drawings.

E. Multispeed Motor Controllers:  Match controller to motor type, application, and number of speeds; include the following accessories:

1. Compelling relay ensures motor starts only at low speed.

2. Accelerating relay ensures properly timed acceleration through speeds lower than that selected.

3. Decelerating relay ensures automatically timed deceleration through each speed.

Retain paragraph below if required.

F. Accessories:  Hookstick operator, adjustable to maximum extension of [14 feet (4.3 m)] <Insert dimension>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Support bus assemblies independent of supports for other elements such as equipment enclosures at connections to panelboards and switchboards, pipes, conduits, ceilings, and ducts.

1. Design each fastener and support to carry load indicated by seismic requirements and to comply with seismic-restraint details according to Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

Retain subparagraph above if requirements for seismic control are included in Part 1.  Retain four subparagraphs below if seismic restraint is not required.  Revise to suit Project.

2. Design each fastener and support to carry 200 lb (90 kg) or 4 times the weight of bus assembly, whichever is greater.

3. Support bus assembly to prevent twisting from eccentric loading.

4. Support bus assembly with not less than 3/8-inch (10-mm) steel rods.  Install side bracing to prevent swaying or movement of bus assembly.  Modify supports after completion to eliminate strains and stresses on bus bars and housings.

5. Fasten supports securely to building structure according to Division 26 Section "Hangers and Supports for Electrical Systems."

B. Install expansion fittings at locations where bus assemblies cross building expansion joints.  Install at other locations so distance between expansion fittings does not exceed manufacturer's recommended distance between fittings.

C. Construct rated fire-stop assemblies where bus assemblies penetrate fire-rated elements such as walls, floors, and ceilings.  Seal around penetrations according to Division 07 Section "Penetration Firestopping."

D. Install weatherseal fittings and flanges where bus assemblies penetrate exterior elements such as walls or roofs.  Seal around openings to make weathertight.  See Division 07 Section "Joint Sealants" for materials and application.

Coordinate floor penetrations with Structural Drawings.

E. Install a concrete curb at least 3 inches (75 mm) high around bus-assembly floor penetrations.

F. Coordinate bus-assembly terminations to equipment enclosures to ensure proper phasing, connection, and closure.

G. Tighten bus-assembly joints with torque wrench or similar tool recommended by bus-assembly manufacturer.  Tighten joints again after bus assemblies have been energized for 30 days.

H. Install bus-assembly, plug-in units.  Support connecting conduit independent of plug-in unit.

3.2 CONNECTIONS

A. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

B. Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

Retain one of three paragraphs below that identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second or third paragraph, retain requirement for field quality-control test reports in "Submittals" Article.

A. Testing Agency:  [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections and prepare test reports.

Retain paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.  Report results in writing.

Retain paragraph and subparagraph below to require Contractor to perform tests and inspections.

C. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph and subparagraph below to describe tests and inspections to be performed by any of the entities in three paragraphs above.

D. Tests and Inspections:

Tests referenced in subparagraph below are from NETA Acceptance Testing Specification and include inspection procedures to verify proper installation.  They also include tests and measurements of insulation resistance and turns ratios.  Cost of extensive testing may not be warranted for some projects.  Revise subparagraph to suit Project.

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

E. Remove and replace units that do not pass tests and inspections and retest as specified above.

F. Infrared Scanning:  Two months after Substantial Completion, perform an infrared scan of bus assembly including joints and plug-in units.

1. Use an infrared-scanning device designed to measure temperature or detect significant deviations from normal values.  Provide documentation of device calibration.

2. Perform 2 follow-up infrared scans of bus assembly, one at 4 months and the other at 11 months after Substantial Completion.

3. Prepare a certified report identifying bus assembly checked and describing results of scanning.  Include notation of deficiencies detected, remedial action taken, and scanning observations after remedial action.

G. Test Labeling:  On completion of satisfactory testing of each unit, attach a dated and signed "Satisfactory Test" label to tested component.

3.4 ADJUSTING

A. Set field-adjustable, circuit-breaker trip ranges[ and overload relay trip settings] as indicated.

3.5 CLEANING

A. Vacuum dirt and debris; do not use compressed air to assist in cleaning.

3.6 PROTECTION

A. Provide final protection to ensure that moisture does not enter bus assembly.

END OF SECTION 262500

	ENCLOSED BUS ASSEMBLIES
	262500 - 1



