Copyright 2004 and 2005 AIA
MASTERSPEC Full Length
06/04 (R 06/05)

Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262726 - WIRING DEVICES
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

1. Receptacles, receptacles with integral GFCI, and associated device plates.

2. Twist-locking receptacles.

3. Receptacles with integral surge suppression units.

4. Wall-box motion sensors.

5. Isolated-ground receptacles.

6. Hospital-grade receptacles.

7. Snap switches and wall-box dimmers.

8. Solid-state fan speed controls.

9. Wall-switch and exterior occupancy sensors.

10. Communications outlets.

11. Pendant cord-connector devices.

12. Cord and plug sets.

13. Floor service outlets, poke-through assemblies, service poles, and multioutlet assemblies.

B. Related Sections include the following:

List below only devices that the reader might expect to find in this Section but are specified elsewhere.

1. Division 27 Section "Communications Horizontal Cabling" for workstation outlets.

1.3 DEFINITIONS

Retain term and abbreviations that remain after this Section has been edited.

A. EMI:  Electromagnetic interference.

B. GFCI:  Ground-fault circuit interrupter.

C. Pigtail:  Short lead used to connect a device to a branch-circuit conductor.

D. RFI:  Radio-frequency interference.

E. TVSS:  Transient voltage surge suppressor.

F. UTP:  Unshielded twisted pair.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  List of legends and description of materials and process used for premarking wall plates.

Retain first paragraph below if products have critical features needing hands-on appraisal.

C. Samples:  One for each type of device and wall plate specified, in each color specified.

D. Field quality-control test reports.

E. Operation and Maintenance Data:  For wiring devices to include in all manufacturers' packing label warnings and instruction manuals that include labeling conditions.

1.5 QUALITY ASSURANCE

A. Source Limitations:  Obtain each type of wiring device and associated wall plate through one source from a single manufacturer.  Insofar as they are available, obtain all wiring devices and associated wall plates from a single manufacturer and one source.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with NFPA 70.

1.6 COORDINATION

Retain this Article if receptacles for Owner-furnished equipment with plugs have unknown or special configurations.

A. Receptacles for Owner-Furnished Equipment:  Match plug configurations.

Retain subparagraph below if cord and plug sets are specified in Part 2.

1. Cord and Plug Sets:  Match equipment requirements.

1.7 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described in subparagraphs below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

1. Service/Power Poles:  [One for every 10] <Insert quantities>, but no fewer than [one] <Insert quantities>.

2. Floor Service Outlet Assemblies:  [One for every 10] <Insert quantities>, but no fewer than [one] <Insert quantities>.

3. Poke-Through, Fire-Rated Closure Plugs:  [One for every five] <Insert quantities> floor service outlets installed, but no fewer than [two] <Insert quantities>.

4. TVSS Receptacles:  [One for every 10] <Insert quantities> of each type installed, but no fewer than [two of each type] <Insert quantities>.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Manufacturers' Names:  Shortened versions (shown in parentheses) of the following manufacturers' names are used in other Part 2 articles:

Manufacturers listed below produce an extensive line of nationally distributed wiring devices.  Add manufacturers if desired.

1. Cooper Wiring Devices; a division of Cooper Industries, Inc. (Cooper).

2. Hubbell Incorporated; Wiring Device-Kellems (Hubbell).

3. Leviton Mfg. Company Inc. (Leviton).

4. Pass & Seymour/Legrand; Wiring Devices & Accessories (Pass & Seymour).

5. <Insert manufacturer's name.>

2.2 STRAIGHT BLADE RECEPTACLES

A. Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

Catalog numbers in subparagraphs below are for 20-A devices; revise catalog numbers if 15-A devices are desired.

a. Cooper; 5351 (single), 5352 (duplex).

b. Hubbell; HBL5351 (single), CR5352 (duplex).

c. Leviton; 5891 (single), 5352 (duplex).

d. Pass & Seymour; 5381 (single), 5352 (duplex).

e. <Insert manufacturer's name; catalog numbers.>

B. Hospital-Grade, Duplex Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498 Supplement SD.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 8300 (duplex).

b. Hubbell; HBL8310 (single), HBL8300H (duplex).

c. Leviton; 8310 (single), 8300 (duplex).

d. Pass & Seymour; 9301-HG (single), 9300-HG (duplex).

e. <Insert manufacturer's name; catalog numbers.>

Isolated-ground receptacles are available in a variety of configurations and ratings including locking-blade types up to 50 A and 250 V.  Revise first paragraph and subparagraphs below to suit Project; indicate different types on Drawings.

C. Isolated-Ground, Duplex Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Hubbell; CR 5253IG.

b. Leviton; 5362-IG.

c. Pass & Seymour; IG6300.

d. <Insert manufacturer's name; catalog number.>

3. Description:  Straight blade; equipment grounding contacts shall be connected only to the green grounding screw terminal of the device and with inherent electrical isolation from mounting strap.  Isolation shall be integral to receptacle construction and not dependent on removable parts.

D. Tamper-Resistant Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; TR8300.

b. Hubbell; HBL8300SG.

c. Leviton; 8300-SGG.

d. Pass & Seymour; 63H.

e. <Insert manufacturer's name; catalog number.>

3. Description:  Labeled to comply with NFPA 70, "Health Care Facilities" Article, "Pediatric Locations" Section.

2.3 GFCI RECEPTACLES

Non-feed-through-type GFCI unit may be selected where no protection of downstream receptacles is required.

A. General Description:  Straight blade, [feed] [non-feed]-through type.  Comply with NEMA WD 1, NEMA WD 6, UL 498, and UL 943, Class A, and include indicator light that is lighted when device is tripped.

B. Duplex GFCI Convenience Receptacles, 125 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

Catalog numbers in subparagraphs below are for feed-through types, arranged to protect receptacles downstream on the same circuit; revise catalog numbers if non-feed-through types are required.

a. Cooper; GF20.

b. Pass & Seymour; 2084.

c. <Insert manufacturer's name; catalog number.>

C. Hospital-Grade, Duplex GFCI Convenience Receptacles, 125 V, 20 A:  Comply with UL 498 Supplement SD.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; HGF20.

b. Hubbell; HGF8300.

c. Leviton; 6898-HG.

d. Pass & Seymour; 2091-SHG.

e. <Insert manufacturer's name; catalog number.>

2.4 TVSS RECEPTACLES

See Editing Instruction No. 3 in the Evaluations for information on TVSS ratings.

A. General Description:  Comply with NEMA WD 1, NEMA WD 6, UL 498, and UL 1449, with integral TVSS in line to ground, line to neutral, and neutral to ground.

1. TVSS Components:  Multiple metal-oxide varistors; with a nominal clamp-level rating of 400 volts and minimum single transient pulse energy dissipation of 240 J, according to IEEE C62.41.2 and IEEE C62.45.

2. Active TVSS Indication:  Visual and audible, with light visible in face of device to indicate device is "active" or "no longer in service."

B. Duplex TVSS Convenience Receptacles:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

Catalog numbers in first three subparagraphs below are for products with visual-only indication.

a. Cooper; 5362BLS.

b. Hubbell; HBL5362SA.

c. Leviton; 5380.

d. <Insert manufacturer's name; catalog number.>

3. Description:  Straight blade, 125 V, 20 A; NEMA WD 6 configuration 5-20R.

C. Isolated-Ground, Duplex Convenience Receptacles:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; IG5362BLS.

b. Hubbell; IG5362SA.

c. Leviton; 5380-IG.

d. <Insert manufacturer's name; catalog number.>

3. Description:  Straight blade, 125 V, 20 A; NEMA WD 6 configuration 5-20R.  Equipment grounding contacts shall be connected only to the green grounding screw terminal of the device and with inherent electrical isolation from mounting strap.  Isolation shall be integral to receptacle construction and not dependent on removable parts.

D. Hospital-Grade, Duplex Convenience Receptacles:  Comply with UL 498 Supplement SD.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 8300BLS.

b. Hubbell; HBL8362SA.

c. Leviton; 8380.

d. <Insert manufacturer's name; catalog number.>

3. Description:  Straight blade, 125 V, 20 A; NEMA WD 6 configuration 5-20R.

E. Isolated-Ground, Hospital-Grade, Duplex Convenience Receptacles:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; IG8300HGBLS.

b. Hubbell; IG8362SA.

c. Leviton; 8380-IG.

d. <Insert manufacturer's name; catalog number.>

3. Description:  Straight blade, 125 V, 20 A; NEMA WD 6 configuration 5-20R.  Comply with UL 498 Supplement SD.  Equipment grounding contacts shall be connected only to the green grounding screw terminal of the device and with inherent electrical isolation from mounting strap.  Isolation shall be integral to receptacle construction and not dependent on removable parts.

2.5 HAZARDOUS (CLASSIFIED) LOCATION RECEPTACLES

A. [Available ]Wiring Devices for Hazardous (Classified) Locations:  Comply with NEMA FB 11 and UL 1010.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Cooper Crouse-Hinds.

b. EGS/Appleton Electric.

c. Killark; a division of Hubbell Inc.

d. <Insert manufacturer's name.>

2.6 TWIST-LOCKING RECEPTACLES

A. Single Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration L5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; L520R.

b. Hubbell; HBL2310.

c. Leviton; 2310.

d. Pass & Seymour; L520-R.

e. <Insert manufacturer's name; catalog number.>

B. Isolated-Ground, Single Convenience Receptacles, 125 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Hubbell; IG2310.

b. Leviton; 2310-IG.

c. <Insert manufacturer's name; catalog number.>

3. Description:  Comply with NEMA WD 1, NEMA WD 6 configuration L5-20R, and UL 498.  Equipment grounding contacts shall be connected only to the green grounding screw terminal of the device and with inherent electrical isolation from mounting strap.  Isolation shall be integral to receptacle construction and not dependent on removable parts.

2.7 PENDANT CORD-CONNECTOR DEVICES

Revise NEMA configuration in paragraph below to suit Project.  Delete "External Cable Grip" Subparagraph if not required.

A. Description:  Matching, locking-type plug and receptacle body connector; NEMA WD 6 configurations L5-20P and L5-20R, heavy-duty grade.

1. Body:  Nylon with screw-open cable-gripping jaws and provision for attaching external cable grip.

2. External Cable Grip:  Woven wire-mesh type made of high-strength galvanized-steel wire strand, matched to cable diameter, and with attachment provision designed for corresponding connector.

2.8 CORD AND PLUG SETS

Retain this Article if cord and plug sets for equipment are furnished by Owner or are specified in other Sections.  Coordinate with other Sections and with Part 3.

A. Description:  Match voltage and current ratings and number of conductors to requirements of equipment being connected.

1. Cord:  Rubber-insulated, stranded-copper conductors, with Type SOW-A jacket; with green-insulated grounding conductor and equipment-rating ampacity plus a minimum of 30 percent.

2. Plug:  Nylon body and integral cable-clamping jaws.  Match cord and receptacle type for connection.

2.9 SNAP SWITCHES

A. Comply with NEMA WD 1 and UL 20.

B. Switches, 120/277 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

Catalog numbers in subparagraphs below are for 20-A devices; revise catalog numbers if 15-A devices are desired.

a. Cooper; 2221 (single pole), 2222 (two pole), 2223 (three way), 2224 (four way).

b. Hubbell; CS1221 (single pole), CS1222 (two pole), CS1223 (three way), CS1224 (four way).

c. Leviton; 1221-2 (single pole), 1222-2 (two pole), 1223-2 (three way), 1224-2 (four way).

d. Pass & Seymour; 20AC1 (single pole), 20AC2 (two pole), 20AC3 (three way), 20AC4 (four way).

e. <Insert manufacturer's name; catalog numbers.>

C. Pilot Light Switches, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 2221PL for 120 V and 277 V.

b. Hubbell; HPL1221PL for 120 V and 277 V.

c. Leviton; 1221-PLR for 120 V, 1221-7PLR for 277 V.

d. Pass & Seymour; PS20AC1-PLR for 120 V.

e. <Insert manufacturer's name; catalog numbers.>

3. Description:  Single pole, with neon-lighted handle, illuminated when switch is "ON."

D. Key-Operated Switches, 120/277 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 2221L.

b. Hubbell; HBL1221L.

c. Leviton; 1221-2L.

d. Pass & Seymour; PS20AC1-L.

e. <Insert manufacturer's name; catalog number.>

3. Description:  Single pole, with factory-supplied key in lieu of switch handle.

E. Single-Pole, Double-Throw, Momentary Contact, Center-Off Switches, 120/277 V, 20 A; for use with mechanically held lighting contactors.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 1995.

b. Hubbell; HBL1557.

c. Leviton; 1257.

d. Pass & Seymour; 1251.

e. <Insert manufacturer's name; catalog number.>

F. Key-Operated, Single-Pole, Double-Throw, Momentary Contact, Center-Off Switches, 120/277 V, 20 A; for use with mechanically held lighting contactors, with factory-supplied key in lieu of switch handle.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 1995L.

b. Hubbell; HBL1557L.

c. Leviton; 1257L.

d. Pass & Seymour; 1251L.

e. <Insert manufacturer's name; catalog number.>

2.10 WALL-BOX DIMMERS

A. Dimmer Switches:  Modular, full-wave, solid-state units with integral, quiet on-off switches, with audible frequency and EMI/RFI suppression filters.

Four-way switching may be added to first paragraph below after verifying availability with manufacturers.

B. Control:  Continuously adjustable [slider] [toggle switch] [rotary knob]; with single-pole or three-way switching.  Comply with UL 1472.

C. Incandescent Lamp Dimmers:  120 V; control shall follow square-law dimming curve.  On-off switch positions shall bypass dimmer module.

1. 600 W; dimmers shall require no derating when ganged with other devices.  [Illuminated when "OFF." ]

Retain subparagraph above or below.  If retaining below, insert other dimmers with their characteristics.  UL 1472 covers ratings from 300 W to 2000 W in increments of 50 W.

2. <Insert other wattage ratings and descriptions.>

Use fluorescent lamp dimmer switches in paragraph below with compatible dimming-type ballasts.  Coordinate with Division 26 Section "Interior Lighting."  Use uniform ballast and lamp types to obtain consistent dimming characteristics.

D. Fluorescent Lamp Dimmer Switches:  Modular; compatible with dimmer ballasts; trim potentiometer to adjust low-end dimming; dimmer-ballast combination capable of consistent dimming with low end not greater than 20 percent of full brightness.

2.11 FAN SPEED CONTROLS

A. Modular, 120-V, full-wave, solid-state units with integral, quiet on-off switches and audible frequency and EMI/RFI filters.  Comply with UL 1917.

The 5-A rating in first subparagraph below allows more than one fan to be controlled by the same device.

1. Continuously adjustable [slider] [toggle switch] [rotary knob], [5 A] [1.5 A].

2. Three-speed adjustable [slider] [rotary knob], 1.5 A.

2.12 OCCUPANCY SENSORS

Each manufacturer's switch rating is different, but rated design values are generally not less than 800-VA fluorescent at 120 V, 1200-VA fluorescent at 277 V, and 800-W incandescent.

Retain one of two paragraphs and associated subparagraphs below.  Adaptive technology includes the ability to sense and memorize usage patterns in the space and help eliminate false offs.

A. Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 6111 for 120 V, 6117 for 277 V.

b. Hubbell; WS1277.

c. Leviton; ODS 10-ID.

d. Pass & Seymour; WS3000.

e. Watt Stopper (The); WS-200.

f. <Insert manufacturer's name; catalog number(s).>

3. Description:  Passive-infrared type, 120/277 V, adjustable time delay up to 30 minutes, 180-degree field of view, with a minimum coverage area of 900 sq. ft. (84 sq. m).

B. Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Hubbell; AT120 for 120 V, AT277 for 277 V.

b. Leviton; ODS 15-ID.

c. <Insert manufacturer's name; catalog number(s).>

3. Description:  Adaptive-technology type, 120/277 V, adjustable time delay up to 20 minutes, 180-degree field of view, with a minimum coverage area of 900 sq. ft. (84 sq. m).

Retain one of first two paragraphs and associated subparagraphs below for square and near-square rectangular rooms.

C. Long-Range Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Hubbell; ATP1600WRP.

b. Leviton; ODWWV-IRW.

c. Pass & Seymour; WA1001.

d. Watt Stopper (The); CX-100.

e. <Insert manufacturer's name; catalog number.>

3. Description:  Passive-infrared type, 120/277 V, adjustable time delay up to 30 minutes, 110-degree field of view, with a minimum coverage area of 1200 sq. ft. (111 sq. m).

D. Long-Range Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Hubbell; ATD1600WRP.

b. Leviton; ODW12-MRW.

c. Watt Stopper (The); DT-200.

d. <Insert manufacturer's name; catalog number.>

3. Description:  Dual technology, with both passive-infrared- and ultrasonic-type sensing, 120/277 V, adjustable time delay up to 30 minutes, 110-degree field of view, and a minimum coverage area of 1200 sq. ft. (111 sq. m).

E. Wide-Range Wall-Switch Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Hubbell; ATP120HBRP.

b. Leviton; ODWHB-IRW.

c. Pass & Seymour; HS1001.

d. Watt Stopper (The); CX-100-3.

e. <Insert manufacturer's name; catalog number.>

3. Description:  Passive-infrared type, 120/277 V, adjustable time delay up to 30 minutes, 150-degree field of view, with a minimum coverage area of 1200 sq. ft. (111 sq. m).

F. Exterior Occupancy Sensors:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Leviton; PS200-10.

b. Watt Stopper (The); EW-100-120.

c. <Insert manufacturer's name; catalog number.>

3. Description:  Passive-infrared type, 120/277 V, weatherproof, adjustable time delay up to 15 minutes, 180-degree field of view, and 110-foot (34-m) detection range.  Minimum switch rating:  1000-W incandescent, 500-VA fluorescent.

2.13 COMMUNICATIONS OUTLETS

A. Telephone Outlet:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 3560-6.

b. Leviton; 40649.

c. <Insert manufacturer's name; catalog number.>

3. Description:  Single RJ-45 jack for terminating 100-ohm, balanced, four-pair UTP; TIA/EIA-568-B.1; complying with Category 5e.  Comply with UL 1863.

B. Combination TV and Telephone Outlet:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Cooper; 3562.

b. Leviton; 40595.

c. <Insert manufacturer's name; catalog number.>

3. Description:  Single RJ-45 jack for 100-ohm, balanced, four-pair UTP; TIA/EIA-568-B.1; complying with Category 5e; and one Type F coaxial cable connector.

2.14 WALL PLATES

A. Single and combination types to match corresponding wiring devices.

1. Plate-Securing Screws:  Metal with head color to match plate finish.

2. Material for Finished Spaces:  [Steel with white baked enamel, suitable for field painting] [Smooth, high-impact thermoplastic] [0.035-inch- (1-mm-) thick, satin-finished stainless steel] [0.04-inch- (1-mm-) thick, brushed brass with factory polymer finish] [0.05-inch- (1.2-mm-) thick anodized aluminum] [0.04-inch- (1-mm-) thick steel with chrome-plated finish].

3. Material for Unfinished Spaces:  [Galvanized steel] [Smooth, high-impact thermoplastic].

4. Material for Damp Locations:  [Thermoplastic] [Cast aluminum] with spring-loaded lift cover, and listed and labeled for use in "wet locations."

B. Wet-Location, Weatherproof Cover Plates:  NEMA 250, complying with type 3R weather-resistant [, die-cast aluminum] [thermoplastic] with lockable cover.

2.15 FLOOR SERVICE FITTINGS

Service fittings in first paragraph below are available for voice and data communication cabling as well as for power.  Edit to suit Project.

A. Type:  Modular, [flush-type] [flap-type] [above-floor], dual-service units suitable for wiring method used.

B. Compartments:  Barrier separates power from voice and data communication cabling.

C. Service Plate:  [Rectangular] [Round], [die-cast aluminum] [solid brass] with satin finish.

D. Power Receptacle:  NEMA WD 6 configuration 5-20R, gray finish, unless otherwise indicated.

E. Voice and Data Communication Outlet:  [Blank cover with bushed cable opening] [Two modular, keyed, color-coded, RJ-45 Category 5e jacks for UTP cable].

2.16 POKE-THROUGH ASSEMBLIES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Hubbell Incorporated; Wiring Device-Kellems.

2. Pass & Seymour/Legrand; Wiring Devices & Accessories.

3. Square D/ Schneider Electric.

4. Thomas & Betts Corporation.

5. Wiremold Company (The).

6. <Insert manufacturer's name.>

C. Description:  Factory-fabricated and -wired assembly of below-floor junction box with multichanneled, through-floor raceway/firestop unit and detachable matching floor service outlet assembly.

Coordinate subparagraph below with Division 27 Section "Communications Horizontal Cabling."

1. Service Outlet Assembly:  [Pedestal type with services indicated] [Flush type with two simplex receptacles and space for two RJ-45 jacks] [Flush type with four simplex receptacles and space for four RJ-45 jacks].

Larger diameter assembly in subparagraph below is available for four simplex receptacles and four voice and data communication outlets in a single, flush-type service outlet.

2. Size:  Selected to fit nominal [3-inch (75-mm)] [4-inch (100-mm)] cored holes in floor and matched to floor thickness.

Revise first subparagraph below to coordinate with fire ratings.

3. Fire Rating:  Unit is listed and labeled for fire rating of floor-ceiling assembly.

4. Closure Plug:  Arranged to close unused [3-inch (75-mm)] [4-inch (100-mm)] cored openings and reestablish fire rating of floor.

Coordinate subparagraph below with Division 27 Section "Communications Horizontal Cabling."

5. Wiring Raceways and Compartments:  For a minimum of four No. 12 AWG conductors and a minimum of [two] [four], 4-pair, Category 5e voice and data communication cables.

2.17 MULTIOUTLET ASSEMBLIES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Hubbell Incorporated; Wiring Device-Kellems.

2. Wiremold Company (The).

3. <Insert manufacturer's name.>

If not indicated on Drawings, add mounting heights, raceway sizes, and types and spacing of receptacle devices to paragraph below.  Add descriptions of special features in assemblies such as fused receptacles, special-purpose switches, and channels for communication wiring.

C. Components of Assemblies:  Products from a single manufacturer designed for use as a complete, matching assembly of raceways and receptacles.

Some finish options may be available from manufacturers.  Select one of two paragraphs below and edit to suit Project.

D. Raceway Material:  [Metal, with manufacturer's standard finish] [PVC].

E. Wire:  No. 12 AWG.

2.18 SERVICE POLES

A. Description:  Factory-assembled and -wired units to extend power and voice and data communication from distribution wiring concealed in ceiling to devices or outlets in pole near floor.

1. Poles:  Nominal 2.5-inch- (65-mm-) square cross section, with height adequate to extend from floor to at least 6 inches (150 mm) above ceiling, and with separate channels for power wiring and voice and data communication cabling.

2. Mounting:  Ceiling trim flange with concealed bracing arranged for positive connection to ceiling supports; with pole foot and carpet pad attachment.

Specify final finish in first subparagraph below if known.

3. Finishes:  [Manufacturer's standard painted finish and trim combination] [Satin-anodized aluminum].

4. Wiring:  Sized for minimum of five No. 12 AWG power and ground conductors and a minimum of four, 4-pair, Category 3 or 5 voice and data communication cables.

5. Power Receptacles:  Two duplex, 20-A, heavy-duty, NEMA WD 6 configuration 5-20R units.

Coordinate subparagraph below with Division 27 Section "Communications Horizontal Cabling."

6. Voice and Data Communication Outlets:  [Blank insert with bushed cable opening] [Two RJ-45 Category 5e jacks] [Four RJ-45 Category 5e jacks].

2.19 FINISHES

See Editing Instruction No. 2 in the Evaluations for a discussion of wiring device colors.  Coordinate with Drawings.

A. Color:  Wiring device catalog numbers in Section Text do not designate device color.

1. Wiring Devices Connected to Normal Power System:  [Almond] [Black] [Brown] [Gray] [Ivory] [White] [As selected by Architect] <Insert color>, unless otherwise indicated or required by NFPA 70 or device listing.

Delete first subparagraph below and edit paragraph and subparagraph above if a separate emergency power system serving wiring devices is not provided.

2. Wiring Devices Connected to Emergency Power System:  [Red] <Insert color>.

3. TVSS Devices:  Blue.

4. Isolated-Ground Receptacles:  [Orange] [As specified above, with orange triangle on face].

PART 3 -  EXECUTION

3.1 INSTALLATION

NECA 1 referenced in paragraph below includes device mounting-height requirements.  See "Product Selection and Application Considerations" Article in the Evaluations for device mounting heights in that standard.

A. Comply with NECA 1, including the mounting heights listed in that standard, unless otherwise noted.

See Editing Instruction No. 4 in the Evaluations for timing and sequencing of construction to assist in avoiding contamination of devices during construction.

B. Coordination with Other Trades:

1. Take steps to insure that devices and their boxes are protected.  Do not place wall finish materials over device boxes and do not cut holes for boxes with routers that are guided by riding against outside of the boxes.

2. Keep outlet boxes free of plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other material that may contaminate the raceway system, conductors, and cables.

3. Install device boxes in brick or block walls so that the cover plate does not cross a joint unless the joint is troweled flush with the face of the wall.

4. Install wiring devices after all wall preparation, including painting, is complete.

C. Conductors:

1. Do not strip insulation from conductors until just before they are spliced or terminated on devices.

2. Strip insulation evenly around the conductor using tools designed for the purpose.  Avoid scoring or nicking of solid wire or cutting strands from stranded wire.

3. The length of free conductors at outlets for devices shall meet provisions of NFPA 70, Article 300, without pigtails.

4. Existing Conductors:

a. Cut back and pigtail, or replace all damaged conductors.

b. Straighten conductors that remain and remove corrosion and foreign matter.

c. Pigtailing existing conductors is permitted provided the outlet box is large enough.

D. Device Installation:

1. Replace all devices that have been in temporary use during construction or that show signs that they were installed before building finishing operations were complete.

2. Keep each wiring device in its package or otherwise protected until it is time to connect conductors.

3. Do not remove surface protection, such as plastic film and smudge covers, until the last possible moment.

4. Connect devices to branch circuits using pigtails that are not less than 6 inches (152 mm) in length.

5. When there is a choice, use side wiring with binding-head screw terminals.  Wrap solid conductor tightly clockwise, 2/3 to 3/4 of the way around terminal screw.

6. Use a torque screwdriver when a torque is recommended or required by the manufacturer.

7. When conductors larger than No. 12 AWG are installed on 15- or 20-A circuits, splice No. 12 AWG pigtails for device connections.

8. Tighten unused terminal screws on the device.

9. When mounting into metal boxes, remove the fiber or plastic washers used to hold device mounting screws in yokes, allowing metal-to-metal contact.

E. Receptacle Orientation:

Retain subparagraph below if the position of the ground pin is important for consistency.  Trade and professional literature is inconsistent in recommending benefits of either orientation.

1. Install ground pin of vertically mounted receptacles [up] [down], and on horizontally mounted receptacles to the [right] [left].

Recommendation in subparagraph below is made in IEEE 602.

2. Install hospital-grade receptacles in patient-care areas with the ground pin or neutral blade at the top.

F. Device Plates:  Do not use oversized or extra-deep plates.  Repair wall finishes and remount outlet boxes when standard device plates do not fit flush or do not cover rough wall opening.

G. Dimmers:

1. Install dimmers within terms of their listing.

2. Verify that dimmers used for fan speed control are listed for that application.

3. Install unshared neutral conductors on line and load side of dimmers according to manufacturers' device listing conditions in the written instructions.

Coordinate two paragraphs below with Drawings.

H. Arrangement of Devices:  Unless otherwise indicated, mount flush, with long dimension vertical and with grounding terminal of receptacles on top.  Group adjacent switches under single, multigang wall plates.

I. Adjust locations of floor service outlets and service poles to suit arrangement of partitions and furnishings.

3.2 IDENTIFICATION

A. Comply with Division 26 Section "Identification for Electrical Systems."

1. Receptacles:  Identify panelboard and circuit number from which served.  Use hot, stamped or engraved machine printing with [black] [white] [red]-filled lettering on face of plate, and durable wire markers or tags inside outlet boxes.

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

1. In healthcare facilities, prepare reports that comply with recommendations in NFPA 99.

2. Test Instruments:  Use instruments that comply with UL 1436.

3. Test Instrument for Convenience Receptacles:  Digital wiring analyzer with digital readout or illuminated LED indicators of measurement.

B. Tests for Convenience Receptacles:

1. Line Voltage:  Acceptable range is 105 to 132 V.

2. Percent Voltage Drop under 15-A Load:  A value of 6 percent or higher is not acceptable.

3. Ground Impedance:  Values of up to 2 ohms are acceptable.

4. GFCI Trip:  Test for tripping values specified in UL 1436 and UL 943.

5. Using the test plug, verify that the device and its outlet box are securely mounted.

6. The tests shall be diagnostic, indicating damaged conductors, high resistance at the circuit breaker, poor connections, inadequate fault current path, defective devices, or similar problems.  Correct circuit conditions, remove malfunctioning units and replace with new ones, and retest as specified above.

C. Test straight blade [convenience outlets in patient-care areas] [hospital-grade convenience outlets] for the retention force of the grounding blade according to NFPA 99.  Retention force shall be not less than 4 oz. (115 g).

END OF SECTION 262726

	WIRING DEVICES
	262726 - 1



