Copyright 2002 and 2005 AIA
MASTERSPEC Full Length
06/02 (R 06/05)

Copyright 2002 and 2005 (R 12/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262913 - ENCLOSED CONTROLLERS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes ac, enclosed controllers rated 600 V and less, of the following types:

Adjust list below to suit Project.

1. Across-the-line, manual and magnetic controllers.

2. Reduced-voltage controllers.

3. Multispeed controllers.

4. Variable frequency controllers for small motor applications.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 26 Section "Electrical Power Monitoring and Control" for interfacing communication and metering requirements.

2. Division 26 Section "Variable-Frequency Motor Controllers" for general-purpose, ac, adjustable-frequency, pulse-width-modulated controllers for use on constant torque loads in ranges up to 200 hp.

3. Division 26 Section "Transient-Voltage Suppression for Low-Voltage Electrical Power Circuits" for low-voltage power, control, and communication surge suppressors.

1.3 SUBMITTALS

A. Product Data:  For each type of enclosed controller.  Include dimensions and manufacturer's technical data on features, performance, electrical characteristics, ratings, and finishes.

B. Shop Drawings:  For each enclosed controller.

1. Include dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

a. Each installed unit's type and details.

b. Nameplate legends.

c. Short-circuit current rating of integrated unit.

Retain subparagraph below if series rating of overcurrent protective devices is used or if combination controllers are used.

d. Listed and labeled for series rating of overcurrent protective devices in combination controllers by an NRTL acceptable to authorities having jurisdiction.

Retain first subparagraph below if combination controllers are used.

e. Features, characteristics, ratings, and factory settings of individual overcurrent protective devices in combination controllers.

2. Wiring Diagrams:  Power, signal, and control wiring.

Delete paragraph below if enclosed controllers are small wall-mounting units.  For large floor-mounting units, retain and revise to suit Project.

C. Coordination Drawings:  Floor plans, drawn to scale, showing dimensioned layout, required working clearances, and required area above and around enclosed controllers where pipe and ducts are prohibited.  Show enclosed controller layout and relationships between electrical components and adjacent structural and mechanical elements.  Show support locations, type of support, and weight on each support.  Indicate field measurements.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

D. Manufacturer Seismic Qualification Certification:  Submit certification that enclosed controllers, accessories, and components will withstand seismic forces defined in Division 26 Section "Vibration and Seismic Controls for Electrical Systems" Include the following:

1. Basis for Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project.  Definition varies with type of building and occupancy and is critical to valid certification.  Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For [manufacturer] [testing agency] [manufacturer and testing agency].

Retain first paragraph below if Contractor is responsible for field quality-control testing.

F. Field quality-control test reports.

G. Operation and Maintenance Data:  For enclosed controllers to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

1. Routine maintenance requirements for enclosed controllers and all installed components.

Retain subparagraph below if circuit breakers are used in combination controllers or as individual units.

2. Manufacturer's written instructions for testing and adjusting overcurrent protective devices.

Coordinate two paragraphs below with Parts 2 and 3.  See Editing Instruction No. 3 in the Evaluations.

H. Load-Current and Overload-Relay Heater List:  Compile after motors have been installed and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents.

Retain paragraph above or below to suit type of motor running overload protection specified in Part 2.  See Evaluations for discussion of types of overload protection.

I. Load-Current and List of Settings of Adjustable Overload Relays:  Compile after motors have been installed and arrange to demonstrate that dip switch settings for motor running overload protection suit actual motor to be protected.

1.4 QUALITY ASSURANCE

Retain paragraph below if solid-state controllers are specified.

A. Manufacturer Qualifications:  A qualified manufacturer.  Maintain, within 100 miles (160 km) of Project site, a service center capable of providing training, parts, and emergency maintenance and repairs.

If an independent testing agency is required, see Division 01 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, retain first paragraph below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and subparagraph below if Contractor selects testing agency.

B. Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

1. Testing Agency's Field Supervisor:  Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

C. Source Limitations:  Obtain enclosed controllers of a single type through one source from a single manufacturer.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

E. Comply with NFPA 70.

Retain paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Delete if controllers are small and wall mounted and space is not a concern.

F. Product Selection for Restricted Space:  Drawings indicate maximum dimensions for enclosed controllers, minimum clearances between enclosed controllers, and for adjacent surfaces and other items.  Comply with indicated maximum dimensions and clearances.

1.5 DELIVERY, STORAGE, AND HANDLING

For large controllers, retain both paragraphs below; delete second paragraph if indoor space is likely to be available at Project site.

A. Store enclosed controllers indoors in clean, dry space with uniform temperature to prevent condensation.  Protect enclosed controllers from exposure to dirt, fumes, water, corrosive substances, and physical damage.

B. If stored in areas subject to weather, cover enclosed controllers to protect them from weather, dirt, dust, corrosive substances, and physical damage.  Remove loose packing and flammable materials from inside controllers; install electric heating of sufficient wattage to prevent condensation.

1.6 PROJECT CONDITIONS

Retain this Article if interruption of existing electrical service is required.

A. Interruption of Existing Electrical Service:  Do not interrupt electrical service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electrical service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of electrical service.

2. Indicate method of providing temporary utilities.

3. Do not proceed with interruption of electrical service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.7 COORDINATION

A. Coordinate layout and installation of enclosed controllers with other construction including conduit, piping, equipment, and adjacent surfaces.  Maintain required workspace clearances and required clearances for equipment access doors and panels.

Retain one or both paragraphs below if required for base-supported enclosed controllers.

B. Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 03 Section "Cast-in-Place Concrete."

C. Coordinate installation of roof curbs, equipment supports, and roof penetrations.  These items are specified in Division 07 Section "Roof Accessories."

Revise two paragraphs below to refer to other Divisions, such as Division 14 for conveyor systems, if control coordination is required.

D. Coordinate features of enclosed controllers and accessory devices with pilot devices and control circuits to which they connect.

E. Coordinate features, accessories, and functions of each enclosed controller with ratings and characteristics of supply circuit, motor, required control sequence, and duty cycle of motor and load.

1.8 EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

A. Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Spare Fuses:  Furnish one spare for every [five] <Insert number> installed, but no fewer than one set of [three] <Insert number> of each type and rating.

2. Indicating Lights:  [Two] <Insert number> of each type installed.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. ABB Power Distribution, Inc.; ABB Control, Inc. Subsidiary.

2. Danfoss Inc.; Danfoss Electronic Drives Div.

3. Eaton Corporation; Cutler-Hammer Products.

4. General Electrical Company; GE Industrial Systems.

5. Rockwell Automation; Allen-Bradley Co.; Industrial Control Group.

6. Siemens/Furnas Controls.

7. Square D.

8. <Insert manufacturer's name.>

2.2 ACROSS-THE-LINE ENCLOSED CONTROLLERS

A. Manual Controller:  NEMA ICS 2, general purpose, Class A, with "quick-make, quick-break" toggle or pushbutton action, and marked to show whether unit is "OFF," "ON," or "TRIPPED."

1. Overload Relay:  Ambient-compensated type with inverse-time-current characteristics and NEMA ICS 2, Class 10 tripping characteristics.  Relays shall have heaters and sensors in each phase, matched to nameplate, full-load current of specific motor to which they connect and shall have appropriate adjustment for duty cycle.

Coordinate paragraph and subparagraphs below with Drawings.

B. Magnetic Controller:  NEMA ICS 2, Class A, full voltage, nonreversing, across the line, unless otherwise indicated.

1. Control Circuit:  120 V; obtained from [integral control power transformer] <Insert source of control power> with a control power [transformer] [source] of sufficient capacity to operate connected pilot, indicating and control devices, plus 100 percent spare capacity.

Select trip class from options in two subparagraphs below.  See Evaluations for discussion.

2. Overload Relay:  Ambient-compensated type with inverse-time-current characteristic and NEMA ICS 2, Class [10] [20] [30] tripping characteristic.  Provide with heaters or sensors in each phase matched to nameplate full-load current of specific motor to which they connect and with appropriate adjustment for duty cycle.

Retain subparagraph above or below.

3. Adjustable Overload Relay:  Dip switch selectable for motor running overload protection with NEMA ICS 2, Class [10] [20] [30] tripping characteristic, and selected to protect motor against voltage and current unbalance and single phasing.  Provide relay with Class II ground-fault protection, with start and run delays to prevent nuisance trip on starting.

Indicate requirements for overcurrent protective devices on Drawings.  Revise paragraph and subparagraphs below if overload relays differ from those indicated for magnetic controllers in subparagraphs above.

C. Combination Magnetic Controller:  Factory-assembled combination controller and disconnect switch.

1. Fusible Disconnecting Means:  NEMA KS 1, heavy-duty, fusible switch with rejection-type fuse clips rated for fuses.  Select and size fuses to provide Type 2 protection according to IEC 947-4-1, as certified by an NRTL.

2. Nonfusible Disconnecting Means:  NEMA KS 1, heavy-duty, nonfusible switch.

3. Circuit-Breaker Disconnecting Means:  NEMA AB 1, motor-circuit protector with field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

2.3 REDUCED-VOLTAGE ENCLOSED CONTROLLERS

Revise controller specifications in this Article to suit Project.  Delete types below if not used.  Coordinate with Drawings.  See Evaluations for selection considerations.

A. Star-Delta Controller:  NEMA ICS 2, closed transition with adjustable time delay.

B. Part-Winding Controller:  NEMA ICS 2, closed transition with separate overload relays for starting and running sequences.

C. Autotransformer Reduced-Voltage Controller:  NEMA ICS 2, closed transition.

D. Solid-State, Reduced-Voltage Controller:  NEMA ICS 2, suitable for use with NEMA MG 1, Design B, polyphase, medium induction motors.

1. Adjustable acceleration rate control utilizing voltage or current ramp, and adjustable starting torque control with up to 500 percent current limitation for 20 seconds.

2. Surge suppressor in solid-state power circuits providing 3-phase protection against damage from supply voltage surges 10 percent or more above nominal line voltage.

3. LED indicators showing motor and control status, including the following conditions:

a. Control power available.

b. Controller on.

c. Overload trip.

d. Loss of phase.

e. Shorted silicon-controlled rectifier.

Delete one or both subparagraphs below.  First item is an energy-conservation feature.  Coordinate with Drawings.

4. Automatic voltage-reduction controls to reduce voltage when motor is running at light load.

5. Motor running contactor operating automatically when full voltage is applied to motor.

2.4 MULTISPEED ENCLOSED CONTROLLERS

Coordinate this Article with Drawings.

A. Multispeed Enclosed Controller:  Match controller to motor type, application, and number of speeds; include the following accessories:

1. Compelling relay to ensure that motor will start only at low speed.

2. Accelerating relay to ensure properly timed acceleration through speeds lower than that selected.

3. Decelerating relay to ensure automatically timed deceleration through each speed.

2.5 VARIABLE FREQUENCY CONTROLLERS

Two paragraphs below provide a sample specification for this type of controller; revise to suit Project.  See Editing Instruction No. 2 in the Evaluations.

A. Description:  NEMA ICS 2, pulse-width-modulated, variable frequency controller; listed and labeled as a complete unit and arranged to provide variable speed of an NEMA MG 1, Design B, 3-phase, induction motor by adjusting output voltage and frequency.

B. Design and Rating:  Match load type such as fans, blowers, and pumps; and type of connection used between motor and load such as direct or through a power-transmission connection.

Retain paragraph below if isolation transformer is required.

C. Isolation Transformer:  Match transformer voltage ratings and capacity to system and motor voltages; and controller, motor, and load characteristics.

Retain one of three options in first paragraph below or revise ratings to suit Project.

D. Output Rating:  3-phase; 6 to [60 Hz, with voltage proportional to frequency throughout voltage range] [66 Hz, with torque constant as speed changes] [120 Hz, with horsepower constant throughout speed range].

E. Unit Operating Requirements:

Revise subparagraphs below to suit Project.

1. Input ac voltage tolerance of [208 V, plus or minus 5] [380 to 500 V, plus or minus 10] [525 to 575 V, plus or minus 10] percent.

2. Input frequency tolerance of 50/60 Hz, plus or minus 6 percent.

3. Minimum Efficiency:  96 percent at 60 Hz, full load.

4. Minimum Displacement Primary-Side Power Factor:  96 percent.

5. Overload Capability:  1.1 times the base load current for 60 seconds; 2.0 times the base load current for 3 seconds.

6. Starting Torque:  100 percent of rated torque or as indicated.

7. Speed Regulation:  Plus or minus 1 percent.

8. Ambient Temperature:  0 to 40 deg C.

F. Isolated control interface allows controller to follow control signal over an 11:1 speed range.

Retain one of two subparagraphs below with paragraph above.

1. Electrical Signal:  4 to 20 mA at 24 V.

2. Pneumatic Signal:  3 to 15 psig (20 to 104 kPa).

G. Internal Adjustability Capabilities:

1. Minimum Speed:  5 to 25 percent of maximum rpm.

2. Maximum Speed:  80 to 100 percent of maximum rpm.

3. Acceleration:  2 to a minimum of 22 seconds.

4. Deceleration:  2 to minimum of 22 seconds.

5. Current Limit:  50 to a minimum of 110 percent of maximum rating.

Retain first paragraph and subparagraphs below if applicable.  Coordinate with Drawings and control sequences.

H. Self-Protection and Reliability Features:

Retain subparagraphs below to suit Project.

1. Input transient protection by means of surge suppressors.

2. Under- and overvoltage trips; inverter overtemperature, overload, and overcurrent trips.

3. Motor Overload Relay:  Adjustable and capable of NEMA 250, Class [10] [20] [30] performance.

4. Notch filter to prevent operation of the controller-motor-load combination at a natural frequency of the combination.

5. Instantaneous line-to-line and line-to-ground overcurrent trips.

6. Loss-of-phase protection.

7. Reverse-phase protection.

8. Short-circuit protection.

9. Motor overtemperature fault.

I. Multiple-Motor Capability:  Controller suitable for service to multiple motors and having a separate overload relay and protection for each controlled motor.  Overload relay shall shut off controller and motors served by it when overload relay is tripped.

Retain one or both of first two paragraphs below to suit Project.

J. Automatic Reset/Restart:  Attempts three restarts after controller fault or on return of power after an interruption and before shutting down for manual reset or fault correction.  Restarting during deceleration shall not damage controller, motor, or load.

K. Power-Interruption Protection:  Prevents motor from re-energizing after a power interruption until motor has stopped.

L. Status Lights:  Door-mounted LED indicators shall indicate the following conditions:

1. Power on.

2. Run.

3. Overvoltage.

4. Line fault.

5. Overcurrent.

6. External fault.

M. Panel-Mounted Operator Station:  Start-stop and auto-manual selector switches with manual speed control potentiometer and elapsed time meter.

N. Indicating Devices:  Meters or digital readout devices and selector switch, mounted flush in controller door and connected to indicate controller output current, voltage, and frequency.

O. Manual Bypass:  Magnetic contactor arranged to safely transfer motor between controller output and bypass controller circuit when motor is at zero speed.  Controller-off-bypass selector switch sets mode, and indicator lights give indication of mode selected.

Retain paragraph above or below or delete both.  For large horsepower motors, consider using a reduced-voltage bypass controller instead of full-voltage controller below; revise to suit Project.

P. Bypass Controller:  NEMA ICS 2, full-voltage, nonreversing enclosed controller with across-the-line starting capability in manual-bypass mode.  Provide motor overload protection under both modes of operation with control logic that allows common start-stop capability in either mode.

Not all manufacturers offer all options in paragraph below.  Coordinate with manufacturers selected.

Q. Integral Disconnecting Means:  [NEMA AB 1, instantaneous-trip circuit breaker] [NEMA AB 1, molded-case switch] [NEMA KS 1, nonfusible switch] [NEMA KS 1, fusible switch] with lockable handle.

Retain paragraph above or below or delete both.

R. Isolating Switch:  Non-load-break switch arranged to isolate variable frequency controller and permit safe troubleshooting and testing, both energized and de-energized, while motor is operating in bypass mode.

If retaining paragraph below, consider adding Specifications for remote indicating devices.

S. Remote Indicating Circuit Terminals:  Mode selection, controller status, and controller fault.

2.6 ENCLOSURES

A. Description:  Flush- or surface-mounting cabinets as indicated.  NEMA 250, Type 1, unless otherwise indicated to comply with environmental conditions at installed location.

Delete items below if not applicable.  Add other Project-specific requirements.

1. Outdoor Locations:  NEMA 250, Type 3R.

2. Kitchen Areas:  NEMA 250, Type 4X, stainless steel.

3. Other Wet or Damp Indoor Locations:  NEMA 250, Type 4.

4. Hazardous Areas Indicated on Drawings:  NEMA 250, Type 7C.

2.7 ACCESSORIES

A. Devices shall be factory installed in controller enclosure, unless otherwise indicated.

Delete any remaining paragraphs and subparagraphs if not applicable.  Coordinate with Drawings.

B. Push-Button Stations, Pilot Lights, and Selector Switches:  NEMA ICS 2, heavy-duty type.

C. Stop and Lockout Push-Button Station:  Momentary-break, push-button station with a factory-applied hasp arranged so padlock can be used to lock push button in depressed position with control circuit open.

D. Control Relays:  Auxiliary and adjustable time-delay relays.

E. Elapsed Time Meters:  Heavy duty with digital readout in hours.

Select one of first two paragraphs and associated subparagraphs below; delete if metering is not required.

F. Meters:  Panel type, 2-1/2-inch (64-mm) minimum size with 90- or 120-degree scale and plus or minus 2 percent accuracy.  Where indicated, provide transfer device with an off position.  Meters shall indicate the following:

1. Ammeter:  Output current, with current sensors rated to suit application.

2. Voltmeter:  Output voltage.

3. Frequency Meter:  Output frequency.

G. Multifunction Digital-Metering Monitor:  Listed and labeled by an NRTL acceptable to authorities having jurisdiction, microprocessor-based unit suitable for three- or four-wire systems and with the following features:

1. Inputs from sensors or 5-A current-transformer secondaries, and potential terminals rated to 600 V.

2. Switch-selectable digital display of the following:

a. Phase Currents, Each Phase:  Plus or minus 1 percent.

b. Phase-to-Phase Voltages, Three Phase:  Plus or minus 1 percent.

c. Phase-to-Neutral Voltages, Three Phase:  Plus or minus 1 percent.

d. Three-Phase Real Power:  Plus or minus 2 percent.

e. Three-Phase Reactive Power:  Plus or minus 2 percent.

f. Power Factor:  Plus or minus 2 percent.

g. Frequency:  Plus or minus 0.5 percent.

h. Integrated Demand with Demand Interval Selectable from 5 to 60 Minutes:  Plus or minus 2 percent.

Retain first subparagraph below if required.

i. Accumulated energy, in megawatt hours (joules), plus or minus 2 percent; stored values unaffected by power outages for up to 72 hours.

3. Mounting:  Display and control unit flush or semiflush mounted in instrument compartment door.

H. Phase-Failure and Undervoltage Relays:  Solid-state sensing circuit with isolated output contacts for hard-wired connection.  Provide adjustable undervoltage setting.

Paragraph below provides one method of protecting against input circuit anomaly while bypass controller is on line.  Consider other methods of providing redundant control of motor loads served.  Features specified below are not standard with all manufacturers.

I. Current-Sensing, Phase-Failure Relays for Bypass Controllers:  Solid-state sensing circuit with isolated output contacts for hard-wired connection; arranged to operate on phase failure, phase reversal, current unbalance of from 30 to 40 percent, or loss of supply voltage; with adjustable response delay.

2.8 FACTORY FINISHES

Revise this Article to include custom colors.  Coordinate custom-color requirements with sample submittal requirements.

A. Finish:  Manufacturer's standard <Insert color> paint applied to factory-assembled and -tested enclosed controllers before shipping.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine areas and surfaces to receive enclosed controllers for compliance with requirements, installation tolerances, <Insert Project-specific conditions,> and other conditions affecting performance.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 APPLICATIONS

Delete this Article if controllers and control devices and their types and features are delineated on Drawings.

A. Select features of each enclosed controller to coordinate with ratings and characteristics of supply circuit and motor; required control sequence; duty cycle of motor, controller, and load; and configuration of pilot device and control circuit affecting controller functions.

B. Select horsepower rating of controllers to suit motor controlled.

3.3 INSTALLATION

Coordinate this Article with Drawings.

Coordinate mounting and anchoring of controllers with drawing details.  If drawing details are explicit, delete paragraph below.

A. For control equipment at walls, bolt units to wall or mount on lightweight structural-steel channels bolted to wall.  For controllers not at walls, provide freestanding racks complying with Division 26 Section "Hangers and Supports for Electrical Systems."

Retain paragraph below for floor-mounting equipment.

B. Install freestanding equipment on concrete bases.

Retain first paragraph below if seismic controls are Project requirement.  Coordinate with Drawings.

C. Comply with mounting and anchoring requirements specified in Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

D. Enclosed Controller Fuses:  Install fuses in each fusible switch.  Comply with requirements in Division 26 Section "Fuses."

3.4 CONCRETE BASES

Retain this Article for floor-mounting units.

A. Coordinate size and location of concrete bases.  Verify structural requirements with structural engineer.

B. Concrete base is specified in Division 26 Section "Hangers and Supports for Electrical Systems," and concrete materials and installation requirements are specified in Division 03.

3.5 IDENTIFICATION

A. Identify enclosed controller, components, and control wiring according to Division 26 Section "Identification for Electrical Systems."

3.6 CONTROL WIRING INSTALLATION

Retain this Article if applicable or if remote control or indication is not required.

A. Install wiring between enclosed controllers according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

B. Bundle, train, and support wiring in enclosures.

C. Connect hand-off-automatic switch and other automatic-control devices where applicable.

1. Connect selector switches to bypass only manual- and automatic-control devices that have no safety functions when switch is in hand position.

2. Connect selector switches with enclosed controller circuit in both hand and automatic positions for safety-type control devices such as low- and high-pressure cutouts, high-temperature cutouts, and motor overload protectors.

3.7 CONNECTIONS

Coordinate conduit installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Conduit installation requirements are specified in other Division 26 Sections.  Drawings indicate general arrangement of conduit, fittings, and specialties.

B. Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

3.8 FIELD QUALITY CONTROL

Retain paragraph and subparagraphs below to require Contractor to prepare enclosed controllers for manufacturer's field service technician and for acceptance testing.

A. Prepare for acceptance tests as follows:

1. Test insulation resistance for each enclosed controller element, bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

Retain paragraph and subparagraphs below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  For solid-state, variable frequency controllers and solid-state, reduced-voltage controllers, supervision by personnel familiar with equipment is important.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to perform the following:

1. Inspect controllers, wiring, components, connections, and equipment installation.[  Test and adjust controllers, components, and equipment.]

2. Assist in field testing of equipment[ including pretesting and adjusting of solid-state controllers].

3. Report results in writing.

Retain one of three paragraphs below.

C. Testing Agency:  Owner will engage a qualified testing and inspecting agency to perform field tests and inspections and prepare test reports.

D. Testing Agency:  Engage a qualified testing and inspecting agency to perform the following field tests and inspections and prepare test reports:

E. Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with either of last two paragraphs above.  Edit to suit Project.  Delete subparagraphs if testing will be performed by Owner-engaged testing and inspecting agency.  See Editing Instruction No. 3 in the Evaluations.

1. Perform each electrical test and visual and mechanical inspection, except optional tests, stated in NETA ATS, "[Motor Control - Motor Starters] [Motor Control - Adjustable Speed Drive Systems]."  Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

3.9 ADJUSTING

This Article assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use; delete if adjustable devices are not used.

A. Set field-adjustable switches and circuit-breaker trip ranges.

3.10 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain enclosed controllers.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 262913

	ENCLOSED CONTROLLERS
	262913 - 1



