Copyright 2002 and 2005 AIA
MASTERSPEC Full Length
12/02 (R 06/05)

Copyright 2002 and 2005, The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 264113 - LIGHTNING PROTECTION FOR STRUCTURES
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes lightning protection for [buildings] [building elements] [building site components].

1.3 DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

A. LPI:  Lightning Protection Institute.

B. NRTL:  National recognized testing laboratory.

1.4 SUBMITTALS

A. Product Data:  For air terminals and mounting accessories.

B. Shop Drawings:  Detail lightning protection system, including air-terminal locations, conductor routing and connections, and bonding and grounding provisions.  Include indications for use of raceway, data on how concealment requirements will be met, and calculations required by NFPA 780 for bonding of grounded and isolated metal bodies.

C. Qualification data for firms and persons specified in "Quality Assurance" Article to demonstrate their capabilities and experience.  Include data on listing or certification by an NRTL or LPI.

Retain first paragraph below for air terminals mounted on single-ply membrane roofing.

D. Certification, signed by Contractor, that roof adhesive for air terminals is approved by manufacturers of both the terminal assembly and the single-ply membrane roofing material.

E. Field inspection reports indicating compliance with specified requirements.

1.5 QUALITY ASSURANCE

A. Installer Qualifications:  Engage an experienced installer who is an NRTL or who is certified by LPI as a Master Installer/Designer.

B. Listing and Labeling:  As defined in NFPA 780, "Definitions" Article.

1.6 COORDINATION

A. Coordinate installation of lightning protection with installation of other building systems and components, including electrical wiring, supporting structures and building materials, metal bodies requiring bonding to lightning protection components, and building finishes.

B. Coordinate installation of air terminals attached to roof systems with roofing manufacturer and Installer.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 01 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Automatic Lightning Protection.

2. ERICO International Corporation.

3. Harger Lightning Protection, Inc.

4. Heary Bros. Lightning Protection Co. Inc.

5. Independent Protection Co.

6. Robbins Lightning Inc.

7. Thompson Lightning Protection, Inc.

8. <Insert manufacturer's name.>

2.2 LIGHTNING PROTECTION SYSTEM COMPONENTS

A. Comply with UL 96.

Select material classification of NFPA 780; see Table 2 in the Evaluations.  NFPA requires Class II air terminals to be solid.

See Editing Instruction No. 2 in the Evaluations.  Specified standards stipulate minimum size requirements for components, depending on selected metal and class of building.  If components larger than minimum size are desired, add appropriate requirements here.

B. Roof-Mounting Air Terminals:  NFPA Class [I] [II], [aluminum] [copper], [solid] [tubular], unless otherwise indicated.

Delete subparagraph below or revise to suit Project.

1. Single-Membrane, Roof-Mounting Air Terminals:  Designed for single-membrane roof materials.

C. Stack-Mounting Air Terminals:  [Stainless steel] [Solid copper] [Monel metal].

D. Ground Rods, Ground Loop Conductors, and Concrete-Encased Electrodes:  Comply with Division 26 Section "Grounding and Bonding for Electrical Systems" and with standards referenced in this Section.

PART 3 -  EXECUTION

3.1 INSTALLATION

Edit first paragraph below to indicate which standards apply.  Retain UL if UL Master Label or LPI certification is specified, and NFPA if the most stringent or comprehensive requirements are needed.

A. Install lightning protection components and systems according to [UL 96A] [ and NFPA 780].

B. Install conductors with direct paths from air terminals to ground connections.  Avoid sharp bends and narrow loops.

C. Conceal the following conductors:

Retain some or all of five subparagraphs below depending on degree of concealment desired for lightning protection components.  If deleting all five, there will be no restrictions on exposed conductors.

1. System conductors.

2. Down conductors.

3. Interior conductors.

4. Conductors within normal view from exterior locations at grade within 200 feet (60 m) of building.

5. Notify Architect at least 48 hours in advance of inspection before concealing lightning protection components.

Exothermic-welded connections are considered more permanent than crimped or bolted connections.  If exothermic-welded connections are desired, retain paragraph below.  Edit if single-ply membrane roofing is not used or if exothermic connections are only required in underground portions of system.

D. Cable Connections:  Use approved exothermic-welded connections for all conductor splices and connections between conductors and other components, except those above single-ply membrane roofing.

Retain paragraph below for single-ply membrane roofing.

E. Air Terminals on Single-Ply Membrane Roofing:  Comply with adhesive manufacturer's written instructions.

Delete two paragraphs and associated subparagraphs below if NFPA 780 compliance is specified; retain if specifying bonding requirements that exceed minimum UL 96A requirements.  See Editing Instruction No. 3 in the Evaluations.  Coordinate with Drawings for counterpoise requirements, if any.

F. Bond extremities of vertical metal bodies exceeding 60 feet (18 m) in length to lightning protection components.

G. A counterpoise installation based on requirements in Division 26 Section "Grounding and Bonding for Electrical Systems" may be used as a ground loop required by NFPA 780, provided counterpoise conductor meets or exceeds minimum requirements in NFPA 780.

1. Bond ground terminals to counterpoise conductor.

2. Bond grounded metal bodies on building within 12 feet (3.6 m) of ground to counterpoise conductor.

3. Bond grounded metal bodies on building within 12 feet (3.6 m) of roof to [counterpoise conductor] [interconnecting loop at eave level or above].

Delete paragraph below if building is electrically continuous steel-framed structure or if building is 60 feet (18 m) tall or less.  See NFPA 780 for other situations where below may be deleted.

H. Bond lightning protection components with intermediate-level interconnection loop conductors to grounded metal bodies of building at 60-foot (18-m) intervals.

3.2 CORROSION PROTECTION

A. Do not combine materials that can form an electrolytic couple that will accelerate corrosion in the presence of moisture unless moisture is permanently excluded from junction of such materials.

B. Use conductors with protective coatings where conditions would cause deterioration or corrosion of conductors.

3.3 FIELD QUALITY CONTROL

Edit this Article to specify inspections for UL Master Label or LPI certification.  See Evaluations.

Retain one of two paragraphs below.

A. UL Inspection:  Provide inspections as required to obtain a UL Master Label for system.

B. Provide an inspection by an inspector certified by LPI to obtain an LPI certification.

END OF SECTION 264113

	LIGHTNING PROTECTION FOR STRUCTURES
	264113 - 1



