Copyright 2005 AIA
MASTERSPEC Full Length
09/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 283112 - ZONED (DC LOOP) FIRE-ALARM SYSTEM
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Fire-alarm control unit.

2. Manual fire-alarm boxes.

3. System smoke detectors.

4. Nonsystem smoke detectors.

5. Heat detectors.

6. Notification appliances.

7. Magnetic door holders.

8. Remote annunciator.

9. Digital alarm communicator transmitter.

10. Radio alarm transmitter.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.  Definitions in NFPA 72 apply to fire-alarm terms used in this Section.

A. LED:  Light-emitting diode.

B. NICET:  National Institute for Certification in Engineering Technologies.

1.4 SYSTEM DESCRIPTION

Description in this article is an example only; revise to suit Project.

A. Noncoded system, dedicated to fire-alarm service only.

1.5 SUBMITTALS

A. General Submittal Requirements:

Retain first subparagraph below if a fire-alarm construction permit is required prior to the Work of this Section and the permit is issued by authorities having jurisdiction after the review and approval of Shop Drawings.

1. Submittals shall be approved by authorities having jurisdiction prior to submitting them to Architect.

See Editing Instruction No. 2 in the Evaluations for discussion about qualifications for system design and installation.  Coordinate subparagraph below with "Quality Assurance" Article.

2. Shop Drawings shall be prepared by persons with the following qualifications:

a. Trained and certified by manufacturer in fire-alarm system design.

b. NICET-certified fire-alarm technician, [Level III] [Level IV] minimum.

Retain subparagraph below if authorities having jurisdiction have licensing requirements.

c. Licensed or certified by authorities having jurisdiction.

First two paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

B. Product Data:  For each type of product indicated.

C. Shop Drawings:  For fire-alarm system.  Include plans, elevations, sections, details, and attachments to other work.

1. Comply with recommendations in the "Documentation" Section of the "Fundamentals of Fire Alarm Systems" Chapter in NFPA 72.

2. Include voltage drop calculations for notification appliance circuits.

3. Include battery size calculations.

4. Include performance parameters and installation details for each detector, verifying that each detector is listed for the complete range of air velocity, temperature, and humidity possible when air-handling system is operating.

5. Include plans, sections, and elevations of heating, ventilating, and air-conditioning ducts, drawn to scale and coordinating installation of duct smoke detectors and access to them.  Show critical dimensions that relate to placement and support of sampling tubes, detector housing, and remote status and alarm indicators.  Locate detectors according to manufacturer's written recommendations.

Retain subparagraph below for projects where routing of cable or conduit is critical and only outlet locations are shown on Drawings.

6. Include floor plans to indicate final outlet locations showing zone designation of each device.  Show size and route of cable and conduits.

First paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain if detector locations are not shown on Drawings.  Coordinate with "Quality Assurance" and "Equipment Installation" articles.  See Editing Instruction No. 7 in the Evaluations for discussion about detector locations. Professional engineer qualifications are specified in Division 01 Section "Quality Requirements."

D. Delegated-Design Submittal:  For smoke and heat detectors indicated to comply with performance requirements and design criteria, including analysis data, signed and sealed by the qualified professional engineer responsible for their preparation.

1. Drawings showing the location of each smoke and heat detector, the ratings of each, and installation details as needed to comply with the listing conditions of the detector.

2. Design Calculations:  Calculate requirements for selecting the spacing and sensitivity of detection, complying with NFPA 72.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

E. Qualification Data:  For qualified Installer.

F. Field quality-control reports.

G. Operation and Maintenance Data:  For fire-alarm systems and components to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data,"[ deliver copies to authorities having jurisdiction and] include the following:

1. Comply with the "Records" Section of the "Inspection, Testing and Maintenance" Chapter in NFPA 72.

2. Provide "Record of Completion Documents" according to NFPA 72 article "Permanent Records" in the "Records" Section of the "Inspection, Testing and Maintenance" Chapter.

3. Record copy of site-specific software.

4. Provide "Maintenance, Inspection and Testing Records" according to NFPA 72 article of the same name and include the following:

a. Frequency of testing of installed components.

b. Frequency of inspection of installed components.

c. Requirements and recommendations related to results of maintenance.

d. Manufacturer's user training manuals.

5. Manufacturer's required maintenance related to system warranty requirements.

6. Abbreviated operating instructions for mounting at fire-alarm control unit.

Retain subparagraph below when Project contains water-based sprinkler or standpipe systems.

7. Copy of NFPA 25.

1.6 QUALITY ASSURANCE

Retain one or both of first two paragraphs below.  See Editing Instruction No. 2 in the Evaluations for a discussion about installer qualifications.  Coordinate with "Submittals" Article.

A. Installer Qualifications:  Personnel shall be trained and certified by manufacturer for installation of units required for this Project.

B. Installer Qualifications:  Installation shall be by personnel certified by NICET as fire-alarm [Level II] [Level III] [Level IV] technician.

Retain first paragraph below for fire-alarm projects that are renovations of or additions to existing facilities.

C. Source Limitations for Fire-Alarm System and Components:  Obtain fire-alarm system from single source from single manufacturer.  Components shall be compatible with, and operate as, an extension of existing system.

D. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

1.7 PROJECT CONDITIONS

Retain this article if interruption of existing fire-alarm system is permitted.

A. Interruption of Existing Fire-alarm Service:  Do not interrupt fire-alarm service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary guard service according to requirements indicated:

1. Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of fire-alarm service.

2. Do not proceed with interruption of fire-alarm service without [Architect's] [Construction Manager's] [Owner's] written permission.

1.8 SEQUENCING AND SCHEDULING

Retain this article if Project requires replacement or extension of an existing system in an occupied building.  Coordinate with Drawings.

A. Existing Fire-Alarm Equipment:  Maintain existing equipment fully operational until new equipment has been tested and accepted.  As new equipment is installed, label it "NOT IN SERVICE" until it is accepted.  Remove labels from new equipment when put into service and label existing fire-alarm equipment "NOT IN SERVICE" until removed from the building.

B. Equipment Removal:  After acceptance of new fire-alarm system, remove existing disconnected fire-alarm equipment and wiring.

1.9 EXTRA MATERIALS

A. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Revise subparagraphs below to suit Project.

1. Lamps for Remote Indicating Lamp Units:  Quantity equal to [10] <Insert number> percent of amount installed, but no fewer than 1 unit.

2. Lamps for Strobe Units:  Quantity equal to [10] <Insert number> percent of amount installed, but no fewer than 1 unit.

3. Smoke and Fire Detectors:  Quantity equal to [10] <Insert number> percent of amount of each type installed, but no fewer than 1 unit of each type.

4. Detector Bases:  Quantity equal to [2] <Insert number> percent of amount of each type installed, but no fewer than 1 unit of each type.

5. Keys and Tools:  One extra set for access to locked and tamperproofed components.

6. Audible and Visual Notification Appliances:  [One] <Insert number> of each type installed.

7. Fuses:  [Two] <Insert number> of each type installed in the system.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Amseco; a Potter brand; Potter Electric Signal Company.

2. Bosch Security Systems.

3. Commercial Products Group/CPG Life Safety Signals.

4. Faraday; Siemens Building Technologies, Inc.

5. Federal Signal Corporation.

6. Fire Control Instruments Inc.; a Honeywell company.

7. Fire-Lite Alarms; a Honeywell company.

8. Gamewell, a Honeywell company.

9. GE Infrastructure; a unit of General Electric Company

10. Gentex Corporation.

11. Harrington Signal, Inc.

12. NOTIFIER; a Honeywell company.

13. Siemens Building Technologies, Inc.; Fire Safety Division.

14. Silent Knight; a Honeywell company.

15. SimplexGrinnell LP; a Tyco International company.

16. <Insert manufacturer's name>.

2.2 SYSTEMS OPERATIONAL DESCRIPTION

Revise this article to provide a functional description applicable to Project.

The word "systems" in the option in first paragraph below refers to systems specified in other Sections that initiate fire-alarm signals.  An example is smoke detectors supplied under Division 08 Section "Door Hardware" that provide for closing of smoke doors or unlocking of related doors.  Coordinate with requirements in other Sections that specify those other systems.

A. Fire-alarm signal initiation shall be by one or more of the following devices[ and systems]:

Retain only those devices and systems in subparagraphs below that are applicable to Project.  Coordinate with requirements in other Sections that specify listed devices and systems.

1. Manual stations.

2. Heat detectors.

Retain one or both of first two subparagraphs below.  Coordinate with Drawings if both types are retained.

3. Smoke detectors.

4. Duct smoke detectors.

5. Automatic sprinkler system water flow.

6. Fire-extinguishing system operation.

7. Fire standpipe system.

8. <Insert alarm-initiating devices and systems>.

B. Fire-alarm signal shall initiate the following actions:

Retain only those actions in subparagraphs below that are applicable to Project.  Coordinate with requirements in other Sections that specify listed devices and systems.

1. Continuously operate alarm notification appliances.

2. Identify alarm zone at fire-alarm control unit[ and remote annunciators].

3. Transmit an alarm signal to the remote alarm receiving station.

4. <Insert signal-initiating actions>.

C. Supervisory signal initiation shall be by one or more of the following devices and systems:

Retain first subparagraph below if applicable to Project.  Coordinate with requirements in other Sections that specify listed devices and systems.

1. Valve supervisory switch.

2. <Insert supervisory signal-initiating devices or systems>.

D. System trouble signal initiation shall be by one or more of the following devices and actions:

Retain only those devises and actions in subparagraphs below that are applicable to Project.  Coordinate with requirements in other Sections that specify listed devices and systems.

1. Open circuits, shorts, and grounds in designated circuits.

2. Opening, tampering with, or removing alarm-initiating and supervisory signal-initiating devices.

3. Loss of primary power at fire-alarm control unit.

4. Ground or a single break in fire-alarm control unit internal circuits.

5. Abnormal ac voltage at fire-alarm control unit.

6. Break in standby battery circuitry.

7. Failure of battery charging.

8. Abnormal position of any switch at fire-alarm control unit[ or annunciator].

9. <Insert trouble signal-initiating devices and actions>.

E. System Trouble and Supervisory Signal Actions:  Initiate notification appliance and annunciate at fire-alarm control unit[ and remote annunciators].

2.3 FIRE-ALARM CONTROL UNIT

Retain first paragraph below and revise general features to suit Project.  Coordinate with implementation details and Drawings.

A. General Requirements for Fire-Alarm Control Unit:

1. Modular, power-limited design with electronic modules, UL 864 listed.

a. Include a real-time clock for time annotation of events.

B. Alphanumeric Display and System Controls:  Display alarm, supervisory, and component status messages and the programming and control menu.

1. Annunciator and Display:  Liquid-crystal type, one line of [40] [80] characters, minimum.

C. Circuits:

1. No Fewer Than [Five] <Insert number> Initiating Device Circuits:

NFPA 72 requires that fire-alarm system design include the designation of system circuit class and style unless redundant.  Capacities on a single circuit should be determined based on the amount of detection that would be lost during a fault condition and the resulting impact on life safety or property protection.  See Editing Instruction No. 3 in the Evaluations for discussion about determining the class of a circuit.

The number in subparagraph above should be the sum of the numbers in subparagraphs below.

a. [Four] <Insert number> circuits, NFPA 72, Class B.

b. [One] <Insert number> circuit(s), NFPA 72, Class A, Style 6

2. No Fewer Than [Two] <Insert number> Notification Appliance Circuits:  NFPA 72, Class B, Style Y.

Retain first paragraph below if connecting to an existing system and retaining the use of the existing evacuation scheme that is different from ANSI S3.41.

D. Notification Appliance Circuit:  Operation shall sound in a <Insert pattern>.

ICC requires that smoke detectors in first paragraph below be system detectors.  NFPA 101 and NFPA 5000 allow them to be nonsystem detectors.

E. Door Controls:  Door hold-open devices that are controlled by smoke detectors at doors in smoke barrier walls shall [be] [not be] connected to fire-alarm system.

F. Transmission to Remote Alarm Receiving Station:  Automatically transmit alarm, supervisory, and trouble signals to a remote alarm station.

First paragraph below is for two-wire supply; revise if three-wire supply or an external dc supply is provided.

G. Primary Power:  24-V dc obtained from 120-V ac service and a power-supply module.  Initiating devices, notification appliances, signaling lines, trouble signals, [supervisory signals] [supervisory and digital alarm communicator transmitters] [and] [digital alarm radio transmitters] shall be powered by the 24-V dc source.

1. Alarm current draw of the entire fire-alarm system shall not exceed 80 percent of the power-supply module rating.

H. Secondary Power:  24-V dc supply system with batteries, automatic battery charger, and automatic transfer switch.

1. Batteries:  [Sealed lead calcium] [Sealed, valve-regulated, recombinant lead acid] [Vented, wet-cell pocket, plate nickel cadmium].

Retain paragraph below to require printed instructions for projects in which a new fire-alarm control unit is provided or if functions of an existing fire-alarm control unit are modified.

I. Instructions:  Computer printout or typewritten instruction card mounted behind a plastic or glass cover in a stainless-steel or aluminum frame.  Include interpretation and describe appropriate response for displays and signals.  Briefly describe the functional operation of the system under normal, alarm, and trouble conditions.

2.4 MANUAL FIRE-ALARM BOXES

A. General Requirements for Manual Fire-Alarm Boxes:  Comply with UL 38.  Boxes shall be finished in red with molded, raised-letter operating instructions in contrasting color; shall show visible indication of operation; and shall be mounted on recessed outlet box.  If indicated as surface mounted, provide manufacturer's surface back box.

Retain one of first two subparagraphs below.  Some owners and authorities having jurisdiction allow double-action type to reduce accidental alarm initiations.

1. Single-action mechanism, [breaking-glass or plastic-rod] [pull-lever] type.

2. Double-action mechanism requiring two actions to initiate an alarm, [breaking-glass or plastic-rod] [pull-lever] type.

3. Station Reset:  Key- or wrench-operated switch.

Retain first subparagraph below if physical protection other than a wire guard is required for manual stations or if protection from false alarms is required.  Delete horn if not required.

4. Indoor Protective Shield:  Factory-fabricated clear plastic enclosure hinged at the top to permit lifting for access to initiate an alarm.  Lifting the cover actuates an integral battery-powered audible horn intended to discourage false-alarm operation.

Retain subparagraph below to add a weatherproof protective shield to manual stations that do not include the horn.

5. Weatherproof Protective Shield:  Factory-fabricated clear plastic enclosure hinged at the top to permit lifting for access to initiate an alarm.

2.5 SYSTEM SMOKE DETECTORS

A. General Requirements for System Smoke Detectors:

UL 268 covers detectors that are part of a fire-alarm system and detectors intended solely for control of releasing devices such as door holders and dampers.  Single- or multiple-station nonsystem smoke detector/alarm units for residential units are specified in "Nonsystem Smoke Detectors" Article.  See Editing Instruction No. 7 in the Evaluations for discussion about detector locations.

1. Operating at 24-V dc, nominal.

In first subparagraph below, retain first option for additions to existing four-wire systems or if detector auxiliary contacts are used for critical control functions such as air-handler shutdowns.  Otherwise, retain type based on class of initiating device circuit.

2. Detectors shall be [four] [two]-wire type.

Retain first subparagraph below if mounting directly to outlet box is not required.  Base-mounted detectors should be used for units with auxiliary alarm outputs.

3. Base Mounting:  Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base.  Provide terminals in the fixed base for connection to building wiring.

4. Self-Restoring:  Detectors do not require resetting or readjustment after actuation to restore them to normal operation.

5. Integral Visual-Indicating Light:  LED type indicating detector has operated[ and power-on status].

Number of settable levels in fire-alarm control unit varies among manufacturers and between detector types.  Indicate specific number of levels on Drawings or in the "Remarks" column of a detector schedule.

6. Provide multiple levels of detection sensitivity for each sensor[, with alarm-verification feature].

B. Photoelectric Smoke Detectors:  Comply with UL 268.

If retaining first paragraph below, indicate location of each detector type on Drawings.

C. Ionization Smoke Detector:  Comply with UL 268.

Coordinate paragraph below with Drawings for power supply and fire-alarm control unit connections.  Review two- and four-wire options in "General Requirements for System Smoke Detectors" Paragraph.  Delete paragraph below and retain "Nonsystem Smoke Detectors" Article for two-wire standalone operation.

D. Duct Smoke Detectors:  Photoelectric type complying with UL 268A.

1. Remote indication[ and test] station.  [Operating key switch initiates an alarm test.]

2. Weatherproof Duct Housing Enclosure:  NEMA 250, Type 4X; NRTL listed for use with the supplied detector.

3. Sampling Tubes:  Design and dimensions as recommended by manufacturer for specific duct size, air velocity, and installation conditions where applied.

Retain subparagraph below if required for direct shutdown of the fan associated with the detector.

4. Relay Fan Shutdown:  Rated to interrupt fan motor-control circuit.

2.6 NONSYSTEM SMOKE DETECTORS

See Editing Instruction No. 4 in the Evaluations for discussion about nonsystem smoke detectors.

A. Single-Station Smoke Detectors:

Verify options in subparagraphs below with manufacturer; certain combinations of options may not be available.

1. Comply with UL 217; suitable for NFPA 101, residential occupancies; operating at 120-V ac[ with 9-V dc battery as the secondary power source.  Provide with "low" or "missing" battery chirping-sound device].

2. Auxiliary Relays:  One [Form C rated at 0.5 A] [Form A and one Form C, both rated at 0.5 A].

3. Audible Notification Appliance:  Piezoelectric sounder rated at 90 dBA at 10 feet (3 m) according to UL 464.

4. Visible Notification Appliance:  177-cd strobe.

5. Heat sensor, 135 deg F (57 deg C) [combination rate-of-rise and ]fixed temperature.

6. Test Switch:  Push-to-test; simulates smoke at rated obscuration.

7. Tandem Connection:  Allow tandem connection of number of indicated detectors; alarm on one detector shall actuate notification on all connected detectors.

8. Plug-in Arrangement:  Detector and associated electronic components shall be mounted in a plug-in module that connects to a fixed base.  Provide terminals in the fixed base for connection to building wiring.

9. Self-Restoring:  Detectors shall not require resetting or readjustment after actuation to restore them to normal operation.

10. Integral Visual-Indicating Light:  LED type indicating detector has operated[ and power-on status].

B. Single-Station Duct Smoke Detectors:

1. Comply with UL 268A; operating at 120-V ac.

2. Base Mounting:  Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base.  The fixed base shall be designed for mounting directly to air duct.  Provide terminals in the fixed base for connection to building wiring.

a. Weatherproof Duct Housing Enclosure:  NEMA 250, Type 4X; NRTL listed for use with the supplied detector.

3. Sampling Tubes:  Design and dimensions as recommended by manufacturer for specific duct size, air velocity, and installation conditions where applied.

Verify with Mechanical Drawings and specifications that shutdown in subparagraph below is required; if not required, delete subparagraph.

4. Relay Fan Shutdown:  Rated to interrupt fan motor-control circuit.

2.7 HEAT DETECTORS

A. General Requirements for Heat Detectors:  Comply with UL 521.

Coordinate two paragraphs below with Drawings.  Revise fixed-temperature values to suit applications and NFPA 72 requirements, or delete values below and indicate on Drawings.  See Editing Instruction No. 7 in the Evaluations for discussion about detector locations.

B. Heat Detector, Combination Type:  Actuated by either a fixed temperature of [135 deg F (57 deg C)] <Insert temperature> or a rate of rise that exceeds [15 deg F (8 deg C)] <Insert temperature> per minute unless otherwise indicated.

1. Mounting:  [Adapter plate for outlet box mounting] [Twist-lock base interchangeable with smoke-detector bases].

C. Heat Detector, Fixed-Temperature Type:  Actuated by temperature that exceeds a fixed temperature of [190 deg F (88 deg C)] <Insert temperature>.

1. Mounting:  [Adapter plate for outlet box mounting] [Twist-lock base interchangeable with smoke-detector bases].

2.8 NOTIFICATION APPLIANCES

A. General Requirements for Notification Appliances:  Connected to notification appliance signal circuits, zoned as indicated, equipped for mounting as indicated and with screw terminals for system connections.

Retain subparagraph below where applicable.

1. Combination Devices:  Factory-integrated audible and visible devices in a single-mounting assembly, equipped for mounting as indicated and with screw terminals for system connections.

Sound-level values in first two paragraphs below are typical.  Show sound output ratings on Drawings if values other than the ones listed are used in complying with audibility requirements.  Comply with interpretations of ADA-ABA Accessibility Guidelines by authorities having jurisdiction.  See Editing Instruction No. 5 in the Evaluations for a discussion about audible system sound levels.

B. Chimes, High-Level Output:  Vibrating type, 81-dBA minimum rated output.

C. Horns:  Electric-vibrating-polarized type, 24-V dc; with provision for housing the operating mechanism behind a grille.  Comply with UL 464.  Horns shall produce a sound-pressure level of 90 dBA, measured 10 feet (3 m) from the horn, using the coded signal prescribed in UL 464 test protocol.

D. Visible Notification Appliances:  Xenon strobe lights comply with UL 1971, with clear or nominal white polycarbonate lens mounted on an aluminum faceplate.  The word "FIRE" is engraved in minimum 1-inch- (25-mm-) high letters on the lens.

Delete first subparagraph below if rated light output is indicated on Drawings.  Required light output for visible alarm strobe lights varies from 75 to 177 cd, depending on the floor area and ceiling height of the space, the mounting height of the device, and whether the space is a sleeping area.  Requirements differ among various governing codes.  Consult authorities having jurisdiction for each project.  See Editing Instruction No. 6 in the Evaluations for discussion about determining the light output of visible notification appliances.

1. Rated Light Output:

a. Indicated on Drawings.

b. [15] [30] [75] [110] [177] <Insert value> cd.

c. 15/30/75/110 cd, selectable in the field.

2. Mounting:  [Indicated on Drawings] [Wall mounted].

3. For units with guards to prevent physical damage, light output ratings shall be determined with guards in place.

4. Flashing shall be in a temporal pattern, synchronized with other units.

5. Strobe Leads:  Factory connected to screw terminals.

6. Mounting Faceplate:  Factory finished, [red] [white].

2.9 MAGNETIC DOOR HOLDERS

Retain this article unless door holders are specified in Division 08 Section "Door Hardware."  If retaining, coordinate first paragraph below with Drawings and with Division 08 Section " Door Hardware."

A. Description:  Units are equipped for wall or floor mounting as indicated and are complete with matching doorplate.

1. Electromagnet:  Requires no more than 3 W to develop 25-lbf (111-N) holding force.

2. Wall-Mounted Units:  Flush mounted unless otherwise indicated.

Retain one of two subparagraphs below.

3. Rating:  24-V ac or dc.

4. Rating:  120-V ac.

B. Material and Finish:  Match door hardware.

2.10 REMOTE ANNUNCIATOR

A. Description:  Annunciator functions shall match those of fire-alarm control unit for alarm, supervisory, and trouble indications.  Manual switching functions shall match those of fire-alarm control unit, including acknowledging, silencing, resetting, and testing.

1. Mounting:  [Flush] [Surface] cabinet, NEMA 250, Type 1.

B. Display Type and Functional Performance:  Alphanumeric display and LED indicating lights shall match those of fire-alarm control unit.  Provide controls to acknowledge, silence, reset, and test functions for alarm, supervisory, and trouble signals.

2.11 DIGITAL ALARM COMMUNICATOR TRANSMITTER

Transmitter in this article is compatible with most central-station receiving equipment, but verify specific compatibility and acceptability of this signal-transmission method for each project.  NFPA 72 and UL 632 require dual telephone lines.

A. Digital alarm communicator transmitter shall be acceptable to the remote central station and shall comply with UL 632 and be listed and labeled by an NRTL.

B. Functional Performance:  Unit shall receive an alarm, supervisory, or trouble signal from fire-alarm control unit and automatically capture [one] [two] telephone line(s) and dial a preset number for a remote central station.  When contact is made with central station(s), signals shall be transmitted.  If service on [either] line is interrupted for longer than 45 seconds, transmitter shall initiate a local trouble signal and transmit the signal indicating loss of telephone line to the remote alarm receiving station over the remaining line.  Transmitter shall automatically report telephone service restoration to the central station.  If service is lost on both telephone lines, transmitter shall initiate the local trouble signal.

C. Local functions and display at the digital alarm communicator transmitter shall include the following:

1. Verification that both telephone lines are available.

2. Programming device.

3. LED display.

4. Manual test report function and manual transmission clear indication.

5. Communications failure with the central station or fire-alarm control unit.

6. <Insert local function>.

D. Digital data transmission shall include the following:

Retain applicable subparagraphs below; revise to match characteristics of fire-alarm control unit and requirements of the central station.

1. Zone of the alarm initiating device.

2. Zone of the supervisory signal.

3. Zone of the trouble initiating device.

4. Loss of ac supply or loss of power.

5. Low battery.

6. Abnormal test signal.

7. Communication bus failure.

8. <Insert signal to be transmitted>.

Retain first paragraph below if secondary power supply at fire-alarm control unit is inadequate or if additional supply is required by Project conditions.

E. Secondary Power:  Integral rechargeable battery and automatic charger.

F. Self-Test:  Conducted automatically every 24 hours with report transmitted to central station.

2.12 RADIO ALARM TRANSMITTER

Retain this article if Project requires transmission of fire-alarm, supervisory, and trouble signals to a remote alarm receiving station by means of radio signals.

A. Transmitter shall comply with NFPA 1221 and shall be listed and labeled by an NRTL.

B. Comply with 47 CFR 90.

C. Description:  Manufacturer's standard commercial product; factory assembled, wired, tested, and ready for installation and operation.

1. Packaging:  A single, modular, NEMA 250, Type 1 metal enclosure with a tamper-resistant flush tumbler lock.

2. Signal Transmission Mode and Frequency:  VHF or UHF 2-W power output, coordinated with operating characteristics of the established remote alarm receiving station designated by Owner.

3. Normal Power Input:  120-V ac.

4. Secondary Power:  Integral-sealed, rechargeable, 12-V battery and charger.  Comply with NFPA 72 requirements for battery capacity; submit calculations.

Verify that antenna type and required wind resistance in first subparagraph below are suitable for Project location.  Wind speed is usually a requirement of the applicable building code.

5. Antenna:  Omnidirectional, coaxial half-wave, dipole type with driving point impedance matched to transmitter and antenna cable output impedance.  Wind-load strength of antenna and mounting hardware and supports shall withstand [100 mph (160 km/h)] <Insert wind speed> with a gust factor of 1.3 without failure.

6. Antenna Cable:  Coaxial cable with impedance matched to the transmitter output impedance.

7. Antenna-Cable Connectors:  Weatherproof.

8. Alarm Interface Devices:  Circuit boards, modules, and other auxiliary devices, integral to the transmitter, matching fire-alarm and other system outputs to message-generating inputs of the transmitter that produce required message transmissions.

D. Functional Performance:  Unit shall receive an alarm, supervisory, or trouble signal from fire-alarm control unit or from its own internal sensors or controls and shall automatically transmit signal along with a unique code that identifies the transmitting station to the remote alarm receiving station.  Transmitted messages shall correspond to standard designations for fire-reporting system to which the signal is being transmitted and shall include separately designated messages in response to the following events or conditions:

1. Transmitter Low-Battery Condition:  Sent when battery voltage is below 85 percent of rated value.

2. System Test Message:  Initiated manually by a test switch within the transmitter cabinet, or automatically at an optionally preselected time, once every 24 hours, with transmission time controlled by a programmed timing device integral to transmitter controls.

3. Transmitter Trouble Message:  Actuated by failure, in excess of one-minute duration, of the transmitter normal power source, derangement of the wiring of the transmitter, or any alarm input interface circuit or device connected to it.

4. Local Fire-Alarm-System Trouble Message:  Initiated by events or conditions that cause a trouble signal to be indicated on the building system.

5. Local Fire-Alarm-System Alarm Message:  Actuated when the building system goes into an alarm state.  Identifies device that initiated the alarm.

6. Local Fire-Alarm-System Supervisory-Alarm Message:  [Actuated when the building alarm system indicates a supervisory alarm.] <Insert condition>.

2.13 DEVICE GUARDS

Retain this article if items are installed in gymnasiums and other spaces where they will be exposed to physical damage.

A. Description:  Welded wire mesh of size and shape for the manual station, smoke detector, gong, or other device requiring protection.

1. Factory fabricated and furnished by manufacturer of the device.

2. Finish:  Paint of color to match the protected device.

PART 3 -  EXECUTION

3.1 EQUIPMENT INSTALLATION

A. Comply with NFPA 72 for installation of fire-alarm equipment.

B. Connecting to Existing Equipment:  Verify that existing fire-alarm system is operational before making changes or connections.

1. Connect new equipment to the existing control panel in the existing part of the building.

2. Connect new equipment to the existing monitoring equipment at the supervising station.

3. Expand, modify, and supplement the existing [control] [monitoring] equipment as necessary to extend the existing [control] [monitoring] functions to the new points.  New components shall be capable of merging with the existing configuration without degrading the performance of either system.

Retain first paragraph below if spacing is not indicated on Drawings.  It is recommended that detector spacing and location be determined by a professional engineer, based on the listing of the detectors and on space/ceiling-plane configurations.  See Editing Instruction No. 7 in the Evaluations for discussion about detector locations.

C. Smoke- or Heat-Detector Spacing:

1. Comply with NFPA 72, "Smoke-Sensing Fire Detectors" Section in the "Initiating Devices" Chapter, for smoke-detector spacing.

2. Comply with NFPA 72, "Heat-Sensing Fire Detectors" Section in the "Initiating Devices" Chapter, for heat-detector spacing.

Revise first subparagraph below to indicate how Contractor shall determine detector spacing.

3. Smooth ceiling spacing shall not exceed [30 feet (9 m)] [Insert distance].

4. Spacing of detectors for irregular areas, for irregular ceiling construction, and for high ceiling areas shall be determined according to Appendix A[ or Appendix B] in NFPA 72.

See Editing Instruction No. 8 in the Evaluations for discussion about placement of smoke detectors for HVAC air inlets and outlets.

5. HVAC:  Locate detectors not closer than [3 feet (1 m)] [5 feet (1.5 m)] from air-supply diffuser or return-air opening.

6. Lighting Fixtures:  Locate detectors not closer than 12 inches (300 mm) from any part of a lighting fixture.

D. Duct Smoke Detectors:  Comply with NFPA 72 and NFPA 90A.  Install sampling tubes so they extend the full width of duct.

E. Heat Detectors in Elevator Shafts:  Coordinate temperature rating and location with sprinkler rating and location.

F. Single-Station Smoke Detectors:  Where more than one smoke alarm is installed within a dwelling or suite, they shall be connected so that the operation of any smoke alarm causes the alarm in all smoke alarms to sound.

G. Remote Status and Alarm Indicators:  Install near each smoke detector and each sprinkler water-flow switch and valve-tamper switch that is not readily visible from normal viewing position.

Coordinate first paragraph below with Drawings.

H. Audible Alarm-Indicating Devices:  Install not less than 6 inches (150 mm) below the ceiling.  Install bells and horns on flush-mounted back boxes with the device-operating mechanism concealed behind a grille.

I. Visible Alarm-Indicating Devices:  Install adjacent to each alarm bell or alarm horn and at least 6 inches (150 mm) below the ceiling.

J. Device Location-Indicating Lights:  Locate in public space near the device they monitor.

K. Fire-Alarm Control Unit:  Surface mounting, with tops of cabinets not more than 72 inches (1830 mm) above the finished floor.

L. Annunciator:  Install with top of panel not more than 72 inches (1830 mm) above the finished floor.

Coordinate paragraph below with Drawings.  Wind speed is usually a requirement of the applicable building code.

M. Antenna for Radio Alarm Transmitter:  Mount to building structure where indicated.  Use mounting arrangement and substrate connection that will resist [100-mph (160-km/h)] <Insert wind speed> wind load with a gust factor of 1.3 without damage.

3.2 CONNECTIONS

Coordinate installation and specialty arrangements with Drawings and with requirements specified in related Sections.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Retain first paragraph below if smoke detectors specified in Division 08 Section "Door Hardware" are alarm-initiating devices.  Coordinate with "Door Controls" Paragraph in "Fire-Alarm Control Unit" Article.

A. For fire-protection systems related to doors in fire-rated walls and partitions and to doors in smoke partitions, comply with requirements in Division 08 Section "Door Hardware."  Connect hardware and devices to fire-alarm system.

1. Verify that hardware and devices are NRTL listed for use with fire-alarm system in this Section before making connections.

B. Connect supervised interface devices to the following devices and systems.  Install the interface device less than 3 feet (1 m) from the device controlled.

Coordinate list below with "Systems Operational Description" Article.

1. Smoke dampers in air ducts of designated air-conditioning duct systems.

2. Supervisory connections at valve supervisory switches.

Retain one of three subparagraphs below.

3. Supervisory connections at fire-pump power failure including a dead-phase or phase-reversal condition.

4. Supervisory connections at fire-pump engine control panel.

5. <Insert connections>.

3.3 IDENTIFICATION

A. Identify system components, wiring, cabling, and terminals.  Comply with requirements for identification specified in Division 26 Section "Identification for Electrical Systems."

B. Install framed instructions in a location visible from fire-alarm control unit.

3.4 GROUNDING

A. Ground fire-alarm control unit and associated circuits; comply with IEEE 1100.  Install a ground wire from main service ground to fire-alarm control unit.

3.5 FIELD QUALITY CONTROL

Retain first paragraph below to require that field quality-control tests be witnessed.  Local ordinance or custom may require that authorities having jurisdiction witness the testing.

A. Field tests shall be witnessed by [Architect] [authorities having jurisdiction] <Insert names or titles of witnesses>.

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

B. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

C. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

If Owner selects and contracts with a central station or another remote alarm receiving station for continuing services, consider making the initial tests and inspections and reacceptance testing the obligation of Contractor, and the monthly, quarterly, semiannual, and annual tests and inspections the obligation of the remote alarm receiving station.

D. Tests and Inspections:

1. Visual Inspection:  Conduct the visual inspection prior to testing.

a. Inspection shall be based on completed Record Drawings and system documentation that is required by NFPA 72 in its "Completion Documents, Preparation" Table in the "Documentation" Section of the "Fundamentals of Fire Alarm Systems" Chapter.

b. Comply with "Visual Inspection Frequencies" Table in the "Inspection" Section of the "Inspection, Testing and Maintenance" Chapter in NFPA 72; retain the "Initial/Reacceptance" column and list only the installed components.

2. System Testing:  Comply with "Test Methods" Table in the "Testing" Section of the "Inspection, Testing, and Maintenance" Chapter in NFPA 72.

Retain first two subparagraphs below for additional tests not required by NFPA 72 but required by some jurisdictions.  Engineer's calculations may be accepted by some jurisdictions in lieu of testing.

3. Test audible appliances for the public operating mode according to manufacturer's written instructions.  Perform the test using a portable sound-level meter complying with Type 2 requirements in ANSI S1.4.

4. Test visible appliances for the public operating mode according to manufacturer's written instructions.

5. Factory-authorized service representative shall prepare the "Fire Alarm System Record of Completion" in the "Documentation" Section of the "Fundamentals of Fire Alarm Systems" Chapter in NFPA 72 and the "Inspection and Testing Form" in the "Records" Section of the "Inspection, Testing and Maintenance" Chapter in NFPA 72.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

E. Reacceptance Testing:  Perform reacceptance testing to verify the proper operation of added or replaced devices and appliances.

F. Fire-alarm system will be considered defective if it does not pass tests and inspections.

G. Prepare test and inspection reports.

Work in two paragraphs below is normally the responsibility of Owner.  Retain one or both paragraphs if Owner needs additional time to contract for inspections required by NFPA 72.

H. Maintenance Test and Inspection:  Perform tests and inspections listed for weekly, monthly, quarterly, and semiannual periods.  Use forms developed for initial tests and inspections.

I. Annual Test and Inspection:  One year after date of Substantial Completion, test fire-alarm system complying with the visual and testing inspection requirements in NFPA 72.  Use forms developed for initial tests and inspections.

3.6 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain fire-alarm system.

END OF SECTION 283112

	ZONED (DC LOOP) FIRE-ALARM SYSTEM
	283112 - 1



