Copyright 2003 AIA
MASTERSPEC
03/03

Copyright 2003, The American Institute of Architects (AIA)

SECTION 02552 - GROUND-LOOP, HEAT-PUMP PIPING
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes piping for [horizontal] [vertical], direct-buried, ground-loop, heat-pump systems that operate between 23 and 104 deg F (minus 5 and plus 40 deg C).

1.3 PERFORMANCE REQUIREMENTS

A. Components and installation shall be capable of withstanding the following minimum working pressure, unless otherwise indicated:

Revise pressure ratings in subparagraph below to suit Project.  Coordinate with Division 15 Section "Water-Source Heat Pumps."

1. Ground-Loop, Heat-Pump Piping:  [160 psig (1100 kPa)] [200 psig (1380 kPa)] <Insert pressure rating>.

1.4 SUBMITTALS

A. Product Data:  For the following:

1. Pipe and fittings.

2. Joining method and equipment.

Retain subparagraph below for climates and piping placement that require freeze protection.

3. Propylene glycol solution.

Retain paragraph below if Contractor is responsible for field quality-control testing.

B. Field quality-control test reports.

PART 2 -  PRODUCTS

2.1 PIPES AND FITTINGS

See Evaluations for discussion on various pipe materials.

A. PE Pipe:  ASTM D 2239, SIDR Numbers 5.3, 7, 9, or 11.5; with PE compound number required to achieve required system working pressure.

1. Molded PE Fittings:  ASTM D 2683 or ASTM D 3261, PE resin, socket- or butt-fusion type, made to match PE pipe dimensions and class.

B. U-Bend Assembly:  Factory fabricated with embossed depth stamp every [24 inches (600 mm)] [36 inches (900 mm)] <Insert dimension> from U-bend.

2.2 BOREHOLE BACKFILL

Retain this Article only for boreholes.

A. Surface Seal:  [Bentonite] [Cement] with thermal conductivity greater than 1.2 Btu/h x sq. ft. x deg F (0.7 W/sq. m x K).

B. Backfill below Surface Seal:  Natural or manufactured sand specified in Division 2 Section "Earthwork."

2.3 ANTIFREEZE SOLUTION

Retain this Article if piping is exposed to freezing temperatures.

A. Propylene Glycol:  Minimum 99 percent propylene glycol with corrosion inhibitors and environmental stabilizer additives to be mixed with water to protect the piping circuit and connected equipment from physical damage from freezing or corrosion.

B. Quantity:  Sufficient solution for initial system startup and for preventive maintenance for one year from date of Substantial Completion.

C. Dilution Water:  Chloride content shall be less than 25 ppm, sulfate less than 25 ppm, and hardness less than 100 ppm.

PART 3 -  EXECUTION

3.1 EARTHWORK

A. Excavating, trenching, warning tape, and backfilling are specified in Division 2 Section "Earthwork."

3.2 HORIZONTAL PIPING INSTALLATION

A. Separate trenches by 10 feet (3 m) minimum, unless otherwise indicated.  Remove rocks in trenches that could contact pipe.

B. Backfill to [24 inches (600 mm)] <Insert depth> above pipe with mud developed from excavated rock-free soil or with sand, pea gravel, or fly ash.  Backfill from slurry level to grade with excavated soil, compacting as specified for pipe burial in Division 2 Section "Earthwork."

Retain first paragraph below if pipe will be installed in body of water; otherwise, delete.

C. Extend pipe from trench onto the bottom of the body of water at an elevation that is at least 12 inches (300 mm) below frost line.  Seal membrane or impervious liner under the body of water after installing piping.

D. Install PE piping in trenches according to ASTM D 2774 or ASTM F 645.

1. Clean PE pipe and fittings and make heat-fusion joints according to ASTM D 2657.  Minimize number of joints.

E. Purge, flush, and pressure test piping before backfilling trenches.

F. Install continuous detectable warning tape for underground piping.  Locate tape a minimum of [24 inches (600 mm)] <Insert depth> below finished grade, directly over piping.  Underground warning tapes are specified in Division 2 Section "Earthwork."

G. Common piping installation requirements are specified in Division 2 Section "Piped Utilities - Basic Materials and Methods."

3.3 VERTICAL PIPING INSTALLATION

Retain this Article if Project includes vertical piping in boreholes.

A. Install PE piping in boreholes according to ASTM D 2774 or ASTM F 645.

1. Clean PE pipe and fittings and make heat-fusion joints according to ASTM D 2657.  Minimize number of joints.

B. Purge, flush, and pressure test piping before backfilling boreholes.

C. After installation of loop pipe in borehole, fill piping loop with water or antifreeze solution, and pump backfill into borehole to discharge at base of borehole.

D. Fill borehole with backfill to a point at least [60 inches (1524 mm)] <Insert depth> below grade and backfill remainder with surface seal material.

E. Extend piping and connect to water-source, ground-loop, heat-pump piping systems at outside face of building wall in locations and pipe sizes indicated.

1. Terminate water-service piping at building wall until building water-source, ground-loop, heat-pump piping systems are installed.  Terminate piping with caps.  Make connections to building water-source, ground-loop, heat-pump piping systems when those systems are installed.

F. Wall sleeves are specified in [Division 2 Section "Piped Utilities - Basic Materials and Methods] [Division 15 Section "Basic Mechanical Materials and Methods]."

G. Mechanical sleeve seals are specified in Division 15 Section "Basic Mechanical Materials and Methods."

3.4 ANTIFREEZE SOLUTION FILL

Delete this Article if Division 15 Section "HVAC Water Treatment" is used.

A. Fill system with required quantity of propylene glycol and water to provide [minus 10 deg F (minus 23 deg C)] <Insert temperature> freezing temperature.

B. Test the dilute solution using gas chromatography to verity concentration of propylene glycol, and forward report to Architect.

3.5 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of piping, fittings, and specialties.

3.6 FIELD QUALITY CONTROL

A. Piping Tests:  Fill piping 24 hours before testing and apply test pressure to stabilize piping.  Use potable water only.

B. Hydrostatic Tests:  Test at not less than 1-1/2 times the pipe working-pressure rating[ allowing for static pressure of borehole depth].

1. Increase pressure in 50-psig (345-kPa) increments and inspect each joint between increments.  Hold at test pressure for 30 minutes.  Slowly increase to next test pressure increment and hold for 30 minutes.  After testing at maximum test pressure, reduce pressure to 30 psig (207 kPa).  Hold for 90 minutes, and measure pressure at 30-minute intervals.  Repair leaks and retest until no leaks exist.

C. Prepare reports of testing activity.

END OF SECTION 02552

GROUND-LOOP, HEAT-PUMP PIPING
02552 - 1

