Copyright 2002 AIA
MASTERSPEC Full Length
08/02 (R 05/06)

Copyright 2002 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 03471 - TILT-UP CONCRETE
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section specifies load-bearing, tilt-up concrete, including the following:

Adjust list below to suit Project.

1. Monolithic panels.

2. Insulated-sandwich panels.

B. Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 Section "Earthwork" for [engineered fill] [and] [drainage fill] under slab-on-grade closure strip.

2. Division 3 Section "Cast-in-Place Concrete" for slab-on-grade closure strip and general concrete construction.

3. Division 3 Section " Cast-in-Place Architectural Concrete" for specially finished formed concrete.

4. Division 5 Section "Metal Fabrications" for embedded metal items and loose hardware.

5. Division 7 Section "Sheet Metal Flashing and Trim" for flashing receivers and reglets.

6. Division 7 Section "Joint Sealants" for elastomeric joint sealants and sealant backings between tilt-up panels.

1.3 DEFINITIONS

A. Face-down Surface:  Concealed surface of as-cast, tilt-up panel formed against the casting slab.

B. Face-up Surface:  Exposed upper surface of as-cast, tilt-up panel.

Retain paragraph below if classifying degree of exposure of aggregate in exposed-aggregate finish.

C. Reveal:  Projection of the coarse aggregate from the matrix after exposure.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. LEED Submittals:

Retain subparagraph below if recycled content is required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  An alternative method of complying with Credit MR 4.1 and MR 4.2 requirements is to retain requirement in Division 1 Section "LEED Requirements" that gives Contractor the option and responsibility for determining how Credit MR 4.1 and MR 4.2 requirements will be met.

1. Product Data for Credit MR 4.1[ and Credit MR 4.2]:  For products having recycled content, documentation indicating percentages by weight of postconsumer and preconsumer recycled content.

a. Include statement indicating costs for each product having recycled content.

Retain subparagraph below if fly ash, ground granulated blast-furnace slag, silica fume, or other materials are used as portland cement replacements for LEED-NC Credit ID 1.1.  To achieve this credit, replacement materials must be substituted for at least 40 percent of the portland cement that would otherwise be used.

2. Design Mixtures for Credit ID 1.1:  For each concrete mixture containing fly ash as a replacement for portland cement or other portland cement replacements and for equivalent concrete mixtures that do not contain portland cement replacements.

C. Design Mixtures:  For each concrete mixture.  Submit alternate design mixtures when characteristics of materials, Project conditions, weather, test results, or other circumstances warrant adjustments.

D. Shop Drawings:  Detail fabrication and installation of tilt-up concrete units.  Indicate panel locations, plans, elevations, dimensions, shapes, cross sections, and details of steel embedments.[  Match panel identification designations on Shop Drawings with those on Contract Drawings.]

1. Include steel reinforcement, detailing fabrication, bending, and placing.  Include material, grade, bar schedules, stirrup spacing, bent-bar diagrams, arrangement, and supports of concrete reinforcement.

2. Include additional steel reinforcement to resist hoisting and erection stresses.

3. Include locations and details of hoisting points and lifting devices for handling and erection.

4. Include engineering analysis data of additional steel reinforcement and hoisting and erection details, signed and sealed by the qualified professional engineer responsible for their preparation.

5. Indicate welded connections by AWS standard symbols.  Detail cast-in inserts, connections, and joints, including accessories.

6. Include layout of wythe connectors for sandwich panels.

Delete paragraph below if no exposed aggregate finishes or if no Samples are required.  Add other material samples if required.

E. Samples:  20-lb (9-kg) <Insert weight> Sample of exposed aggregate.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

F. Welding certificates.

Delete paragraph and subparagraph below if material test reports are not required.

G. Material Test Reports:  For the following, from a qualified testing agency, indicating compliance with requirements:

Retain option in subparagraph below if retaining service record data with "Coarse Aggregates" Paragraph in Part 2 "Concrete Materials" Article.

1. Aggregates.[  Include service record data indicating absence of deleterious expansion of concrete due to alkali aggregate reactivity.]

Delete paragraph and subparagraphs below if material certificates are not required.

H. Material Certificates:  For each of the following, signed by manufacturers:

Edit list below to suit Project.

1. Cementitious materials.

2. Admixtures.

3. Steel reinforcement and accessories.

4. Bondbreakers.

5. Curing compounds.

6. Inserts and embedments.

7. Sandwich-panel insulation and wythe connectors.

Retain paragraph below if Contractor is responsible for field quality-control testing and inspections other than special inspections.

I. Field quality-control test[ and inspection] reports.

Delete paragraph below if no preinstallation conference.

J. Minutes of preinstallation conference.

1.5 QUALITY ASSURANCE

Delete first paragraph below if certification of Tilt-up Supervisor is not required; this is a recently introduced certification program.

A. Installer Qualifications:  A qualified installer who employs a supervisor on Project who is an ACI-certified Tilt-up Supervisor.

B. Manufacturer Qualifications:  A firm experienced in manufacturing ready-mixed concrete products and that complies with ASTM C 94/C 94M requirements for production facilities and equipment.

Delete subparagraph below if not required.

1. Manufacturer certified according to NRMCA's "Certification of Ready Mixed Concrete Production Facilities."

Retain first paragraph below if Contractor or manufacturer selects testing agency for mixture design, material test reports, or field quality control.  Retain option if field quality-control testing agency employed by Contractor must be approved by authorities having jurisdiction.

C. Testing Agency Qualifications:  An independent agency,[ acceptable to authorities having jurisdiction,] qualified according to ASTM C 1077 and ASTM E 329 for testing indicated, as documented according to ASTM E 548.

Retain subparagraph below, required by ACI 301, if emphasis is needed.  ASTM C 1077 notes relevant field or laboratory technician certification by ACI, NRMCA, and PCA, or the National Institute for Certification in Engineering Technologies may demonstrate evidence of competence.

1. Personnel conducting field tests shall be qualified as ACI Concrete Field Testing Technician, Grade I, according to ACI CP-01 or an equivalent certification program.

Retain subparagraph below if requiring minimum qualifications for laboratory personnel performing testing and for laboratory supervisor.

2. Personnel performing laboratory tests shall be an ACI-certified Concrete Strength Testing Technician and Concrete Laboratory Testing Technician - Grade I.  Testing agency laboratory supervisor shall be an ACI-certified Concrete Laboratory Testing Technician - Grade II.

D. Source Limitations:  Obtain each type or class of cementitious material of the same brand from the same manufacturer's plant, obtain aggregate from one source, and obtain admixtures through one source from a single manufacturer.

Delete first paragraph and subparagraphs below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

E. Welding:  Qualify procedures and personnel according to the following:

Select applicable standards from two subparagraphs below.

1. AWS D1.1, "Structural Welding Code--Steel."

2. AWS D1.4, "Structural Welding Code--Reinforcing Steel."

F. ACI Publications:  Comply with ACI 301, "Specification for Structural Concrete," Sections 1 through 5, unless modified by requirements in the Contract Documents.

G. Concrete Testing Service:  Engage a qualified independent testing agency to perform material evaluation tests and to design concrete mixtures.

Delete paragraph and subparagraphs below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.  TCA suggests forming 48-by-96-inch (1200-by-2400-mm) panels.

H. Mockups:  Cast and erect tilt-up concrete panel mockups to demonstrate typical reveals, surface finishes, texture, color, and standard of workmanship.

1. Build mockup panels in the location and of the size indicated or, if not indicated, as directed by Architect.

Delete subparagraph below unless retaining special finishes.

2. In presence of Architect, damage part of an exposed surface for each finish, color, and texture required, and demonstrate materials and techniques proposed for repairs to match adjacent undamaged surfaces.

Delete subparagraph below if default requirement in Division 1 Section "Quality Requirements" is to demolish and remove mockups.

3. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

Usually retain paragraph and subparagraphs below for major concrete installations.  Preinstallation conference helps minimize misunderstandings and reviews Project conditions that might lead to significant problems.  Delete if Work of this Section is not extensive or complex enough to justify a preinstallation conference.  If retaining, coordinate with Division 1.

I. Preinstallation Conference:  Conduct conference at Project site to comply with requirements in Division 1 Section "Project Management and Coordination."

Retain first subparagraph and associated subparagraphs below if warranted by complexity of design mixtures and quality control of concrete materials.

1. Before submitting design mixtures, review concrete design mixture and examine procedures for ensuring quality of concrete materials.  Require representatives of each entity directly concerned with tilt-up concrete to attend, including the following:

a. Contractor's superintendent.

b. Independent testing agency responsible for concrete design mixtures.

c. Ready-mix concrete manufacturer.

d. Tilt-up concrete subcontractor.

2. Review [special inspection procedures;] [testing and inspecting agency procedures for field quality control;] [tilt-up concrete finishes and finishing;] [cold- and hot-weather concreting procedures;] [curing procedures;] [casting-slab construction, flatness and levelness, finish, and joint requirements;] [steel reinforcement installation;] [hoisting and erection plans;] [measurement of fabrication and erection tolerances;] [tilt-up concrete repair procedures;] and tilt-up concrete protection.

PART 2 -  PRODUCTS

2.1 FORMS AND ACCESSORIES

Revise this Article to suit Project.

A. Forms:  Metal, dressed lumber, or other approved materials that are nonreactive with concrete and that will provide continuous, true, and smooth concrete surfaces.

B. Chamfer Strips:  Wood, metal, PVC, or rubber strips, 3/4 by 3/4 inch (19 by 19 mm).

Delete first paragraph below if not using form liners; revise to add description of chosen form liner if required.

C. Form Liners:  Units of face design, texture, arrangement, and configuration indicated.  Furnish with manufacturer's recommended liquid-release agent that will not bond with, stain, or adversely affect concrete surfaces and will not impair subsequent surface treatments of concrete.

D. Reveal Strips:  Metal, PVC, rubber, straight dressed wood, or plywood; with sides kerfed.

E. Sealer:  Penetrating, clear, polyurethane wood form sealer formulated to reduce absorption of bleedwater and prevent migration of set-retarding chemicals from wood or plywood.

2.2 STEEL REINFORCEMENT

Delete or revise this Article to suit steel reinforcement requirements.

Retain first paragraph below if recycled content is required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  USGBC allows a default value of 25 percent to be used for steel, without documentation; higher percentages can be claimed if they are supported by appropriate documentation.  The Steel Recycling Institute indicates that reinforcing bars are made by the electric arc furnace method, which typically has 57.5 percent postconsumer recycled content and 6.5 percent preconsumer recycled content.

A. Recycled Content of Steel Products:  Provide products with an average recycled content of steel products so postconsumer recycled content plus one-half of preconsumer recycled content is not less than [25] [60] <Insert number> percent.

B. Reinforcing Bars:  ASTM A 615/A 615M, Grade 60 (Grade 420), deformed.

Retain first paragraph below for reinforcement that is welded or if added ductility is sought.

C. Low-Alloy-Steel Reinforcing Bars:  ASTM A 706/A 706M, deformed.

D. Plain-Steel Wire:  ASTM A 82, [as drawn] [galvanized].

E. Plain-Steel Welded Wire Reinforcement:  ASTM A 185, fabricated from as-drawn steel wire into flat sheets.

F. Deformed-Steel Welded Wire Reinforcement:  ASTM A 497, flat sheet.

G. Bar Supports:  Manufactured according to CRSI's "Manual of Standard Practice" of plastic or CRSI Class 1 plastic-protected steel wire or Class 2 stainless-steel wire.

2.3 CONCRETE MATERIALS

A. Cementitious Material:  Use the following cementitious materials, of the same type, brand, and source, throughout the Project:

Select type and color of portland cement from options in subparagraph below.

1. Portland Cement:  ASTM C 150, Type [I] [II] [I/II] [III] [V], [gray] [white].[  Supplement with the following:]

Select supplementary cementing materials from two subparagraphs below if permitted.  Ready-mix manufacturer blends these materials with portland cement.  Fly ash, slag, or pozzolanic materials may slow rate of concrete strengthening and affect color uniformity of panels.  Availability of Class F fly ash predominates over Class C fly ash.

a. Fly Ash:  ASTM C 618, Class [C] [F].

b. Ground Granulated Blast-Furnace Slag:  ASTM C 989, Grade 100 or 120.

Retain subparagraph below if factory-blended hydraulic cement is permitted; verify availability of options before specifying.  Fly ash, slag, or pozzolanic materials in the nonportland cement part of blended hydraulic cement may slow rate of concrete strengthening, affect color uniformity, and influence choice of bondbreaker.

2. Blended Hydraulic Cement:  ASTM C 595, Type [IS, portland blast-furnace slag] [IP, portland-pozzolan] [I (PM), pozzolan-modified portland] [I (SM), slag-modified portland] cement.

Select class of aggregate from options in first paragraph below or revise to suit Project.  ASTM C 33 limits deleterious substances in coarse aggregate depending on climate severity and in-service location of concrete.  Classes in options are ASTM C 33 default classes for concrete subject to frequent wetting for Severe, Moderate, and Negligible weathering regions, respectively.  Revise first two options to Class 5S or Class 5M if more restrictive controls for exposed architectural concrete apply.  Retain last option if damage caused by concrete expansion from alkali silica or alkali carbonate reactions is anticipated.

B. Coarse Aggregate:  ASTM C 33, Class [4S] [4M] [1N] <Insert class> coarse aggregate or better, graded.  Provide aggregates from a single source[ with documented service record data of at least 10 years' satisfactory service in similar applications and service conditions using similar aggregates and cementitious materials].

Select coarse-aggregate size from options in subparagraph below; add gradation requirements if preferred.  Aggregate size limits relate to spacing of steel reinforcement, depth of slab, or thickness of concrete member.

1. Maximum Coarse-Aggregate Size:  [1 inch (25 mm)] [3/4 inch (19 mm)] <Insert dimension> nominal.

C. Fine Aggregate:  [ASTM C 33] [or] [ASTM C 144], manufactured or natural sand, from same source for Project, free of materials with deleterious reactivity to alkali in cement.

Retain first paragraph and subparagraphs below if exposed aggregate is required in addition to coarse aggregate.  Coordinate with panel finish.  Revise to describe large facing aggregate for sand-bed exposure method if required.

D. Exposed Coarse Aggregate:  Hard and durable; washed; free of material that reacts with cementitious material or causes staining; from a single source, as follows:

Select exposed-aggregate sizes from three subparagraphs below or revise to include one size or a range of gradations if preferred.  Coarse-aggregate sizes range from 1/4 inch (6 mm) to more than 1-1/2 inches (38 mm).  Add other descriptions such as source and shape if required.

1. Aggregate Sizes:  [3/4 to 1 inch (19 to 25 mm)] [1/2 to 3/4 inch (13 to 19 mm)] [3/8 to 5/8 inch (10 to 16 mm)] nominal.

2. Gradation:  [Uniformly] [Gap] graded.

3. Source and Material:  <Insert source and material.>

E. Water:  ASTM C 94/C 94M[ and potable].

2.4 ADMIXTURES

A. Air-Entraining Admixture:  ASTM C 260.

B. Chemical Admixtures:  Provide admixtures certified by manufacturer to be compatible with other admixtures and that will not contribute water-soluble chloride ions exceeding those permitted in hardened concrete.  Do not use calcium chloride or admixtures containing calcium chloride.

Select one or more chemical admixtures from six subparagraphs below.

1. Water-Reducing Admixture:  ASTM C 494/C 494M, Type A.

2. Retarding Admixture:  ASTM C 494/C 494M, Type B.

3. Water-Reducing and Retarding Admixture:  ASTM C 494/C 494M, Type D.

4. High-Range, Water-Reducing Admixture:  ASTM C 494/C 494M, Type F.

5. High-Range, Water-Reducing and Retarding Admixture:  ASTM C 494/C 494M, Type G.

6. Plasticizing and Retarding Admixture:  ASTM C 1017/C 1017M, Type II.

Retain paragraph and subparagraph below for integrally colored tilt-up concrete.

C. Color Pigment:  ASTM C 979, synthetic mineral-oxide pigments or colored water-reducing admixtures; color stable,[ free of carbon black,] nonfading, and resistant to lime and other alkalis.

Select one of three options in subparagraph below.

1. Color:  [As indicated by manufacturer's designation] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

2.5 BONDBREAKERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, products listed in this Article.

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Products:  Subject to compliance with requirements, provide one of the following products listed in this Article.

Select one or more bondbreaker types from four paragraphs and associated subparagraphs below.  Some bondbreakers also act as membrane-forming curing compounds and comply with ASTM C 309, Type 1, Class B.  Coordinate choice of bondbreaker with choice of curing compounds in Division 3 Section "Cast-in-Place Concrete" if slab-on-grade is used as casting slab to minimize incompatibility.

C. Solvent-Borne, Chemically Reactive Bondbreaker:  Penetrating polymerized solution containing no oils, waxes, paraffins, or silicones, and compatible with casting-slab curing compound.

1. Burke by Edoco; Clean Lift 90 V.O.C.

2. Conspec Marketing and Manufacturing Co., Inc., a Dayton Superior Company; Conspec CST VOC.

3. Dayton/Richmond Concrete Accessories; Maxi Tilt.

4. Dayton Superior Corporation; Sure Lift (J-6).

5. <Insert manufacturer's name; product name or designation.>

D. Solvent-Borne, Membrane-Forming Bondbreaker:  Dissipating polymerized solution containing no oils, waxes, paraffins, or silicones, and compatible with casting-slab curing compound.

1. Burke by Edoco; Super Bondbreaker V.O.C.

2. Conspec Marketing and Manufacturing Co., Inc., a Dayton Superior Company; Tilt-Eez VOC.

3. <Insert manufacturer's name; product name or designation.>

E. Waterborne, Chemically Reactive Bondbreaker:  Penetrating polymerized emulsion containing no oils, waxes, paraffins, or silicones, and compatible with casting-slab curing compound.

1. Burke by Edoco; Super Tilt Bondbreaker W.B.

2. Conspec Marketing and Manufacturing Co., Inc., a Dayton Superior Company; Conspec CST/WB.

3. Dayton/Richmond Concrete Accessories; Maxi Tilt E.

4. Dayton Superior Corporation; Sure-Lift WB (J-5).

5. Nox-Crete Products Group, Kinsman Corporation; Silcoseal 2000F.

6. <Insert manufacturer's name; product name or designation.>

F. Waterborne, Membrane-Forming Bondbreaker:  Dissipating polymerized emulsion containing no oils, waxes, paraffins, or silicones, and compatible with casting-slab curing compound.

1. Burke by Edoco; Super Bondbreaker W.B.

2. Conspec Marketing and Manufacturing Co., Inc., a Dayton Superior Company; Tilt-Eez WB.

3. Dayton/Richmond Concrete Accessories; Rich Tilt E.

4. <Insert manufacturer's name; product name or designation.>

2.6 CURING MATERIALS

Evaporation retarder in paragraph below temporarily reduces moisture loss from tilt-up concrete surfaces awaiting finishing in hot, dry, and windy conditions.  Evaporation retarders are not curing compounds.

A. Evaporation Retarder:  Waterborne, monomolecular film forming; manufactured for application to fresh concrete.

Select curing aids and materials from two paragraphs below, retaining optional materials when applicable.

B. Absorptive Cover:  AASHTO M 182, Class 2, burlap cloth made from jute or kenaf, weighing approximately 9 oz./sq. yd. (305 g/sq. m) when dry.

C. Moisture-Retaining Cover:  ASTM C 171, polyethylene film or white burlap-polyethylene sheet.

Retain paragraph below if low-VOC emissions are required.  Verify that curing compounds do not exceed maximum emission limits of authorities having jurisdiction.

D. Clear, Waterborne, Membrane-Forming Curing Compound:  ASTM C 309, Type 1, Class B.

2.7 CONNECTION MATERIALS

A. Embedded Metal Items and Loose Hardware:  Materials for securing tilt-up concrete panels together and to supporting and adjacent construction are specified in Division 5 Section "Metal Fabrications."

Retain paragraph above or below and coordinate with Division 5 Section "Metal Fabrications."  If retaining above, delete remainder of this Article.  Retain below if only loose hardware, which is that part of the connection not embedded in the panel, is specified in Division 5 Section "Metal Fabrications."

B. Loose Hardware:  Materials for securing tilt-up concrete panels together and to supporting and adjacent construction are specified in Division 5 Section "Metal Fabrications."

Select materials for embedded items and connections from first six paragraphs below or revise to suit Project.

C. Carbon-Steel Shapes and Plates:  ASTM A 36/A 36M.

ASTM A 307 defines the term "studs" to include stud stock or threaded rods.

D. Carbon-Steel Bolts and Studs:  ASTM A 307, Grade A (ASTM F 568M, Property Class 4.6); carbon-steel, hex-head bolts and studs; carbon-steel nuts; and flat, unhardened steel washers.

E. Unheaded Carbon-Steel Rods and Nuts:  ASTM A 36/A 36M, threaded rods with ASTM A 563, nuts.

F. Welded Headed Studs:  AWS D1.1, Type B headed studs, and cold-finished, carbon-steel bars.

Retain first paragraph below for weldable reinforcement if used for anchor portions of embedments or for chord splices in seismic regions.

G. Low-Alloy-Steel Reinforcing Bars:  ASTM A 706/A 706M, deformed.

H. Chord Bar Sleeves:  Tubular sheathing, plastic or moisture-resistance-treated cardboard.

I. Welding Electrodes:  Comply with AWS standards.

Delete galvanizing below if not required.  Field welding should generally not be permitted on galvanized elements unless galvanizing is removed.

J. Hot-Dip Galvanized Finish:  Apply zinc coating to steel connections by hot-dip process, complying with ASTM A 123/A 123M or ASTM A 153/A 153M as applicable.

1. Zinc Repair Paint:  SSPC-Paint 20.

Delete priming below if not required.

K. Shop-Primed Finish:  Prepare surfaces of steel connections, except those surfaces to be embedded in concrete, according to requirements in SSPC-SP 3, and shop-apply primer according to SSPC-PA 1.

1. Primer:  [MPI#79, "Alkyd Anti-Corrosive Metal Primer"] [MPI#76, "Quick Dry Alkyd Metal Primer]."

2.8 LIFTING INSERTS AND ACCESSORIES

Items in this Article are not specified in detail.  Although selection of lifting inserts and accessories is Contractor's responsibility, specifier may determine features such as finishes that affect panels in service.

A. Furnish inserts, dowels, bolts, nuts, washers, and other items to be cast in panels for tilting and lifting.

Retain subparagraph below, revising materials if required, if rust spots or other damage to concrete or finishes could result.

1. Manufacture inserts with feet of plastic, galvanized steel wire, plastic-tipped steel wire, or stainless-steel-tipped steel wire.

B. Furnish brace anchors and other accessories to be cast in panels and in casting slab for attaching bracing.

Retain subparagraph below, revising materials if required, if rust spots or other damage to concrete or finishes could result.

1. Manufacture wall brace anchors and accessories with feet of galvanized steel wire, plastic-tipped steel wire, or stainless-steel-tipped steel wire.

Consider retaining subparagraph below if brace anchor legs might puncture vapor retarder under slab-on-grade.

2. Manufacture floor brace anchors that will not penetrate vapor retarder under slab-on-grade.

2.9 BEARING PADS

Select bearing pads, also called "leveling shims," from this Article.

A. Elastomeric Pads:  AASHTO M 251, plain, vulcanized, 100 percent polychloroprene (neoprene) elastomer, molded to size or cut from a molded sheet; Type A Shore durometer hardness of 50 to 70, ASTM D 2240; and minimum tensile strength 2250 psi (15.5 MPa), ASTM D 412.

B. Random, Fiber-Reinforced Elastomeric Pads:  Preformed, randomly oriented synthetic fibers set in elastomer with a Type A Shore durometer hardness of 70 to 90, ASTM D 2240.

C. Cotton-Duck-Fabric-Reinforced Elastomeric Pads:  Preformed, horizontally layered cotton-duck fabric bonded in elastomer with a Type A Shore durometer hardness of 80 to 100, ASTM D 2240.

D. High-Density Plastic Strips:  Multimonomer, nonleaching plastic.

2.10 GROUT

Select type of grout to fill gap between panels and foundation from this Article.

A. Cement Grout:  Portland cement, ASTM C 150, Type I; and clean, natural sand, ASTM C 404.  Mix at ratio of 1 part cement to 2-1/2 parts sand, by volume, with minimum water required for placement and hydration.

Retain paragraph below if nonshrink grout is required or if cement-grout shrinkage could cause structural deficiency.

B. Nonmetallic, Nonshrink Grout:  Premixed, nonmetallic, noncorrosive, nonstaining grout containing selected silica sands, portland cement, shrinkage-compensating agents, and plasticizing and water-reducing agents; complying with ASTM C 1107, of consistency suitable for application.

2.11 SANDWICH-PANEL INSULATION

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Extruded-Polystyrene Board Insulation:  ASTM C 578, Type IV, square edged.

Select insulation material from paragraph above or paragraph and subparagraphs below.  Coordinate insulation selection with wythe connector selection in "Sandwich-Panel Accessories" Article because some manufacturers market insulation and wythe connectors as systems.

B. Faced Polyisocyanurate Board Insulation:  ASTM C 1289, Type I, square edged; with aluminum/polyethylene facer.

1. Available Product:  Subject to compliance with requirements, a product that may be incorporated into the Work includes, but is not limited to, "Isocast R" by The Dow Chemical Company.

Retain subparagraph above for nonproprietary or below for proprietary specification.  Refer to Division 1 Section "Product Requirements."

2. Product:  Subject to compliance with requirements, provide "Isocast R" by The Dow Chemical Company.

2.12 SANDWICH-PANEL ACCESSORIES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Select one or more types of wythe connectors from this Article.  Revise and add another type if available and required.

A. Resin Wythe Connectors:  Manufactured thermoplastic resin connector rods, notched, with integral resin flange around shaft of connector rod; alkaline resistant; for noncomposite structural action.

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

Retain subparagraph above for nonproprietary or first subparagraph below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Composite Technologies Corporation; Blucore.

b. Owens Corning; Pinkcore.

c. <Insert manufacturer's name; product name or designation.>

B. Fiber/Polymer Composite Wythe Connectors:  Manufactured composite glass-fiber and vinyl-ester polymer connector rods, notched, with polymer collars injection molded around shaft of connector rod; alkaline resistant; for noncomposite structural action.

1. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain subparagraph above for nonproprietary or first subparagraph below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

2. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

a. Composite Technologies Corporation.

b. Dow Chemical Company (The).

c. <Insert manufacturer's name.>

Dayton/Richmond uses different arrangements of stainless-steel sheet tubular and flat anchors as well as connector pins in the same panels.  Add anchor height and diameter or length, and connector pin diameter and length, to description in paragraph below or indicate on Drawings.

C. Stainless-Steel Wythe Connectors:  Manufactured of stainless-steel sheet, ASTM A 240/A 240M, Type 304; round tube and rectangular flat anchors; punched with round holes for anchor rods and oval holes for concrete bond; equipped with bright, hard-drawn steel wire anchor rods, 1/4 inch (6.4 mm) in diameter, 28 inches (710 mm) long; and L-shaped crimped connector pins manufactured of stainless-steel wire, ASTM A 580/A 580M, Type 304; for noncomposite structural action.

1. Available Manufacturer:  Subject to compliance with requirements, a manufacturer offering products that may be incorporated into the Work includes Dayton/Richmond Concrete Accessories.

Retain subparagraph above for nonproprietary or below for proprietary specification.  Refer to Division 1 Section "Product Requirements."

2. Manufacturer:  Subject to compliance with requirements, provide product by Dayton/Richmond Concrete Accessories.

Retain polyethylene sheet below if required to prevent shear transfer between insulation and concrete wythe.  Polyethylene sheet may also act as a vapor retarder within the panel.

D. Polyethylene Sheet:  ASTM D 4397, 4 mils (0.10 mm) thick.

2.13 MISCELLANEOUS MATERIALS

Retain paragraph below if exposed-aggregate finish is required for face-up surface.  Do not use as a retarder for face-down, exposed-aggregate surfaces.

A. Chemical Surface Retarder:  Water-soluble, liquid set retarder with color dye, for horizontal concrete surface application, capable of temporarily delaying final hardening of concrete to depth of reveal or etch required of specified finish.

Form retarder below is used as a surface retarder for face-down, exposed-aggregate finishes.  Form retarder is often applied directly to casting slab that is cured with a curing compound and that has no bondbreaker.  Mold release may be needed under form retarder.  Consult manufacturer to verify need for mold release with form retarder and compatibility with curing compound and bondbreaker, if used.

B. Form Retarder:  Chemical liquid set retarder, for application on hardened horizontal concrete and capable of temporarily delaying final hardening of newly placed concrete to depth of reveal specified.

Retain mold release below if required for use under form retarder.

1. Mold Release:  Solution specially formulated by manufacturer for use under form retarder.

Delete embedded flashing reglets below if surface-mounted reglets are used or if reglets are not required.  Revise shape and coordinate details and locations with Drawings.

C. Flashing Reglets:  Open type having continuous groove not less than 1-1/8 inches (28 mm) deep by 3/16 inch (5 mm) wide at opening and sloped upward to 45 degrees.  Temporarily fill or cover face openings of reglets to prevent intrusion of concrete or debris.

Select reglet material from three subparagraphs below or revise if another material is required.  If retaining more than one material, indicate locations of each here or on Drawings.

1. Stainless Steel:  ASTM A 240/A 240M, Type 304, soft annealed, not less than 0.0187 inch (0.5 mm) thick.

2. Copper Strip:  ASTM B 370, Temper H00 or O60, not less than 16 oz./sq. ft. (0.55 mm thick).

3. Hot-Dip Galvanized Steel Sheet:  ASTM A 653/A 653M, G90 (Z275) coating, not less than 0.0217 inch (0.55 mm) thick.

Delete paragraph below if not required.  Indicate sizes and locations on Drawings.

D. Dovetail Anchor Slots:  Hot-dip galvanized steel sheet, not less than 0.0336 inch (0.85 mm) thick, with bent tab anchors.  Temporarily fill or cover face opening of slots to prevent intrusion of concrete or debris.

2.14 REPAIR MATERIALS

Bonding agents may be used directly from container or as an admixture in cement or sand-cement slurry.

A. Bonding Agent:  ASTM C 1059, Type II, nonredispersible, acrylic emulsion or styrene butadiene.

B. Patching Mortar:  Dry-pack mix consisting of 1 part portland cement to 2-1/2 parts fine aggregate passing No. 16 (1.18-mm) sieve, using only enough water for handling and placing.

2.15 CONCRETE MIXTURES

A. Prepare design mixtures for each type and strength of concrete, proportioned on basis of laboratory trial mixture or field test data, or both, according to ACI 301.

1. Use a qualified independent testing agency for preparing and reporting proposed concrete design mixtures based on laboratory trial mixtures.

B. Proportion concrete mixture as follows:

Select strength from options in subparagraph below or revise to suit Project.  Coordinate compressive strength with water-cementitious materials ratio if concrete will be subject to special exposure conditions or sulfate exposure as identified in ACI 318 (ACI 318M).

1. Minimum Compressive Strength:  [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] <Insert strength> at 28 days.

Select water-cementitious materials ratio from options in subparagraph below, revise to suit Project, or delete if in-service durability conditions are benign and limits on water-cementitious materials ratio are not required.  Coordinate water-cementitious materials ratio with compressive strength.

2. Maximum Water-Cementitious Materials Ratio:  [0.50] [0.45] [0.40] <Insert ratio>.

Select slump limit from options in subparagraph below or revise to suit Project.

3. Slump Limit:  [4 inches (100 mm)] [5 inches (125 mm)] [8 inches (200 mm) for concrete with verified slump of 2 to 4 inches (50 to 100 mm) before adding high-range, water-reducing admixture or plasticizing admixture] <Insert dimension>, plus or minus 1 inch (25 mm).

Percentages in options in two subparagraphs below are default air contents required by ACI 301 for severe exposure.

4. Air Content:  [5-1/2] <Insert number> percent plus or minus 1.5 percent for 1-1/2-inch (38-mm) nominal maximum aggregate size at point of delivery.

5. Air Content:  [6] <Insert number> percent plus or minus 1.5 percent for [1-inch (25-mm)] [3/4-inch (19-mm)] nominal maximum aggregate size at point of delivery.

Retain first option in subparagraph below if required for LEED-NC Credit ID 1.1.  This credit can be achieved by replacing at least 40 percent of the portland cement, which would otherwise be used in concrete, with other cementitious materials.  Retain second option if limiting percentage of cementitious materials that can replace portland cement.  Neither ACI 301 nor ACI 318 (ACI 318M) limits amount of cementitious materials that can replace portland cement unless concrete is exposed to deicing chemicals.

6. Cementitious Materials:[  Use fly ash, pozzolan, ground granulated blast-furnace slag, and silica fume as needed to reduce the total amount of portland cement, which would otherwise be used, by not less than 40 percent.][  Limit percentage, by weight, of cementitious materials other than portland cement in concrete according to ACI 301 requirements.]

Retain appropriate option for chloride limits in first paragraph below.  Percentages in options below repeat ACI 301 limits, respectively, for reinforced concrete exposed to chloride and reinforced concrete that will not be dry or protected from moisture.

C. Limit water-soluble chloride-ion content in hardened concrete to [0.15] [0.30] percent by weight of cement.

D. Admixtures:  Use admixtures according to manufacturer's written instructions.

Delete or revise two subparagraphs below to suit Project.

1. Use [water-reducing] [high-range, water-reducing] [or] [plasticizing] admixture in concrete, as required, for placement and workability.

2. Use water-reducing and retarding admixture when required by high temperatures, low humidity, or other adverse placement conditions.

Retain paragraph below if integrally colored concrete is required; indicate locations here or on Drawings.

E. Color Pigment:  Add color pigment to concrete mixture according to manufacturer's written instructions and to result in hardened concrete color consistent with approved mockup.

2.16 CONCRETE MIXING

A. Ready-Mixed Concrete:  Measure, batch, mix, and deliver concrete according to ASTM C 94/C 94M, and furnish batch ticket information.

1. When air temperature is above 90 deg F (32 deg C), reduce mixing and delivery time to 60 minutes.

Delete paragraph and subparagraph below if Project-site-produced concrete is not permitted.  ACI 301 applies measuring, batching, and mixing requirements from ASTM C 94/C 94M to this concrete.

B. Project-Site-Produced Concrete:  Measure, batch, and mix concrete according to ASTM C 94/C 94M.  Mix concrete materials in appropriate drum-type batch machine mixer.

1. Provide a batch ticket for each batch discharged and used in the Work, indicating Project identification name and number, date, mix type, mix time, quantity, and amount of water added.  Record panel locations where concrete is deposited.

PART 3 -  EXECUTION

3.1 FORMS

A. Construct and brace formwork so tilt-up concrete panels are of size, shape, alignment, elevation, and position indicated.

1. Construct forms on slab-on-grade or on temporary casting slab, at Contractor's option.

2. Provide for openings, offsets, recesses, reveals, rustications, reglets, and blockouts.

Delete subparagraph below if form liners are not used.

3. Place form liners accurately to provide finished surface texture indicated.  Provide solid backing and supports to maintain stability of liners during concreting.  Coat form liner with form-release agent.

B. Fabricate forms for easy removal without hammering or prying against concrete surfaces.  Use kerfed inserts, such as those forming reglets, rustications, and recesses, for easy removal.

C. Set edge forms for panels to achieve required panel thickness.

D. Chamfer exposed corners and edges, unless otherwise indicated, using chamfer strips fabricated to produce uniform, smooth lines and tight edge joints.

E. Coat contact surfaces of wood forms and chamfers with sealer before placing reinforcement.

3.2 BONDBREAKERS

Usually retain this Article.  For face-down, exposed-aggregate finish, a bondbreaker is usually not needed if a form retarder is used.  A bondbreaker is not needed if sand-bed method of exposing aggregate is used.

A. Uniformly and continuously apply two coats of bondbreaker to casting-slab surfaces by power spray or roller according to manufacturer's written instructions, before placing steel reinforcement.  Recoat areas subjected to moisture before drying.  Maintain continuity of coating until concrete placement.

B. After placing steel reinforcement, touch up or recoat worn or damaged areas with bondbreaker.  Do not splash or coat steel reinforcement and inserts.

3.3 FORM RETARDER

Retain this Article if face-down, exposed-aggregate finish requires a retarder.  When using a form retarder, consult manufacturer if bondbreaker is needed.  Mold release is sometimes recommended before applying form retarder, especially over bondbreaker.

A. Uniformly and continuously apply form retarder to slab surfaces by power spray, roller, or brush according to manufacturer's written instructions, before placing steel reinforcement.  Recoat areas subjected to moisture before drying.  Maintain continuity of coating until concrete placement.

Delete subparagraph below if mold release is not required.

1. Uniformly apply mold release according to manufacturer's written instructions and allow to dry before applying form retarder.

B. After placing steel reinforcement, touch up or recoat worn or damaged areas with form retarder.  Do not splash or coat steel reinforcement and inserts.

3.4 REINFORCEMENT AND INSERTS

A. General:  Comply with CRSI's "Manual of Standard Practice" for fabricating and placing reinforcement.

B. Accurately position, support, and secure reinforcement against displacement.  Locate and support reinforcement with bar supports to maintain minimum concrete cover.

Delete first subparagraph below if welding is not permitted or required.

1. Field weld reinforcement according to AWS D1.4, where indicated.

2. Do not tack-weld crossing reinforcing bars.

3. Set wire ties so ends are directed into concrete, not toward exposed concrete surfaces.

Delete first paragraph below if no welded wire reinforcement.

C. Install welded wire reinforcement in longest practicable lengths on bar supports spaced to minimize sagging.  Lap edges and ends of adjoining sheets at least one mesh spacing.  Offset laps of adjoining sheet widths to prevent continuous laps in either direction.  Lace overlaps with wire.

D. Accurately place and securely support embedded items, anchorages, inserts, cramps, retainers, bar chords and sleeves, and other items to be built into panels.  Coordinate with other trades for installing cast-in items.

Delete paragraph below if not using stainless-steel wythe connectors in sandwich panels.

E. Wythe Connectors:  Accurately place and securely support stainless-steel anchors and connecting pins for sandwich panels.

3.5 PANEL CASTING, GENERAL

A. Comply with ACI 301 for handling, placing, and consolidating concrete.

B. Maintain position of steel reinforcement, inserts, and anchors during concrete placement, consolidation, and finishing.

C. Screed panel surfaces to correct level with a straightedge and strike off.

1. Begin initial floating before excess moisture or bleedwater appears on the surface.  Use bull floats or darbies to form a uniform and open-textured surface plane free of humps or hollows.  Do not disturb panel surfaces before beginning finishing operations.

D. Form chamfers at top edges of panel perimeters, openings, and similar locations not formed by chamfer strips, unless otherwise indicated.

Select grade from options in paragraph below.  Coordinate with "Face-up Finishes" and "Face-down Finishes" articles.  If retaining more than one grade, indicate locations of each here or on Drawings.  Grade options reflect surface defects recognized by TCA's "Tilt-up Concrete Association's Guideline Specifications."  Usually retain either Grade A, the highest level, or Grade B, an intermediate level of appearance.  Limit Grade C to projects where exterior appearance does not matter.  See Evaluations for descriptions of surface defects.

E. Surface Defects:  Limit visible surface defects to those permitted by TCA's "Tilt-up Concrete Association's Guideline Specifications" for [Grade A, Architectural] [Grade B, Standard] [Grade C, Utility] panel surfaces.

3.6 SANDWICH-PANEL CASTING

Delete this Article if sandwich panels are not required.  If sandwich panels are required, retain this Article along with "Panel Casting, General" Article.

A. Cast and screed supported wythe over casting slab.

B. [Resin] [Fiber/Polymer Composite] Wythe Connectors:

1. While concrete is still plastic, place polyethylene sheet over top surface, overlapping sheet edges 6 inches (150 mm) and extending beyond edges of panels.

2. Immediately place insulation, abutting edges and ends between boards.  Stagger end joints between rows.  Stagger joints of insulation layers one-half of board apart.  Insert wythe connectors through predrilled insulation, and consolidate concrete around connectors according to manufacturer's written instructions.

C. Stainless-Steel Wythe Connectors:  Place insulation through projecting connectors, abutting edges and ends between boards.  Stagger end joints between rows.  Stagger joints of insulation layers one-half of board apart.

1. Place polyethylene sheet over insulation, overlapping edges 6 inches (150 mm) and extending beyond edges of panels.

D. Cast, screed, and apply initial float finish to structural wythe.

3.7 CASTING TOLERANCES

A. Cast tilt-up concrete panels without exceeding the following tolerances:

Tolerances in subparagraphs and associated subparagraphs below are based on TCA's "Tilt-up Concrete Association's Guideline Specifications."  Add other tolerances or revise those below to suit Project.

1. Height and Width of Panels:

a. For Panels up to 20 Feet (6.1 m) Tall:  1/4 inch (6 mm) wide.

b. For Panels 20 to 30 Feet (6.1 to 9.1 m) Tall:  3/8 inch (10 mm) wide.

c. Each Additional 10 Feet (3.05 m) in Excess of 30 Feet (9.1 m) Tall:  1/8 inch (3 mm) wide.

2. Thickness:  3/16 inch (5 mm).

3. Skew of Panel or Opening:  Difference in length of diagonals of 1/8 inch per 72 inches (3 mm per 1830 mm) with a maximum difference of 1/2 inch (13 mm).

4. Openings Cast into Panel:

a. Size of Opening:  1/4 inch (6 mm).

b. Location of Centerline of Opening:  1/4 inch (6 mm).

5. Location and Placement of Embedded Items:

a. Inserts, Bolts, and Pipe Sleeves:  3/8 inch (10 mm).

b. Lifting and Bracing Inserts:  As required by manufacturer.

c. Lateral Placement of Weld Plate Embedments:  1 inch (25 mm).

d. Tipping and Flushness of Weld Plate Embedments:  1/4 inch (6 mm).

6. Deviation of Steel Reinforcement Cover:  Maintain minimum cover required by ACI 301.

3.8 FACE-UP FINISHES

Select face-up finishes from this Article or insert another finish if required.  Upper surface of site-cast, tilt-up panels usually forms the inside of a building.  Confirm quality and appearance of finishes through mockups if required.

A. Float Finish:  Consolidate surface of plastic concrete with power-driven floats or by hand floating.  Restraighten and cut down high spots and fill low spots.  Repeat float passes and restraighten until surface is left with a uniform, smooth, granular texture.

B. Trowel Finish:  After applying float finish, apply first trowel finish and consolidate plastic concrete by hand trowel or power-driven trowel.  Continue troweling passes and restraighten until surface is free of trowel marks and is uniform in texture and appearance.

C. Trowel and Fine-Broom Finish:  After applying float finish, apply a partial trowel finish to plastic concrete, stopping after second troweling.  Immediately after second troweling, and when concrete is still plastic, slightly scarify the surface with a fine broom.

Select brooming pattern from options in subparagraph below or revise to suit Project.

1. Broom surface in a [top-to-bottom] [side-to-side] direction.

Retain one of two exposed-aggregate finish paragraphs and associated subparagraphs below if face-up surface of site-cast panel will be exposed to exterior of building.  Revise description of finishing procedure if required.

D. Brushed Exposed-Aggregate Finish:  Produce exposed-aggregate finish to exterior surface of concrete by washing and brushing before panel erection, as follows:

Delete first subparagraph below if not seeding surface with additional aggregate.

1. Immediately after floating, broadcast a single layer of aggregate uniformly onto panel surface.  Tamp seeded aggregate into plastic concrete, and float to embed aggregate with mortar cover of 1/16 inch (1.6 mm).

2. Spray chemical surface retarder on panel according to manufacturer's written instructions.

3. Cover panel surface with plastic sheeting, sealing laps with tape, and remove when ready to continue finishing operations.

4. Without dislodging aggregate, remove excess mortar by lightly brushing surface with stiff nylon-bristle broom.

5. Fine spray surface with water, and brush.  Repeat water flushing and brushing cycle until cement film is removed from aggregate surfaces to depth required.

E. Abrasive-Blast, Exposed-Aggregate Finish:  Produce exposed-aggregate finish to exterior surface of concrete by abrasive-blast finish before panel erection, as follows:

1. Immediately after floating, spray chemical surface retarder on panel surface according to manufacturer's written instructions.

Delete subparagraph above and first subparagraph below if retarder is not used with abrasive-blast finish to expose aggregate.

2. Cover with plastic sheeting, sealing laps with tape, and remove after concrete has hardened.

3. Apply abrasive-blast finish using abrasive grit, equipment, application techniques, and cleaning procedures to expose aggregate and surrounding matrix surfaces as follows:

Select degree of exposure from three subparagraphs below.

a. Light Exposure:  Expose fine aggregate with occasional exposure of coarse aggregate and uniform color; maximum reveal of 1/16 inch (1.6 mm).

b. Medium Exposure:  Generally expose coarse aggregate with slight reveal; maximum reveal of 1/4 inch (6 mm).

c. Heavy Exposure:  Expose and reveal coarse aggregate to a maximum projection of 1/3 of its diameter; reveal of 1/4 to 1/2 inch (6 to 13 mm).

Retain acid cleaning below if required to remove hazy appearance of abraded surface.

4. Acid Cleaning:  After abrasive blasting, clean surfaces with a 5 to 10 percent concentration of hydrochloric acid wash.  Thoroughly neutralize and flush acid from finished surfaces with water under pressure.  Protect casting slab and adjacent panels from acid wash.

3.9 FACE-DOWN FINISHES

Select face-down finishes from this Article or insert another finish if required.  Face-down finishes may be as-cast finishes or finishes applied to hardened concrete after panels are erected.  Confirm quality and appearance of finishes through mockups if required.  Retain descriptions of more than one finish if different finishes are required on separate portions of the same panel.  Indicate locations of each finish on Drawings.

A. Smooth, As-Cast Finish:  Cast panel to produce a surface free of pockets, sand streaks, and honeycombs.  Produce a surface appearance of uniform color and texture.

B. Form-Liner Finish:  Cast panel over form liners placed, secured, and sealed over casting slab to produce a textured surface free of pockets, streaks, and honeycombs.  Produce a surface appearance of uniform color and texture.

Select one of four paragraphs and associated subparagraphs below if exposed-aggregate finish is required.

C. Abrasive-Blast, Exposed-Aggregate Finish:  Produce exposed-aggregate finish to exterior surface of concrete by abrasive-blasting after panel erection.

1. Apply abrasive-blast finish using abrasive grit, equipment, application techniques, and cleaning procedures to expose aggregate and surrounding matrix surfaces as follows:

Select degree of exposure from three subparagraphs below.

a. Light Exposure:  Expose fine aggregate with occasional exposure of coarse aggregate and uniform color; maximum reveal of 1/16 inch (1.6 mm).

b. Medium Exposure:  Generally expose coarse aggregate with slight reveal; maximum reveal of 1/4 inch (6 mm).

c. Heavy Exposure:  Expose and reveal coarse aggregate to a maximum projection of 1/3 of its diameter; reveal of 1/4 to 1/2 inch (6 to 13 mm).

D. Brushed Exposed-Aggregate Finish:  Produce exposed-aggregate finish to exterior surface of concrete by washing and brushing after panel erection, as follows:

1. After panel erection and without dislodging aggregate, remove excess mortar by lightly brushing surface with stiff nylon-bristle broom.

2. Fine spray surface with water, and brush.  Repeat water flushing and brushing cycle until cement film is removed from aggregate surfaces to depth required.

Retain paragraph and subparagraphs below if bushhammer exposed-aggregate finish is required.  Usually limit this finish to concrete having minimum compressive strength of 4000 psi (27.6 MPa) and a minimum age of 14 days, to prevent aggregate loosening.

E. Bushhammer Exposed-Aggregate Finish:  Allow concrete to cure at least 14 days before starting bushhammer surface finish operations.

1. Surface Continuity:  Perform bushhammer finishing in as continuous an operation as possible, maintaining continuity of finish on each surface or area of Work.  Maintain required patterns or variances of cut as shown on Drawings or to match mockup.

2. Surface Cut:  Maintain required depth of cut and general aggregate exposure.  Use power tool with bushhammer attachments for large, flat surfaces, and use hand hammers for small areas, at corners and edges, and for restricted locations where power tools cannot reach.

Sand-bed method below is not often used and is reserved for exposed aggregate larger than 2 inches (50 mm).  Consider nonstructural depth of exposed aggregate in determining panel thickness.

F. Sand-Bed, Exposed-Aggregate Finish:  Place selected exposed aggregate on a sand bed over casting slab before placing reinforcement, embedments, and concrete.  After erecting panel, remove sand to expose aggregate.

3.10 CONCRETE PROTECTING AND CURING

A. Protect freshly placed concrete from premature drying and excessive cold or hot temperatures according to ACI 301.

1. Apply evaporation retarder in hot, dry, or windy weather to protect concrete from rapid moisture loss before and during finishing operations.  Apply according to manufacturer's written instructions after screeding and bull floating concrete, but before float finishing.

B. Begin curing immediately after finishing concrete.  Cure by one or a combination of the following methods according to ACI 308.1:

Select curing methods from three subparagraphs and associated subparagraphs below.  Delete other methods if restricting Contractor's range of options.

1. Moisture Curing:  Keep surfaces continuously moist for not less than seven days with the following materials:

Retain first three subparagraphs below as Contractor's options unless not suited for Project.

a. Water.

b. Continuous water-fog spray.

c. Absorptive cover, water saturated and kept continuously wet.  Cover concrete surfaces and edges with 12-inch (300-mm) lap over adjacent absorptive covers.

2. Moisture-Retaining-Cover Curing:  Cover concrete surfaces with moisture-retaining cover for curing concrete, placed in widest practicable width, with sides and ends lapped at least 12 inches (300 mm), and sealed by waterproof tape or adhesive.  Cure for not less than seven days.  Immediately repair any holes or tears during curing period, using cover material and waterproof tape.

3. Curing Compound:  Apply uniformly in continuous operation by power spray or roller according to manufacturer's written instructions.  Recoat areas subjected to heavy rainfall within three hours after initial application.  Maintain continuity of coating and repair damage during curing period.

3.11 ERECTION

A. Use erection equipment with care to prevent damage to floor slabs and panels.

B. Lift, support, and erect panels only at designated lifting or supporting points indicated on Shop Drawings.

C. Do not erect panels until[ 75 percent of] 28-day compressive strength of concrete has been verified.

Retain paragraph above or first paragraph below, revising if required.

D. Do not erect panels until verified compressive strength of concrete exceeds [2500 psi (17.2 MPa)] <Insert strength>.

E. Install tilt-up concrete panels level, plumb, square, and true.  Place panels on leveled grout-setting pads or shims in correct position.  Maintain joint width of [1/2 inch (13 mm)] [3/4 inch (19 mm)] <Insert width> between panels.

Revise subparagraph below if exposing face-up panel surfaces to exterior of building.  Traditionally, face-down panel surfaces are exposed to exterior and Contractor plans tilting procedure accordingly.

1. Install tilt-up concrete panels with face-down surfaces exposed to exterior of building.

Coordinate requirements with and indicate building's design loads on Drawings.

F. Temporarily brace and support panels securely in position against loads comparable in intensity to those for which structure was designed.  Maintain braces and supports in place, undisturbed, until entire integrated supporting structure has been completed and permanent connections to panels are secured.

G. Anchor panels in place and, if indicated, to one another.

Delete subparagraph below if no welded connections; if retaining, edit to suit Project.

1. Weld steel connectors to steel supports and embedments indicated, complying with AWS D1.1.

H. Solidly grout-fill gaps between foundation system and bottom of panels.

3.12 FIELD QUALITY CONTROL

Retain one of first two paragraphs below.

Retain first option in paragraph below if authorities having jurisdiction require Owner to engage a special inspector.  Retain last option if Owner engages testing agency, with or without a special inspector.

A. Testing and Inspecting:  Owner will engage a [special inspector] [and] [qualified testing and inspecting agency] to perform tests and inspections and to submit reports.

Retain first paragraph below if Contractor engages testing agency.

B. Testing and Inspecting:  Engage a qualified testing and inspecting agency to perform tests and inspections and to submit reports.

C. Inspections:

Retain seven subparagraphs below if special inspections are required.  Items below are examples of special inspections and are based on IBC requirements; revise to add other inspections or to suit requirements of other building codes.

1. Steel reinforcement placement.

2. Steel reinforcement welding.

3. Headed bolts and studs.

4. Verification of use of required design mixture.

5. Concrete placement, including conveying and depositing.

6. Curing procedures and maintenance of curing temperature.

7. Verification of concrete strength before erection of tilt-up panels.

D. Testing Services:  Tests shall be performed according to ACI 301.

3.13 ERECTION TOLERANCES

A. Install tilt-up concrete panels without exceeding the following erection tolerances:

Erection tolerances in subparagraphs and associated subparagraphs below are based on TCA's "Tilt-up Concrete Association's Guideline Specifications."

1. Joint Width Variation (Exterior Face):  Without decreasing or increasing more than 50 percent from specified joint width, maintain joint width as follows:

a. For Panels up to 20 Feet (6.1 m) Tall:  1/4 inch (6 mm).

b. Each Additional 10 Feet (3.05 m) in Excess of 20 Feet (6.1 m) Tall:  1/8 inch (3 mm).

2. Joint Taper:  Maximum 3/8 inch (10 mm) over length, but not greater than the following:

a. For Panels up to 20 Feet (6.1 m) Tall:  1/4 inch (6 mm).

b. Each Additional 10 Feet (3.05 m) in Excess of 20 Feet (6.1 m) Tall:  1/8 inch (3 mm)
3. Panel Alignment:

a. Alignment of Horizontal and Vertical Joints:  1/4 inch (6 mm).

b. Offset in Exterior Face of Adjacent Panels:  1/4 inch (6 mm).

3.14 FILLING AND REPAIRS

A. Patch holes and voids left by erecting and bracing inserts on tilt-up panels and slabs-on-grade.  Cut or chip edges of voids perpendicular to concrete surface.  Fill blockouts where indicated.

1. Clean, dampen with water, and brush-coat holes, voids, and blockouts with bonding agent.  Fill and compact with patching mortar of a stiff consistency before bonding agent has dried.

Delete subparagraph below if a matching repair finish is not required.

2. Finish surfaces of fills and repairs to Architect's approval, with materials of same colors and textures as finishes on surrounding surfaces.

Delete galvanized steel repairs in first paragraph below if not required.

B. Repair damaged galvanized steel surfaces of connectors by cleaning and applying a coat of zinc repair paint.

C. Repair damage to tilt-up panels and slabs-on-grade resulting from tilt-up work, as directed by Architect.

D. Remove and replace tilt-up panels that do not comply with requirements in this Section.

E. Demolish and remove temporary concrete casting slabs.

END OF SECTION 03471END OF SECTION 03471

TILT-UP CONCRETE
03471 - 1

