Copyright 2005 AIA
MASTERSPEC Full Length
08/05 (R 02/06)

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 07141 - COLD FLUID-APPLIED WATERPROOFING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Single-component polyurethane waterproofing.

2. Two-component polyurethane waterproofing.

3. Polyester waterproofing.

4. Latex-rubber waterproofing.

5. Molded-sheet drainage panels.

6. Insulation.

7. Plaza deck pavers.

B. Related Section:

Retain subparagraph below for requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 7 Section "Joint Sealants" for joint-sealant materials and installation.

1.3 SUBMITTALS

First three paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of product indicated.  Include manufacturer's written instructions for evaluating, preparing, and treating substrate, technical data, and tested physical and performance properties of waterproofing.

B. Shop Drawings:  Show locations and extent of waterproofing.  Include details for substrate joints and cracks, sheet flashings, penetrations, inside and outside corners, tie-ins with adjoining waterproofing, and other termination conditions.

Retain subparagraph below if using pedestal-supported concrete pavers on plaza decks over waterproofing.

1. Include setting drawings showing layout, sizes, sections, profiles, and joint details of pedestal-supported concrete pavers.

C. Samples:  For the following products:

In subparagraphs below, delete samples not required.  Insert number or revise size of Samples if applicable.

1. Flashing sheet, 10 by 8 inches (250 by 200 mm).

2. Membrane-reinforcing fabric, 10 by 8 inches (250 by 200 mm).

3. Insulation, 10 by 8 inches (250 by 200 mm).

4. Drainage panel, 4 by 4 inches (100 by 100 mm).

5. Plaza deck paver, [4 by 4 inches (100 by 100 mm) square] [full sized] in each color and texture required.

6. Paver pedestal assembly.

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

D. Qualification Data:  For Installer.

E. Product Test Reports:  For waterproofing, based on evaluation of comprehensive tests performed by a qualified testing agency.

F. Field quality-control reports.

G. Warranty:  Sample of special warranty.

1.4 QUALITY ASSURANCE

Delete first paragraph below if not applicable.  For warranty purposes, a manufacturer may qualify an installer.  Coordinate selections in paragraph with qualifications manufacturer requires of Installer.  Retain first option if manufacturer approves or licenses Installer.  Retain second option if placing minimal restrictions on Installer.

A. Installer Qualifications:  A firm that is [approved or licensed by] [acceptable to] waterproofing manufacturer for installation of waterproofing required for this Project.

Select applicable products from options in first paragraph below.  Insert other products if required.

B. Source Limitations:  Obtain waterproofing materials[, protection course] [and] [molded-sheet drainage panels] from single source from single manufacturer.

Delete first paragraph below if not required.  If retaining, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise wording if only one mockup is required.  If not using pavers, delete optional sentence.

C. Mockups:  Before beginning installation, install waterproofing to 100 sq. ft. (9.3 sq. m) <Insert area>of [deck] [wall] to demonstrate surface preparation, crack and joint treatment, corner treatment, thickness, texture, and execution quality.[  Install pavers and paver supports to demonstrate aesthetic effects and set quality standards for materials and execution.]

If not using pavers, delete option in first subparagraph below.

1. If Architect determines mockups do not comply with requirements, reapply waterproofing[ and reinstall overlaying construction] until mockups are approved.

2. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

Retain subparagraph below if mockups are erected as part of building rather than erected separately and the intention is to make an exception to the default requirement in Division 1 Section "Quality Requirements" for demolishing and removing mockups when directed unless otherwise indicated.

3. Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

Retain paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

D. Preinstallation Conference:  Conduct conference at [Project site]<Insert location>.

1. Review waterproofing requirements including surface preparation, substrate condition and pretreatment, minimum curing period, forecasted weather conditions, special details and flashings, installation procedures, testing and inspection procedures, and protection and repairs.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Deliver liquid materials to Project site in original containers with seals unbroken, labeled with manufacturer's name, product brand name and type, date of manufacture, shelf life, and directions for storing and mixing with other components.

B. Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by waterproofing manufacturer.

C. Remove and replace liquid materials that cannot be applied within their stated shelf life.

D. Protect stored materials from direct sunlight.

1.6 PROJECT CONDITIONS

Revise first paragraph below if waterproofing type can accommodate other environmental conditions.

A. Environmental Limitations:  Apply waterproofing within the range of ambient and substrate temperatures recommended by waterproofing manufacturer.  Do not apply waterproofing to a damp or wet substrate, when relative humidity exceeds 85 percent, or when temperatures are less than 5 deg F (3 deg C) above dew point.

1. Do not apply waterproofing in snow, rain, fog or mist, or when such weather conditions are imminent during application and curing period.

B. Maintain adequate ventilation during application and curing of waterproofing materials.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.  Manufacturers' warranties vary; some offer a materials-only warranty, others a labor-and-material warranty.  Example in first paragraph below is a labor-and-material warranty; if a separate special installer's warranty is needed, delete option for Installer to jointly sign manufacturer's warranty.  Most manufacturers' warranties do not include costs of exposing the waterproof membrane on plaza decks or below-grade walls.

A. Special Manufacturer's Warranty:  Manufacturer's standard form in which waterproofing manufacturer[ and Installer] agree to repair or replace waterproofing that does not comply with requirements or that fails to remain watertight within specified warranty period.

1. Warranty does not include failure of waterproofing due to failure of substrate prepared and treated according to requirements or formation of new joints and cracks in substrate that exceed 1/16 inch (1.6 mm) in width.

Verify available warranties and warranty periods with manufacturers listed in Part 2 articles.

2. Warranty Period:  [Five] <Insert number> years from date of Substantial Completion.

Retain paragraph below if a Special Installer's Warranty is required and if this is an accepted practice locally.  Usually retain Special Manufacturer's Warranty above with Special Installer's Warranty below.  Coordinate requirements of both special warranties to clarify responsibilities.  If a specific installer's warranty form is required, see Division 7 low-slope roofing Sections for an example that may be modified for waterproofing and inserted at the end of this Section.

B. Special Installer's Warranty:  Specified form, [on warranty form at end of this Section, ]signed by Installer, covering Work of this Section, for warranty period of [two] <Insert number> years.

Retain subparagraph below for plaza decks if applicable; revise if necessary.

1. Warranty includes removing and reinstalling protection board, drainage panels, insulation, pedestals, and pavers on plaza decks.

PART 2 -  PRODUCTS

2.1 SINGLE-COMPONENT POLYURETHANE WATERPROOFING

Retain option in first paragraph below if manufacturers can confirm compliance with ASTM C 836.

A. Single-Component, Modified Polyurethane Waterproofing:  Comply [with ASTM C 836 and ]with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Some modified polyurethane membranes may not comply with all physical requirements in ASTM C 836 (e.g., hardness).  Verify with selected manufacturers if applicable.

a. American Permaquik Inc.; PQ 6800.

b. Anti-Hydro International, Inc.; A-H Seamless Membrane.

c. Carlisle Coatings & Waterproofing Inc.; CCW-525.

d. CETCO; LDC 60.

e. Degussa Building Systems; HLM 5000.

f. Karnak Corporation; One-Kote System.

g. Meadows, W.R., Inc.; Sealtight Meadow-Pruf Seamless

h. Mer-Kote Products, Inc.; Mer-Thane 320.

i. Neogard, Div. of Jones-Blair; Neogard 7401.

j. Pacific Polymers International, Inc.; [Elasto-Deck B.T.] [Elasto-Deck B.T. 100% Solids] [Elasto-Deck B.T. H20].

k. Tremco Incorporated; [Tremproof 60] [Vulkem 250 GC] [Vulkem 201].

l. United Coatings; Elastall 1000.

m. <Insert manufacturer's name; product name or designation>.

Retain option in first paragraph below if manufacturer can confirm compliance with ASTM C 836.

B. Single-Component, Reinforced, Modified Polyurethane Waterproofing:  Comply [with ASTM C 836 and ]with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Some modified polyurethane membranes may not comply with all physical requirements in ASTM C 836.  Verify with selected manufacturer if applicable.

a. Carlisle Coatings & Waterproofing Inc.; CCW-525-H.

b. <Insert manufacturer's name; product name or designation>.

C. Single-Component, Unmodified Polyurethane Waterproofing:  Comply with ASTM C 836 and with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. 3M; Scotch Clad 5893/5864.

b. Tremco Incorporated; Vulkem 101.

c. <Insert manufacturer's name; product name or designation>.

2.2 TWO-COMPONENT POLYURETHANE WATERPROOFING

A. Two-Component, Modified Polyurethane Waterproofing:  Comply with ASTM C 836 and with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Gaco Western Inc.; LM-60.

b. Tremco Incorporated; Vulkem 222.

c. <Insert manufacturer's name; product name or designation>.

B. Two-Component, Unmodified Polyurethane Waterproofing:  Comply with ASTM C 836 and with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Carlisle Coatings & Waterproofing Inc.; CCW 703 Liquiseal.

b. Pacific Polymers International, Inc.; [Elasto-Deck B.T. 1000] [Elasto-Deck B.T. Two-Component].

c. 3M; FC 100.

d. Tremco Incorporated; Vulkem 102.

e. <Insert manufacturer's name; product name or designation>.

Retain option in paragraph below if manufacturer can confirm compliance with ASTM C 836.

C. Two-Component, Reinforced, Unmodified Polyurethane Waterproofing:  Comply [with ASTM C 836 and ]with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Kemper System, Inc.; Kemperol 2K-PUR.

b. <Insert manufacturer's name; product name or designation>.

2.3 POLYESTER WATERPROOFING

Retain option in paragraph below if manufacturers can confirm compliance with ASTM C 836.

A. Two-Component, Reinforced, Unsaturated Polyester Waterproofing:  Comply [with ASTM C 836 and ]with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Kemper System, Inc.;  Kemperol BR.

b. Landmark Products, Inc.; Triflex D.

c. <Insert manufacturer's name; product name or designation>.

2.4 LATEX-RUBBER WATERPROOFING

Retain option in first paragraph below if manufacturer can confirm compliance with ASTM C 836.

A. Two-Component, Unreinforced, Latex-Rubber Waterproofing:  Comply [with ASTM C 836 and ]with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Grace, W. R. & Co.; Procor.

b. <Insert manufacturer's name; product name or designation>.

Retain option in paragraph below if manufacturer can confirm compliance with ASTM C 836.

B. Two-Component, Reinforced, Latex-Rubber Waterproofing:  Comply [with ASTM C 836 and ]with manufacturer's written physical requirements.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Grace, W. R. & Co.; Procor Deck System 3R.

b. <Insert manufacturer's name; product name or designation>.

2.5 AUXILIARY MATERIALS

A. General:  Provide auxiliary materials recommended by manufacturer to be compatible with one another and with waterproofing, as demonstrated by waterproofing manufacturer, based on testing and field experience.

B. Primer:  Manufacturer's standard, factory-formulated polyurethane or epoxy primer.

Usually retain sheet flashings for unreinforced, single- or two-component polyurethane waterproofing.

C. Sheet Flashing:  50-mil- (1.3-mm-) minimum, nonstaining, uncured sheet neoprene.

1. Adhesive:  Manufacturer's recommended contact adhesive.

Retain first paragraph below if reinforced waterproofing is required.  Verify weight of reinforcing fabric recommended by manufacturer for application.  First two options are based on Kemper System's product data, second on Landmark Products' data.

D. Membrane-Reinforcing Fabric:  Nonwoven, needle-punched white polyester fabric, [6-oz./sq. yd. (200-g/sq. m)] [5-oz./sq. yd. (169-g/sq. m)] [3.2-oz./sq. yd. (109-g/sq. m)] [manufacturer's standard] weight.

E. Joint Reinforcing Strip:  Manufacturer's recommended fiberglass mesh or polyester fabric.

F. Joint Sealant:  Multicomponent polyurethane sealant, compatible with waterproofing, complying with ASTM C 920 Type M, Class 25; Grade NS for sloping and vertical applications or Grade P for deck applications; Use NT exposure; and as recommended by manufacturer for substrate and joint conditions.

1. Backer Rod:  Closed-cell polyethylene foam.

2.6 PROTECTION COURSE

Retain one or more types of protection course in this article if applicable.  Delete this article if molded-sheet drainage panels or insulation drainage panels will replace protection course.  Verify acceptability of type of protection course with waterproofing manufacturer. If more than one type of protection course is required, indicate locations such as plaza deck and foundation walls.

Protection course in first paragraph below is manufactured by W. R. Meadows and is also available from a number of other waterproofing manufacturers.

A. Protection Course:  ASTM D 6506, semirigid sheets of fiberglass or mineral-reinforced-asphaltic core, pressure laminated between two asphalt-saturated fibrous liners and as follows:

Retain one of first two subparagraphs below.

1. Thickness:  [1/8 inch (3 mm)] [1/4 inch (6 mm)], nominal.

2. Thickness:  1/8 inch (3 mm), nominal, for vertical applications; 1/4 inch (6 mm), nominal, elsewhere.

3. Adhesive:  Rubber-based solvent type recommended by waterproofing manufacturer for type of protection course.

First option in first paragraph below describes Dow Chemical Company's "Protection Board III"; last option describes Pactiv's "Green Guard PB4."

B. Protection Course:  Fan folded, with a core of extruded-polystyrene board insulation faced [one] [or] [both] side(s) with plastic film, nominal thickness of 1/4 inch (6 mm), with compressive strength not less than 8 psi (55 kPa) per ASTM D 1621 and maximum water absorption by volume of 0.6 percent per ASTM C 272.

First paragraph below describes Owens Corning's "Fanfold DWB."

C. Protection Course:  Unfaced, fan-folded, rigid, extruded-polystyrene board insulation; nominal thickness of 1/4 inch (6 mm) with compressive strength of not less than 8 psi (55 kPa) per ASTM D 1621.

First paragraph below describes Insulfoam's "R-Tech Fanfold."  Retain applicable thickness option.

D. Protection Course:  Fan folded, with a core of molded-polystyrene board insulation faced both sides with plastic film, nominal thickness of [1/4 inch (6 mm)] [3/8 inch (9.5 mm)] [1/2 inch (13 mm)], with compressive strength not less than 12 psi (83 kPa) per ASTM D 1621 and water absorption by volume of less than 1 percent per ASTM C 272.

First paragraph below describes Owens Corning's "Foamular Half-Inch."

E. Protection Course:  Unfaced, extruded-polystyrene board insulation; ASTM C 578, Type X, 1/2 inch (13 mm) thick.

F. Protection Course:  Molded-polystyrene board insulation, ASTM C 578, Type I, 0.90-lb/cu. ft. (15-kg/cu. m) minimum density, 1-inch (25-mm) minimum thickness.

2.7 MOLDED-SHEET DRAINAGE PANELS

Retain this article if molded-sheet drainage panels are required.  Retain first paragraph below if molded-sheet drainage panel products are specified in another Section.

A. Molded-Sheet Drainage Panel:  Comply with Division 2 Section "Subdrainage."

Retain one or both paragraphs below if specifying drainage panels in this Section.  Retain first paragraph if specifying nonwoven-geotextile-faced drainage panels, usually for foundation walls.

B. Nonwoven-Geotextile-Faced, Molded-Sheet Drainage Panel: Manufactured composite subsurface drainage panels consisting of a nonwoven, needle-punched geotextile facing with an apparent opening size not exceeding No. 70 (0.21-mm) sieve laminated to one side[ with] [or] [without] a polymeric film bonded to the other side of a studded, nonbiodegradable, molded-plastic-sheet drainage core, with a vertical flow rate of 9 to 15 gpm per ft. (112 to 188 L/min. per m).

Retain paragraph below if specifying woven-geotextile-faced drainage panels, usually for plaza decks.

C. Woven-Geotextile-Faced, Molded-Sheet Drainage Panel: Manufactured composite subsurface drainage panels consisting of a woven-geotextile facing with an apparent opening size not exceeding No. 40 (0.43-mm) sieve, laminated to one side[ with] [or] [without] a polymeric film bonded to the other side of a studded, nonbiodegradable, molded-plastic-sheet drainage core, with a horizontal flow rate not less than 2.8 gpm per ft. (35 L/min. per m).

2.8 INSULATION

Retain first paragraph below if board insulation is required over waterproofing and if board insulation forms the first layer beneath an insulation drainage panel.

A. Board Insulation:  Extruded-polystyrene board insulation complying with ASTM C 578, [square] [or] [shiplap] edged.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. DiversiFoam Products.

b. Dow Chemical Company (The).

c. Owens Corning.

d. Pactiv Corporation.

e. T. Clear Corporation.

f. <Insert manufacturer's name>.

Type IV and Type VI insulation in first two subparagraphs below are usually limited to vertical applications.  Type VII and Type V insulation, with higher compressive strengths, are used on plaza decks.

2. Type IV, 25-psi (173-kPa) minimum compressive strength.

3. Type VI, 40-psi (276-kPa) minimum compressive strength.

4. Type VII, 60-psi (414-kPa) minimum compressive strength.

5. Type V, 100-psi (690-kPa) minimum compressive strength.

Retain first paragraph below for unfaced insulation drainage panels for foundation wall applications.  DiversiFoam's "CertiFoam 25 Drainage Board," Dow's "Perimate," and Pactiv's "Green-Guard-DC" are Type IV.  DiversiFoam's "CertiFoam 40 Drainage Board" is Type VI.

B. Unfaced, Wall Insulation Drainage Panels:  Extruded-polystyrene board insulation complying with ASTM C 578, [Type IV, 25-psi (173-kPa)] [Type VI, 40-psi (276-kPa)] minimum compressive strength; unfaced; fabricated with shiplap or channel edges and with one side having grooved drainage channels.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. DiversiFoam Products; CertiFoam [25] [40] Drainage Board.

b. Dow Chemical Company (The); Perimate.

c. Pactiv Corporation; Green-Guard-DC.

d. <Insert manufacturer's name; product name or designation>.

Retain first paragraph below for geotextile-faced insulation drainage panels for foundation wall applications.  Owens Corning's "Insul-Drain" and T. Clear's "Thermadry 750" are Type IV; T. Clear's "Thermadry 1250" is Type VI.

C. Geotextile-Faced, Wall Insulation Drainage Panels:  Extruded-polystyrene board insulation complying with ASTM C 578, [Type IV, 25-psi (173-kPa)] [Type VI, 40-psi (276-kPa)] minimum compressive strength; fabricated with tongue-and-groove edges and with one side having grooved drainage channels faced with a nonwoven-geotextile filter fabric.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Owens Corning; Insul-Drain.

b. T. Clear Corporation; Thermadry [750] [1250].

c. <Insert manufacturer's name; product name or designation>.

Retain first paragraph below for plaza deck applications if unfaced insulation drainage panels with ribbed drainage channels are required.  Retain Type VI insulation for limited, intermittent pedestrian traffic; retain Type VII for heavier pedestrian traffic.  Dow's "Styrofoam Ribbed Roofmate" and Owens Corning's "Foamular 404 RB" are Type VI; DiversiFoam's "Certifoam Plaza Deck" and Owens Corning's "Foamular 604 RB" are Type VII.

D. Unfaced, Plaza Deck, Insulation Drainage Panels:  Extruded-polystyrene board insulation complying with ASTM C 578, [Type VI, 40-psi (276-kPa)] [Type VII, 60-psi (414-kPa)] minimum compressive strength; unfaced; fabricated with shiplapped or channel edges and with one side having ribbed drainage channels.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. DiversiFoam Products; CertiFoam Plaza Deck.

b. Dow Chemical Company (The); Styrofoam Ribbed Roofmate.

c. Owens Corning; [Foamular 404 RB] [Foamular 604 RB].

d. <Insert manufacturer's name; product name or designation>.

Retain paragraph below if Type VII geotextile-faced insulation is required for heavy pedestrian traffic.

E. Geotextile-Faced, Plaza Deck, Insulation Drainage Panels:  Extruded-polystyrene board insulation complying with ASTM C 578, Type VII, 60-psi (414-kPa) minimum compressive strength; fabricated with tongue-and-groove edges and with one side having grooved drainage channels faced with manufacturer's standard, nonwoven-geotextile filter fabric.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Products:  Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. T. Clear Corporation; Thermadry 1750.

b. <Insert manufacturer's name; product name or designation>.

2.9 PLAZA DECK PAVERS

Retain this article if plaza deck pavers are required.  Retain one of first two paragraphs below if cross-referencing paver materials from other Sections.

A. Plaza Deck Pavers:  [Brick] [Concrete] [Asphalt-block] pavers specified in Division 2 Section "Unit Pavers."

B. Plaza Deck Pavers:  [Granite] [Limestone] [Marble] [Quartz-based stone] [Slate] pavers specified in Division 9 Section "Stone Paving and Flooring."

Delete both paragraphs above and retain first paragraph below if plaza deck concrete pavers are required.  Verify availability of deck pavers with characteristics selected.  Paragraph below describes concrete pavers commonly used in pedestal set applications over insulation and waterproofing or for placing on a setting bed.  Limit pedestal systems to pedestrian plazas.

C. Plaza Deck Pavers:  Heavyweight, hydraulically pressed, concrete units, [square edged] [with top edges beveled 3/16 inch (5 mm)], manufactured for use as plaza deck pavers; minimum compressive strength of [7500 psi (52 MPa)] [6500 psi (45 MPa)] <Insert value>, ASTM C 140; absorption not greater than 5 percent, ASTM C 140; no breakage and maximum 1 percent mass loss when tested for freeze-thaw resistance according to ASTM C 67.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Hanover Architectural Products.

b. Hastings Pavement Company, LLC.

c. Roofblok Ltd.

d. Sunny Brook Pressed Concrete Co.

e. Wausau Tile, Inc.; Terra-Paving Div.

f. Westile Roofing Products.

g. <Insert manufacturer's name>.

Select one thickness and one face size from options in first two subparagraphs below.  Include special paver sizes and insert descriptions of custom pavers such as stair tread and riser units, coping or curbed termination pavers, and oversize pavers.

3. Thickness:  [1-5/8 inches (41 mm)] [1-3/4 inches (45 mm)] [2 inches (51 mm)] [2-3/8 inches (60 mm)] <Insert dimension>.

4. Face Size:  [8-7/8 inches (225 mm) square] [9 inches (229 mm) square] [9-by-18 inches (229-by-457 mm)] [12 inches (305 mm) square] [12-by-24 inches (305-by-610 mm)] [18 inches (457 mm) square] [24 inches (610 mm) square] [As indicated] <Insert dimensions and shape>.

5. Color:  [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

Delete first paragraph below if using pedestal systems for paver supports.

D. Setting Bed:  Provide [aggregate] [mortar] [bituminous] setting-bed materials specified in Division 2 Section "Unit Pavers."

Delete paragraph below if setting-bed systems are required.

E. Paver Pedestals:  Paver manufacturer's standard SBR rubber, high-density polyethylene, or polyurethane paver support assembly, including [fixed-height] [adjustable or stackable] pedestals, shims, and spacer tabs for joint spacing of [1/8 inch (3 mm)] [3/16 inch (5 mm)] [1/8 to 3/16 inch (3 to 5 mm)].

Retain one of first two subparagraphs below and insert list of manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. <Insert manufacturer's name>.

Retain subparagraph below if specifying Wausau Tile, Inc.'s "Terr-Adjust" tilting and telescoping pedestals.

3. Concrete Fill:  ACI 301, compressive strength of 5000 psi (34 MPa) at 28 days and air content of 6 percent.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements and other conditions affecting performance.

1. Verify that concrete has cured and aged for minimum time period recommended by waterproofing manufacturer.

2. Verify that substrate is visibly dry and free of moisture.  Test for capillary moisture by plastic sheet method according to ASTM D 4263.

3. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 SURFACE PREPARATION

A. Clean and prepare substrate according to manufacturer's written recommendations.  Provide clean, dust-free, and dry substrate for waterproofing application.

B. Mask off adjoining surfaces not receiving waterproofing to prevent spillage or overspray affecting other construction.

C. Close off deck drains and other deck penetrations to prevent spillage and migration of waterproofing fluids.

D. Remove grease, oil, bitumen, form-release agents, paints, curing compounds, acid residues, and other penetrating contaminants or film-forming coatings from concrete.

Retain subparagraph below for decks if a controlled substrate surface finish is needed for waterproofing adhesion.

1. Abrasive blast clean concrete surfaces uniformly to expose top surface of fine aggregate according to ASTM D 4259 with a self-contained, recirculating, blast-cleaning apparatus.  Remove material to provide a sound surface free of laitance, glaze, efflorescence, curing compounds, concrete hardeners, or form-release agents.  Remove remaining loose material and clean surfaces according to ASTM D 4258.

E. Remove fins, ridges, and other projections and fill honeycomb, aggregate pockets, and other voids.

3.3 PREPARATION AT TERMINATIONS AND PENETRATIONS

Retain first option in first paragraph below for plaza and horizontal decks; retain second option for vertical surfaces such as planters and foundation walls.

A. Prepare vertical and horizontal surfaces at terminations and penetrations through waterproofing and at expansion joints, drains, and sleeves according to [ASTM C 898] [ASTM C 1471] and manufacturer's written instructions.

B. Prime substrate unless otherwise instructed by waterproofing manufacturer.

C. Apply waterproofing in two separate applications, and embed a joint reinforcing strip in the first preparation coat when recommended by waterproofing manufacturer.

1. Provide sealant cants around penetrations and at inside corners of deck-to-wall butt joints when recommended by waterproofing manufacturer.

3.4 JOINT AND CRACK TREATMENT

Retain first option in first paragraph below for plaza and horizontal decks; retain second option for vertical surfaces such as planters and foundation walls.

A. Prepare, treat, rout, and fill joints and cracks in substrate according to [ASTM C 898] [ASTM C 1471] and waterproofing manufacturer's written instructions.  Remove dust and dirt from joints and cracks, complying with ASTM D 4258, before coating surfaces.

1. Comply with ASTM C 1193 for joint-sealant installation.

2. Apply bond breaker between sealant and preparation strip.

3. Prime substrate and apply a single thickness of preparation strip extending a minimum of 3 inches (75 mm) along each side of joint.  Apply waterproofing in two separate applications and embed a joint reinforcing strip in the first preparation coat.

Revise paragraph below if expansion-joint gaskets or expansion-joint cover assemblies are used.

B. Install sheet flashing and bond to deck and wall substrates where indicated or required according to waterproofing manufacturer's written instructions.

1. Extend sheet flashings onto perpendicular surfaces and other work penetrating substrate according to ASTM C 898.

3.5 WATERPROOFING APPLICATION

Retain first option in first paragraph below for plaza and horizontal decks; retain second option for vertical surfaces such as planters and foundation walls.

A. Apply waterproofing according to [ASTM C 898] [ASTM C 1471] and manufacturer's written instructions.

B. Start installing waterproofing in presence of manufacturer's technical representative.

C. Apply primer over prepared substrate.

D. Unreinforced Waterproofing Applications:  Mix materials and apply waterproofing by spray, roller, notched squeegee, trowel, or other application method suitable to slope of substrate.

Generally retain first option in first subparagraph below for polyurethane waterproofing; retain second option for two-coat, unreinforced latex rubber used in limited-height vertical applications.

1. Apply one or more coats of waterproofing to obtain a seamless membrane free of entrapped gases, with an average dry film thickness of [60 mils (1.5 mm) and a minimum dry film thickness of 50 mils (1.3 mm) at any point] [120 mils (3 mm)] <Insert thickness>.

2. Apply waterproofing to prepared wall terminations and vertical surfaces.

3. Verify wet film thickness of waterproofing every 100 sq. ft. (9.3 sq. m).

E. Reinforced Waterproofing Applications:  Mix materials and apply waterproofing by roller, notched squeegee, trowel, or other suitable application method.

Coordinate total thickness of waterproofing membrane with weight of membrane-reinforcing fabric and type of waterproofing.  First two options in first subparagraph below are based on product data from polyester waterproofing manufacturer; third option is based on product data from latex-rubber waterproofing manufacturer.  Verify thickness required for application with manufacturer.

1. Apply first coat of waterproofing, embed membrane-reinforcing fabric, and apply second coat of waterproofing to completely saturate reinforcing fabric and to obtain a seamless reinforced membrane free of entrapped gases, with an average dry film total thickness of [70 mils (1.8 mm)] [80 mils (2 mm)] [120 mils (3 mm)] <Insert thickness>.

2. Apply reinforced waterproofing to prepared wall terminations and vertical surfaces.

3. Verify wet film thickness of waterproofing every 100 sq. ft. (9.3 sq. m).

F. Install protection course with butted joints over nominally cured membrane before starting subsequent construction operations.

Retain applicable options in subparagraph below if drainage panels or board insulation will be used and are permitted by waterproofing manufacturer to replace protection course.

1. [Molded-sheet drainage panels] [Insulation drainage panels] [Board insulation] may be used in place of a separate protection course to vertical applications when approved by waterproofing manufacturer.

3.6 MOLDED-SHEET DRAINAGE PANEL INSTALLATION

A. Place and secure molded-sheet drainage panels, with geotextile facing away from wall or deck substrate, according to manufacturer's written instructions.  Use adhesives[ or mechanical fasteners] that do not penetrate waterproofing.  Lap edges and ends of geotextile fabric to maintain continuity.  Protect installed molded-sheet drainage panels during subsequent construction.

Retain subparagraph below if board insulation or protection course is installed before installing molded-sheet drainage panels.

1. For vertical applications, install [board insulation] [protection course] before installing drainage panels.

3.7 INSULATION INSTALLATION

A. Install [one or more layers of board insulation to achieve required thickness] [insulation drainage panels] over waterproofed surfaces.  Cut and fit to within 3/4 inch (19 mm) of projections and penetrations.

Delete first paragraph below if support is not required during backfilling.

B. On vertical surfaces, set insulation units in adhesive applied according to manufacturer's written instructions.  Use type of adhesive recommended in writing by insulation manufacturer.

C. On horizontal surfaces, place insulation units unadhered according to manufacturer's written instructions.  Stagger end joints and tightly abut insulation units.

3.8 PLAZA DECK PAVER INSTALLATION

Delete first paragraph below if using paver pedestal supports.

A. Setting Bed:  Install setting bed in locations and of thickness indicated to comply with requirements in [Division 2 Section "Unit Pavers."] [Division 9 Section "Stone Paving and Flooring."]

B. Install concrete pavers, in locations indicated, according to manufacturer's written instructions.

Retain first two paragraphs below if setting pavers on paver pedestals.

C. Accurately install [fixed] [adjustable]-height paver pedestals in locations and to elevations required.  Adjust for final level and slope with shims.

Delete concrete fill in subparagraph below unless using Wausau Tile's tilting and telescoping paver pedestals.

1. Fill paver pedestal with concrete mix, strike smooth with top of pedestal, and cure according to ACI 301.

D. Loosely lay pavers on pedestals, maintaining a uniform open joint width.  Tightly seat pavers against spacers to eliminate lateral movement or drift of paving assembly.  Align joint patterns parallel in each direction.

Revise subparagraph below to suit Project.  Consider paved area layout, paver module, and construction tolerances when imposing limits.  Verify minimum dimensions with paver manufacturer.  Minimum pedestal dimensions may also govern.  Custom-dimensioned pavers or pavers scored to repeat module may be available.

1. Lay out pavers to avoid less-than-half-width pavers at perimeter or other terminations.

Insert special installation requirements here.  Examples might include tread/riser units on tabs or treatment of pavers at plaza/building expansion joints.

E. Install pavers to not vary more than 1/16 inch (1.6 mm) in elevation between adjacent pavers or more than 1/16 inch (1.6 mm) from surface plane elevation of individual paver.

F. Maintain tolerances of paving installation within [1/4 inch in 10 feet (1:48)] <Insert surface tolerance> of surface plane in any direction.

3.9 FIELD QUALITY CONTROL

Retain first paragraph below if a manufacturer's site representative is required.  Manufacturer may also require this as a warranty condition.

A. Engage a full time site representative qualified by the waterproofing membrane manufacturer to inspect substrate conditions, surface preparation, and application of the membrane, flashings, protection, and drainage components; and to furnish daily reports to Architect.

Delete first paragraph below if waterproofing is limited to vertical applications.  Revise paragraph by identifying particular areas on Project to flood test.  Limit water depth to not exceed load capacity of deck.

B. Flood Testing:  Flood test each deck area for leaks, according to recommendations in ASTM D 5957, after completing waterproofing but before overlaying construction is placed.  Install temporary containment assemblies, plug or dam drains, and flood with potable water.

1. Flood to an average depth of 2-1/2 inches (64 mm) with a minimum depth of 1 inch (25 mm) and not exceeding a depth of 4 inches (100 mm).  Maintain 2 inches (50 mm) of clearance from top of sheet flashings.

ASTM D 5957 sets 24 hours as minimum and 72 hours as maximum duration for flood testing.

2. Flood each area for [24] [48] [72] hours.

3. After flood testing, repair leaks, repeat flood tests, and make further repairs until waterproofing installation is watertight.

C. [Owner will engage] [Engage] an independent testing agency to observe flood testing and examine underside of decks and terminations for evidence of leaks during flood testing.

3.10 CURING, PROTECTION, AND CLEANING

A. Cure waterproofing according to manufacturer's written recommendations, taking care to prevent contamination and damage during application stages and curing.

Retain subparagraph below for horizontal applications.

1. Do not permit foot or vehicular traffic on unprotected membrane.

B. Protect waterproofing from damage and wear during remainder of construction period.

Retain first paragraph below if board insulation or insulation drainage panels are required and may be exposed for a period on plaza decks.

C. Protect installed [board insulation] [insulation drainage panels] from damage due to ultraviolet light, harmful weather exposures, physical abuse, and other causes.  Immediately after installation, provide temporary coverings where insulation will be subject to abuse and cannot be concealed and protected by permanent construction.

D. Clean spillage and soiling from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

Insert Special Installer's Warranty Form here if required.

END OF SECTION 07141

COLD FLUID-APPLIED WATERPROOFING
07141 - 1

