Copyright 2004 AIA
MASTERSPEC Full Length
05/04 (R 05/06)

Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 14240 - HYDRAULIC ELEVATORS
This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

Edit first paragraph below to suit Project.  The term "freight elevator" is defined in ASME A17.1 to mean elevators used primarily for carrying freight and not accessible to the general public.  ASME A17.1 does not have the same requirements for freight elevators as for passenger elevators, so it is important to use proper terminology.  Elevators used both for passenger service and for moving freight, often called "service elevators," are passenger elevators, even though car finishes may be similar to freight elevators.

A. This Section includes hydraulic [passenger] [and] [service] elevators.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 2 Section "Earthwork" for excavating well hole to accommodate cylinder assembly.

Delete subparagraph above and retain subparagraph below if elevator work includes cylinder excavation (normally part of elevator work).  Delete both subparagraphs if in-ground cylinder is not used.

2. Division 2 Section "Earthwork" for disposition of excavated material from cylinder well hole.

Retain one or more of first four subparagraphs and associated subparagraphs below, depending on building structure.

3. Division 3 Section "Cast-in-Place Concrete" for setting sleeves, inserts, and anchoring devices in concrete.

4. Division 4 Section "Unit Masonry Assemblies" for setting sleeves, inserts, and anchoring devices in masonry and for grouting elevator entrance frames installed in masonry walls.

5. Division 5 Section "Structural Steel" for the following:

a. Attachment plates, angle brackets, and other preparation of structural steel for fastening guide-rail brackets.

Delete subparagraph below if only one elevator or one elevator per shaft.

b. Divider beams.

Delete first subparagraph below if not required.

c. Hoist beams.

d. Structural-steel shapes for subsills that are part of steel frame.

For concrete frame buildings, delete subparagraph and associated subparagraphs above and retain subparagraph and appropriate associated subparagraphs below.

For steel frame buildings, retain subparagraph and associated subparagraphs above for items that are part of steel frame and subparagraph and associated subparagraphs below for items that are not part of steel frame.

6. Division 5 Section "Metal Fabrications" for the following:

a. Attachment plates and angle brackets for supporting guide-rail brackets.

Delete subparagraph below if only one elevator or one elevator per shaft.

b. Divider beams.

Delete first subparagraph below if not required.

c. Hoist beams.

d. Structural-steel shapes for subsills.

e. Pit ladders.

Delete subparagraph below if not required.  Other means can often be used to avoid metal cants.  See Evaluations.  If retaining, show details on Drawings and add requirements to Division 5 Section "Metal Fabrications."

f. Cants in hoistways made from steel sheet.

Retain subparagraph below for adjacent elevator pits that are at different elevations but not more than 24 inches (600 mm) different in elevation.

7. Division 5 Section "Pipe and Tube Railings" for railings between adjacent elevator pits.

Retain first subparagraph below only for custom fixture trim.

8. Division 5 Section "Ornamental Metal" for combination units that contain hall push-button stations.

9. Division 9 Section "<Insert Section title>" for finish flooring in elevator cars.

10. Division 9 painting Sections for field painting of hoistway entrance doors and frames.

Retain subparagraph below for adjacent elevator pits that are more than 24 inches (600 mm) different in elevation.

11. Division 10 Section "Wire Mesh Partitions" for guards between adjacent elevator pits.

Delete first subparagraph below if security access system equipment is not in the Contract.

12. Division 13 Section "Security Access" for security access system equipment used to restrict elevator use.

13. Division 13 Section "Fire Alarm" for smoke detectors in elevator lobbies to initiate emergency recall operation[ and heat detectors in shafts and machine rooms to disconnect power from elevator equipment before sprinkler activation] and for connection to elevator controllers.

14. Division 14 Section "Hydraulic Freight Elevators" for hydraulic elevators used primarily for carrying freight and not accessible to the general public.

15. Division 16 Sections for electrical service for elevators to and including[ fused] disconnect switches at machine room door[ and standby power source, transfer switch, and connection from auxiliary contacts in transfer switch to controller].

16. Division 16 Section "Voice and Data Communication Cabling" for telephone service to elevators.

Retain paragraph below if allowances are used for elevator car finishes.

C. Allowances:  Provide finished passenger[ and service] elevator cars under the Elevator Car Allowance specified in Division 1 Section "Allowances." Allowance includes furnishing and installing the following:

Edit list below to suit Project.  Coordinate with requirements for elevator car enclosures and hoistway entrances in Part 2.

1. Car wall finishes including trim.

2. Car floor finishes.

3. Car ceiling finishes.

Usually delete first subparagraph below and select from standard door finishes.  Custom door finishes can be expensive.

4. Car[ and hoistway] door finishes.

5. Car door sills.

6. Car light fixtures.

7. Handrails.

8. Cutouts and other provisions for installing elevator signal equipment in cars.

Delete paragraph below if excavation is included in another Section, is not required, or if the possibility of encountering rock is not anticipated.

D. Unit Prices:  Rock excavation for cylinder well holes will be paid for under the unit price indicated in the Contract and as specified in Division 1 Section "Unit Prices."

1.3 DEFINITIONS

Retain terms that remain after this Section has been edited.

A. Definitions in ASME A17.1 apply to work of this Section.

B. Defective Elevator Work:  Operation or control system failure, including excessive malfunctions; performances below specified ratings; excessive wear; unusual deterioration or aging of materials or finishes; unsafe conditions; need for excessive maintenance; abnormal noise or vibration; and similar unusual, unexpected, and unsatisfactory conditions.

C. Service Elevator:  A passenger elevator that is also used to carry freight.

1.4 SUBMITTALS

A. Product Data:  Include capacities, sizes, performances, operations, safety features, finishes, and similar information.  Include product data for the following:

1. Car enclosures and hoistway entrances.

2. Operation, control, and signal systems.

B. Shop Drawings:  Show plans, elevations, sections, and large-scale details indicating service at each landing, machine room layout, coordination with building structure, relationships with other construction, and locations of equipment and signals.  Include large-scale layout of car control station[ and standby power operation control panel].  Indicate variations from specified requirements, maximum dynamic and static loads imposed on building structure at points of support, and maximum and average power demands.

C. Samples for Initial Selection:  For finishes involving color selection.

Delete paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain first paragraph below with or without above, or delete if standard finishes are specified.

D. Samples for Verification:  For exposed finishes of cars, hoistway doors and frames, and signal equipment; 3-inch- (75-mm-) square Samples of sheet materials; and 4-inch (100-mm) lengths of running trim members.

E. Manufacturer Certificates:  Signed by elevator manufacturer certifying that hoistway, pit, and machine room layout and dimensions, as shown on Drawings, and electrical service, as shown and specified, are adequate for elevator system being provided.

Coordinate first paragraph below with qualification requirements in Division 1 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

F. Qualification Data:  For Installer.

G. Operation and Maintenance Data:  For elevators to include in emergency, operation, and maintenance manuals.

Usually delete subparagraph below for projects where Owner's staff will not maintain elevators; retaining will increase cost of elevators.

1. In addition to items specified in Division 1 Section "Operation and Maintenance Data," include diagnostic and repair information available to manufacturer's and Installer's maintenance personnel.

H. Inspection and Acceptance Certificates and Operating Permits:  As required by authorities having jurisdiction for normal, unrestricted elevator use.

I. Warranty:  Special warranty specified in this Section.

J. Continuing Maintenance Proposal:  Service agreement specified in this Section.

1.5 QUALITY ASSURANCE

A. Installer Qualifications:  Elevator manufacturer[ or manufacturer's authorized representative who is trained and approved for installation of units required for this Project].

B. Source Limitations:  Obtain elevators[, including electric traction passenger elevators specified in another Division 14 Section,] through one source from a single manufacturer.

Retaining subparagraph below may limit competition but will eliminate pieced-together systems.  If retaining and special cabs, entrances, or signal fixtures are required, edit to suit Project.

1. Provide major elevator components, including pump-and-tank units, plunger-cylinder assemblies, controllers, signal fixtures, door operators, car frames, cabs, and entrances, manufactured by a single manufacturer.

Always retain code-compliance requirement in paragraph below.  The 2003 International Building Code (IBC) requires compliance with ASCE 7-02, and the 2000 IBC has similar requirements.  Authorities having jurisdiction may also require other specific code references, although most are already incorporated by reference in ASME A17.1.  Insert other requirements if any.

C. Regulatory Requirements:  Comply with ASME A17.1[ and elevator design requirements for earthquake loads in ASCE 7].

Effective peak velocity acceleration (Av), or seismic risk zone, is needed to design elevator to comply with ASME A17.1.  Maps with seismic risk zones are in the Uniform Building Code; maps with values of Av are in BOCA International codes and in ASCE 7-95.  Av could be determined by elevator manufacturer, based on Project's address.

1. Effective peak velocity acceleration (Av) for Project's location is [less than 0.10 (seismic risk zones 0 and 1)] [greater than or equal to 0.10, but less than 0.20 (seismic risk zone 2)] [greater than or equal to 0.20 (seismic risk zones 3 and 4)].

Information in three subparagraphs below is needed to design elevator to comply with ASCE 7-98, ASCE 7-02, or the 2000 IBC.

Design earthquake spectral response acceleration, short period (Sds) is determined by Project's location and site classification.  Subparagraph below could be deleted if this information is given in structural notes on Drawings.

2. Design earthquake spectral response acceleration, short period (Sds) for Project is <Insert value>.

Seismic design category is determined by Project's Seismic Use Group and Project's design earthquake spectral response acceleration, short period (Sds).  Subparagraph below could be deleted if this information is given in structural notes on Drawings.

3. Project's seismic design category is [A] [B] [C] [D].

Elevator importance factor is generally 1.0 unless structure is in Seismic Use Group III and elevators are necessary for continued operation of facility or failure of elevators could impair continued operation of facility, in which case it is 1.5.

4. Elevator importance factor is [1.5] [1.0].

Insert other subparagraphs as needed to inform elevator manufacturer of seismic design criteria.

Usually retain one of two standards in paragraph below to comply with authorities having jurisdiction and other applicable laws and regulations.

D. Accessibility Requirements:  Comply with Section [4.10 in the U.S. Architectural & Transportation Barriers Compliance Board's "Americans with Disabilities Act (ADA), Accessibility Guidelines for Buildings and Facilities (ADAAG)."] [407 in ICC A117.1.]

Delete paragraph below if not applicable, such as for elevators that are not within a fire-rated shaft.

E. Fire-Rated Hoistway Entrance Assemblies:  Door and frame assemblies complying with NFPA 80 that are listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction, for fire-protection ratings indicated, based on testing at as close to neutral pressure as possible according to [NFPA 252] [UBC Standard 7-2] [or] [UL 10B].

1.6 DELIVERY, STORAGE, AND HANDLING

A. Deliver, store, and handle materials, components and equipment in manufacturer's protective packaging.

B. Store materials, components, and equipment off of ground, under cover, and in a dry location.  Handle according to manufacturer's written recommendations to prevent damage, deterioration, or soiling.

1.7 COORDINATION

A. Coordinate installation of sleeves, block outs, and items that are embedded in concrete or masonry for elevator equipment.  Furnish templates and installation instructions and deliver to Project site in time for installation.

Retain first paragraph below only if cylinder well-hole excavation is included in Division 2 Section "Earthwork" and well casing is required and furnished by elevator contractor.

B. Furnish well casing and coordinate delivery with related excavation work.

C. Coordinate sequence of elevator installation with other work to avoid delaying the Work.

D. Coordinate locations and dimensions of other work relating to hydraulic elevators including pit ladders, sumps, and floor drains in pits; entrance subsills; and electrical service, electrical outlets, lights, and switches in pits and machine rooms.

1.8 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements."

A. Special Manufacturer's Warranty:  Manufacturer's standard form in which manufacturer agrees to repair, restore, or replace defective elevator work within specified warranty period.

Verify available warranties for units and components and insert number in subparagraph below.

1. Warranty Period:  [One year] <Insert warranty period> from date of Substantial Completion.

1.9 MAINTENANCE SERVICE

To avoid problems, initial maintenance service and warranty should run concurrently.  Manufacturer's warranties typically cover only the cost of parts; paragraph below covers the cost of labor to replace defective, damaged, or worn parts as well as routine maintenance.  Revise time period if required by Owner; 3 to 12 months is typical.

A. Initial Maintenance Service:  Beginning at Substantial Completion, provide [one year's] <Insert time period> full maintenance service by skilled employees of elevator Installer.  Include monthly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper elevator operation at rated speed and capacity.  Provide parts and supplies same as those used in the manufacture and installation of original equipment.

1. Perform maintenance, including emergency callback service, during normal working hours.

Retain subparagraph above or below.  Retaining below can add appreciable cost to continuing service contract but may not add much cost for initial maintenance service.

2. Include 24-hour-per-day, 7-day-per-week emergency callback service.

Retain subparagraph below with either subparagraph above.  Revise to one hour for hospitals, etc., and for metropolitan areas or to more than two hours for remote locations.

a. Response Time:  Two hours or less.

Usually retain one of two paragraphs below with paragraph and subparagraphs above.  Both paragraphs below provide service contracts beyond initial maintenance service.  If continuing maintenance proposal is to be submitted at time of bid, include that information in the Instructions to Bidders.

B. Continuing Maintenance Proposal:  Provide a continuing maintenance proposal from Installer to Owner, in the form of a standard [one-year] [two-year] [five-year] <Insert agreement period> maintenance agreement, starting on date initial maintenance service is concluded.  State services, obligations, conditions, and terms for agreement period and for future renewal options.

Retain paragraph below if Owner has standard elevator service agreement; otherwise, retain paragraph above.

C. Continuing Maintenance Proposal:  Provide a continuing maintenance proposal from Installer to Owner with terms, conditions, and obligations as set forth in, and in the same form as, "Draft of Elevator Maintenance Agreement" at end of this Section, starting on date initial maintenance service is concluded.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list below if naming manufacturers.  See Division 1 Section "Product Requirements." Verify that manufacturer has service facilities within reasonable distance of Project location.  Possibly add local or regional manufacturers.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Fujitec America, Inc.

2. KONE Inc.

3. Otis Elevator Co.

4. Schindler Elevator Corp.

5. ThyssenKrupp Elevator.

6. <Insert manufacturer's name.>

2.2 SYSTEMS AND COMPONENTS

This Article contains example requirements only; insert others to suit Project.

A. General:  Provide manufacturer's standard elevator systems.  Where components are not otherwise indicated, provide standard components published by manufacturer as included in standard preengineered elevator systems and as required for complete system.

B. Pump Units:  Positive-displacement type with a maximum of 10 percent variation between no load and full load and with minimum pulsations.  Provide[ either of] the following:

1. Pump, with fan-cooled squirrel-cage induction motor, mounted on oil tank with vibration isolation mounts.  Enclose pump in prime-painted steel enclosure lined with 1-inch- (25-mm-) thick, glass-fiber insulation board.

Retain subparagraph above or below, or allow manufacturer to use either.  Pump below may be more expensive but is quieter.

2. Submersible pump, with submersible squirrel-cage induction motor, suspended inside oil tank from vibration isolation mounts.

Retain subparagraph below with either subparagraph above if required; consult Project's electrical engineer.  If retaining, select one of two options or retain both to allow manufacturer to provide either.  Consult manufacturers to verify starting options available in motor sizes required.

3. Provide motor with [wye-delta] [or] [solid-state] starting.

Retain subparagraph below instead of above if desired and available; consult manufacturers.  Feature below provides smoother starting and stopping as well as reduced starting current.

4. Provide variable-voltage variable-frequency motor control.

C. Hydraulic Silencers:  Provide hydraulic silencer containing pulsation-absorbing material in a blowout-proof housing at pump unit.

D. Piping:  Provide size, type, and weight piping recommended by manufacturer, and provide flexible connectors to minimize sound and vibration transmissions from power unit.

Usually retain subparagraph below with in-ground cylinders to eliminate corrosion resulting from stray currents.  Delete if PVC protective cylinder casing is used.

1. Provide dielectric couplings at cylinder units.

Usually retain subparagraph below if underground piping is required.  ASME A17.1 also allows monitored cathodic protection or a protective coating for protecting underground piping from corrosion.

2. Casing for Underground Piping:  PVC pipe complying with ASTM D 1785, joined with PVC fittings complying with ASTM D 2466 and solvent cement complying with ASTM D 2564.

Retain one of first two paragraphs below.  Product in second paragraph can help eliminate the possibility of contamination of soil and ground water by leaked or spilled hydraulic fluid.  For sprinkler-protected buildings, NFPA 13 allows sprinkler in elevator pit to be eliminated for enclosed, noncombustible shafts that do not contain combustible hydraulic fluids.

E. Hydraulic Fluid:  Elevator manufacturer's standard [fire-resistant] fluid with additives as needed to prevent oxidation of fluid, corrosion of cylinder and other components, and other adverse effects.

F. Hydraulic Fluid:  Nontoxic, readily biodegradable[, fire-resistant fluid] made from vegetable oil with antioxidant, anticorrosive, antifoaming, and metal-passivating additives.  Hydraulic fluid is approved by elevator manufacturer for use with elevator equipment.

1. Product:  Subject to compliance with requirements, provide "Hydro Safe" by Hydro Safe Oil Division, Inc.

G. Inserts:  Furnish required concrete and masonry inserts and similar anchorage devices for installing guide rails, machinery, and other components of elevator work where installation of devices is specified in another Section.

Paragraph below provides means of protecting in-ground cylinder from corrosion.  ASME A17.1 also allows other methods of cylinder protection but requires means of monitoring and maintaining method of protection.  If another means of cylinder protection is required, delete paragraph and insert another and describe means of protection used.  See Evaluations.

H. Protective Cylinder Casing:  PVC or HDPE pipe casing complying with ASME A17.1, of sufficient size to provide not less than 1-inch (25-mm) clearance from cylinder and extending above pit floor.  Provide means to monitor casing effectiveness to comply with ASME A17.1.

Filler in first paragraph below can be used with protective cylinder casing to provide additional corrosion and leak protection by filling space between cylinder and casing.

I. Corrosion Protective Filler:  A nontoxic, petroleum-based gel formulated for filling the space between hydraulic cylinder and protective casing.  Filler is electrically nonconductive, displaces or absorbs water, and gels or solidifies at temperatures below 60 deg F (16 deg C).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list below if naming manufacturers and products.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

2. Products:  Subject to compliance with requirements, provide one of the following:

a. Hydro Safe Oil Division, Inc.; No-Ox-Id Liquid Elevator Casing Filler E-800.

b. Union-Gard, a division of Dome Services L.L.C.; Union-Gard 160.

c. <Insert manufacturer's name; product name or designation.>

J. Car Frame and Platform:  Welded steel units.

K. Guides:  Provide either roller guides or sliding guides at top and bottom of car and counterweight frames.  If sliding guides are used, provide guide-rail lubricators or polymer-coated, nonlubricated guides.

2.3 OPERATION SYSTEMS

A. General:  Provide manufacturer's standard microprocessor operation system [for each elevator] [for each group of elevators] as required to provide type of operation system indicated.

Retain paragraph and applicable subparagraphs below for cars that are not in groups.  If only one elevator is required, retain paragraph and delete option in title.

B. [Single-Car ]Auxiliary Operations:  In addition to primary operation system features, provide the following operational features for elevators where indicated:

Typical operational features are described in subparagraphs below.  Delete those not required; add others as desired.  Identify elevators that require features by listing in "Elevators" Article.

Caution:  There are many possible definitions of standby (emergency) power operation.  Subparagraphs below are examples only; coordinate with Division 16 Sections and ensure that what is to be provided is clear both here and in Division 16 and that emergency generators have adequate capacity for specified operation.

1. Standby Power Operation:  On activation of standby power, car is returned to a designated floor and parked with doors open.  Car can be manually put in service on standby power, either for return operation or for regular operation, by switches in control panel located at [main lobby] [fire command station] <Insert location>.  Manual operation causes automatic operation to cease.

2. Standby-Powered Lowering:  On activation of standby power, if car is at a floor it remains at that floor, opens its doors, and shuts down.  If car is between floors, it is lowered to a preselected floor, opens its doors, and shuts down.  If car is below the preselected floor, it is lowered to the next lower floor, opens its doors, and shuts down.

3. Standby-Powered Lowering:  On activation of standby power, car is lowered to the lowest floor, opens its doors, and shuts down.

Retain one of three subparagraphs above or one of first two subparagraphs below, or delete all five.  Battery-powered lowering may be an unnecessary expense because ASME A17.1 requires a manually operated valve that permits lowering car at not more than 20 fpm (0.10 m/s).  Roped hydraulic elevators, however, cannot be lowered manually because they have safeties, which grab guide rails if power fails and must be released electrically.

4. Battery-Powered Lowering:  If power fails and car is at a floor, it remains at that floor, opens its doors, and shuts down.  If car is between floors, it is lowered to a preselected floor, opens its doors, and shuts down.  If car is below the preselected floor, it is lowered to the next lower floor, opens its doors, and shuts down.  System includes rechargeable battery and automatic recharging system.

5. Battery-Powered Lowering:  When power fails, car is lowered to the lowest floor, opens its doors, and shuts down.  System includes rechargeable battery and automatic recharging system.

6. Automatic Dispatching of Loaded Car:  When car load exceeds 80 percent of rated capacity, doors will begin closing.

7. Nuisance Call Cancel:  When car calls exceed a preset number while car load is less than a predetermined weight, all car calls are canceled.  Preset number of calls[ and predetermined weight] can be adjusted.

Retain paragraph and applicable subparagraphs below for elevators in groups; delete if Project requires only one elevator.

C. Group Auxiliary Operations:  In addition to primary operation system features, provide the following operational features for elevators and elevator groups where indicated:

Typical operational features are described in subparagraphs below.  Delete those not required; add others as desired.  Identify elevators that require features by listing in "Elevators" Article.

Caution:  There are many possible definitions of standby (emergency) power operation.  Subparagraphs below are examples only; coordinate with Division 16 Sections and ensure that what is to be provided is clear both here and in Division 16 and that emergency generators have adequate capacity for specified operation.

1. Standby Power Operation:  On activation of standby power, cars are returned to a designated floor and parked with doors open.  Only one car is moved upward at a time, with priority given to loaded cars.  If a car cannot be returned after two attempts, it is removed from the system.  When all cars have been returned or removed from the system, one car is automatically placed in service.  If car selected for service cannot operate within 60 seconds, the system removes car from service and places another car in service.  Cars can be manually put in service on standby power, either for return operation or for regular operation, by switches in control panel located at [main lobby] [fire command station] <Insert location>.  Manual operation causes automatic operation to cease.

2. Standby Power Operation:  On activation of standby power, cars are returned to lowest floor and parked with doors open.  If a car cannot be returned, it is removed from the system.  One car is selected for service on standby power by a switch located at [main lobby] [fire command station] <Insert location>.

3. Standby-Powered Lowering:  On activation of standby power, cars that are at a floor remain at that floor, open their doors, and shut down.  Cars that are between floors are lowered to a preselected floor, open their doors, and shut down.  Cars that are below the preselected floor are lowered to the next lower floor, open their doors, and shut down.

4. Standby-Powered Lowering:  On activation of standby power, cars are lowered to the lowest floor, open their doors, and shut down.

Retain one of four subparagraphs above or one of first two subparagraphs below, or delete all six.  Battery-powered lowering may be an unnecessary expense because ASME A17.1 requires a manually operated valve that permits lowering car at not more than 20 fpm (0.10 m/s).  Roped hydraulic elevators, however, cannot be lowered manually because they have safeties, which grab guide rails if power fails and must be released electrically.

5. Battery-Powered Lowering:  If power fails, cars that are at a floor remain at that floor, open their doors, and shut down.  Cars that are between floors are lowered to a preselected floor, open their doors, and shut down.  Cars that are below the preselected floor are lowered to the next lower floor, open their doors, and shut down.  System includes rechargeable battery and automatic recharging system.

6. Battery-Powered Lowering:  When power fails, cars are lowered to the lowest floor, open their doors, and shut down.  System includes rechargeable battery and automatic recharging system.

7. Automatic Dispatching of Loaded Car:  When car load exceeds 80 percent of rated capacity, doors will begin closing.

8. Nuisance Call Cancel:  When car calls exceed a preset number while car load is less than a predetermined weight, all car calls are canceled.  Preset number of calls[ and predetermined weight] can be adjusted.

If selecting "remote switch" option in subparagraph below, show location on Drawings.

9. [Emergency Hospital] [Priority] Service:  Service is initiated by a [keyswitch] [card reader] [remote switch] at designated floors.  One elevator is removed from group operation and directed to the floor where service was initiated.  On arriving at the floor, elevator opens its doors and parks[ and a lighted sign directs passengers to exit elevator].  Car is placed in operation by selecting a floor and pressing door close button or by operating keyswitch to put car in independent service.  After responding to floor selected or being removed from independent service, car is returned to group operation.  If car is not placed in operation within a preset time after being called, it is returned to group operation.

Always retain first subparagraph below for service elevators that are part of a group.

10. Independent Service:  Keyswitch in car control station removes car from group operation and allows it to respond only to car calls.  Key cannot be removed from keyswitch when car is in independent service.  When in independent service, doors close only in response to door close button.

11. Loaded-Car Bypass:  When car load exceeds 80 percent of rated capacity, car will respond only to car calls, not to hall calls.

Delete paragraph and subparagraphs below if security features are not required.  If retaining, select features required or revise to suit Project.  Indicate in "Elevators" Article which elevators require selected features.

D. Security Features:  Provide the following security features, where indicated.  Security features shall not affect emergency firefighters' service.

Usually select only one option (usually first) for card-reader location in first subparagraph below unless complex security arrangements require otherwise; additional card readers add cost to system and are annoying to passengers.

1. Card-Reader Operation:  System uses card readers at [car control stations] [and] [hall push-button stations] to authorize calls.  Security system determines which landings and at what times calls require authorization by card reader.  Provide required conductors in traveling cable and panel in machine room for interconnecting card readers, other security access system equipment, and elevator controllers.  [Allow space as indicated for card reader in car] [Provide stripe-swipe card reader integral with each car control station].

a. Security access system equipment is specified in Division 13 Section "Security Access."

Retain subparagraph above if security access system is included in the Contract; retain subparagraph below for a separate security access system contract.  Coordinate either with system used.

b. Security access system equipment is not in the Contract.

First subparagraph below includes simple security feature suitable for dormitories and similar facilities.  Usually select only one keyswitch location; additional keyswitches add cost to system and are annoying to passengers.

2. Keyswitch Operation:  Push buttons are activated and deactivated by security keyswitches at [car control stations] [and] [hall push-button stations].  Key is removable only in deactivated position.

3. Keypad Operation:  Allows each landing to be restricted or unrestricted.  When a restricted landing button is pressed, a "Restricted Floor" lamp lights and remains lit until landing access code has been entered into a keypad or predetermined time period has elapsed.  Car calls for restricted landings do not register until landing access code is entered into keypad within predetermined time period after landing button is pressed.

a. Access codes are programmed at each car operating panel using a security keyswitch.  Keypad operation can be activated and deactivated by security keyswitch at main landing.

Features in subparagraph and associated subparagraph above and subparagraph below are offered by some manufacturers.  Verify availability before retaining.  Select first option below for single elevators and second option for groups.

4. Car-to-Lobby Feature:  Feature, activated by keyswitch at main lobby, that causes [car] [all cars in a group] to return immediately to lobby and open doors for inspection.  On deactivation by keyswitch, calls registered before keyswitch activation are completed and normal operation is resumed.

2.4 DOOR REOPENING DEVICES

Device in paragraph below is standard with most manufacturers; delete paragraph and insert another if required.

A. Infrared Array:  Provide door reopening devices with uniform array of 36 or more microprocessor-controlled, infrared light beams projecting across car entrance.  Interruption of one or more of the light beams shall cause doors to stop and reopen.

Generally retain paragraph below to minimize elevator delay; feature may be unnecessary for low-rise elevators.

B. Nudging Feature:  After car doors are prevented from closing for predetermined adjustable time, through activating door reopening device, a loud buzzer shall sound and doors shall begin to close at reduced kinetic energy.

2.5 FINISH MATERIALS

A. General:  Provide the following materials for exposed parts of elevator car enclosures, car doors, hoistway entrance doors and frames, and signal equipment as indicated.

B. Cold-Rolled Steel Sheet:  ASTM A 1008/A 1008M, commercial steel, Type B, exposed, matte finish.

C. Hot-Rolled Steel Sheet:  ASTM A 1011/A 1011M, commercial steel, Type B, pickled.

D. Stainless-Steel Sheet:  ASTM A 240/A 240M, Type 304.

1. Textured Stainless-Steel Sheet:  Product with [coined] [embossed] texture rolled into exposed surface.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs below if naming a manufacturer and product.  See Division 1 Section "Product Requirements."

a. Available Product:  Subject to compliance with requirements, a product that may be incorporated into the Work includes, but is not limited to, "<Insert product name>" by <Insert manufacturer's name>.

b. Product:  Subject to compliance with requirements, provide "<Insert product name>" by <Insert manufacturer's name>.

Review manufacturer's product data and coordinate description in subparagraph below with product selected; delete subparagraph if no further treatment is required after rolling.  Product cost varies widely depending on options chosen.

c. Metal surface is [satin polished] [satin relieved] [titanium nitride colored] [oxide colored] [satin polished and titanium nitride colored] [satin relieved and titanium nitride colored] [satin polished and oxide colored] [satin relieved and oxide colored] [color coated and satin relieved] [color coated and bright relieved] after rolling.

E. Stainless-Steel Bars:  ASTM A 276, Type 304.

Retain paragraph above or first paragraph below, or both if needed for handrails.

F. Stainless-Steel Tubing:  ASTM A 554, Grade MT 304.

G. Bronze Plate and Sheet:  ASTM B 36/B 36M, Alloy UNS No. C28000 (muntz metal).

H. Bronze Extrusions:  ASTM B 455, Alloy UNS No. C38500 (architectural bronze).

Retain paragraph above or first paragraph below, or both if needed for handrails.  Retain paragraph above if needed for door sills.

I. Bronze Tubing:  ASTM B 135 (ASTM B 135M), Alloy UNS No. C23000 (red brass, 85 percent copper).

J. Aluminum Extrusions:  ASTM B 221 (ASTM B 221M), Alloy 6063.

Delete paragraph below if no nickel silver door sills, which are more expensive but more durable than aluminum door sills.

K. Nickel Silver Extrusions:  ASTM B 151/B 151M, Alloy UNS No. C74500 or No. C77600.

Retain applicable plastic-laminate types in paragraph below.  Type HGS is standard general-purpose type, 1.2 mm (0.048 inch) thick.  Type HGL is general-purpose type that is standard for European manufacturers, 1.0 mm (0.039 inch) thick.  Type HGP is standard post-forming type, 1.0 mm (0.039 inch) thick.  Type BKV is standard vertical backing type, 0.7 mm (0.028 inch) thick.

L. Plastic Laminate:  High-pressure type complying with NEMA LD 3, [Type HGS for flat applications] [Type HGL for flat applications] [Type HGP for postformed applications] [and] [Type BKV for panel backing].

2.6 CAR ENCLOSURES

Removable wall panels allow panels to be replaced with little downtime and allow car, with finished wall panels removed, to be used during construction.  Cars with nonremovable panels are less expensive.  Removable roof can be useful for moving large objects; before retaining last option in paragraph below, verify availability and cost.

A. General:  Provide [enameled-steel car enclosures to receive removable] [steel-framed car enclosures with nonremovable] wall panels, with [removable ]car roof, access doors, power door operators, and ventilation.

1. Provide standard railings complying with ASME A17.1 on car tops where required by ASME A17.1.

2. Provide finished car including materials and finishes specified below.

Retain subparagraph above if allowance is not used; retain subparagraph below if allowance is used.  If all car finishes are not included in allowance, retain option in subparagraph below and specify excluded finishes in "Materials and Finishes" Paragraph.

3. Refer to "Allowances" Paragraph, in Part 1 "Summary" Article, for items to be provided under the Elevator Car Allowance.  Provide items not included in the Elevator Car Allowance as needed for finished car[ including materials and finishes specified below].

Delete paragraph and subparagraphs below if car allowance is used and all materials and finishes listed below are included in allowance.  Detail cars on Drawings if special finishes and designs are desired.

B. Materials and Finishes:  Provide manufacturer's standards, but not less than the following:

Delete subparagraphs below not required; revise or add additional items to suit Project.

1. Subfloor:  Underlayment grade, exterior plywood, 5/8-inch (16-mm) nominal thickness.

2. Floor Finish:  [Specified in a Division 9 Section] [Elevator manufacturer's standard level-loop nylon carpet; color as selected by Architect from manufacturer's full range].

3. Enameled-Steel Wall Panels:  Flush, hollow-metal construction; fabricated from cold-rolled steel sheet.  Provide with factory-applied enamel finish; colors as selected by Architect from manufacturer's full range.

4. Stainless-Steel Wall Panels:  Flush, hollow-metal construction; fabricated from stainless-steel sheet.

5. Bronze Wall Panels:  Flush, hollow-metal construction; fabricated from bronze sheet.

Particleboard and adhesive used for laminating panels in first subparagraph below generally contain urea formaldehyde.  If low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.4, it is better to specify another wall panel finish, such as metal, rather than trying to specify plastic-laminate wall panels that will comply with ASME A17.1 and are made without urea formaldehyde.

6. Plastic-Laminate Wall Panels:  Plastic laminate adhesively applied to [1/2-inch (13-mm) fire-retardant-treated particleboard] [manufacturer's standard honeycomb core] with[ plastic-laminate panel backing and] manufacturer's standard protective edge trim.  Panels have a flame-spread index of [25] [75] or less, when tested according to ASTM E 84.  Plastic-laminate color, texture, and pattern as selected by Architect from [plastic-laminate] [elevator] manufacturer's full range.

7. Fabricate car with recesses and cutouts for signal equipment.

8. Fabricate car door frame integrally with front wall of car.

Usually select from standard door finishes in first four subparagraphs below.  Custom door finishes can be expensive.

9. Enameled-Steel Doors:  Flush, hollow-metal construction; fabricated from cold-rolled steel sheet.  Provide with factory-applied enamel finish; colors as selected by Architect from manufacturer's full range.

10. Stainless-Steel Doors:  Flush, hollow-metal construction; fabricated [from stainless-steel sheet] [or] [by laminating stainless-steel sheet to exposed faces and edges of enameled cold-rolled steel doors using adhesive that fully bonds metal to metal without telegraphing or oil-canning].

11. Bronze Doors:  Flush, hollow-metal construction; fabricated by laminating bronze sheet to exposed faces and edges of enameled cold-rolled steel doors using adhesive that fully bonds metal to metal without telegraphing or oil-canning.

12. Plastic-Laminate Doors:  Flush, hollow-metal construction; fabricated by laminating plastic laminate to exposed faces of enameled cold-rolled steel doors and covering edges with protective edge trim[ matching return panels].  Plastic-laminate color, texture, and pattern as selected by Architect from [plastic-laminate] [elevator] manufacturer's full range.

13. Sight Guards:  Provide sight guards on car doors.

14. Sills:  Extruded metal, with grooved surface, 1/4 inch (6.4 mm) thick.

15. Luminous Ceiling:  Fluorescent light fixtures and ceiling panels of translucent acrylic or other permanent rigid plastic.

Ceilings in first subparagraph below are offered by some manufacturers.  Before selecting options, verify availability with selected manufacturers.

16. [Metal] [Metallic-Finish, Plastic-Laminate] Ceiling:  Flush panels, with [incandescent downlights in the center of] [four low-voltage downlights in] each panel.[  Align ceiling panel joints with joints between wall panels.]

17. Handrails:  Manufacturer's standard handrails, of shape, metal, and finish indicated.

2.7 HOISTWAY ENTRANCES

A. General:  Provide manufacturer's standard horizontal-sliding, door-and-frame hoistway entrances complete with track systems, hardware, sills, and accessories.  Provide frame size and profile to coordinate with hoistway wall construction.

Delete subparagraph below if no gypsum board shaft walls.

1. Where gypsum board wall construction is indicated, provide self-supporting frames with reinforced head sections.

B. Materials and Fabrication:  Provide manufacturer's standards, but not less than the following:

Delete subparagraphs below not required; revise or add additional items to suit Project.

1. Enameled-Steel Frames:  Formed from cold-rolled or hot-rolled steel sheet.  Provide with factory-applied enamel finish; colors as selected by Architect from manufacturer's full range.

First subparagraph below may be desirable for applying field-applied finish such as stone.  Finishes can also be applied to enameled-steel frames in subparagraph above, but door opening will be reduced due to thickness of finish, and edges of finish will be visible from inside elevator car when doors are fully open.  Before retaining subparagraph below, verify availability and cost.

2. Steel Subframes:  Formed from cold-rolled or hot-rolled steel sheet with factory-applied enamel finish or corrosion-inhibiting primer.  Fabricate to receive applied finish as indicated.

3. Stainless-Steel Frames:  Formed from stainless-steel sheet.

4. Bronze Frames:  Formed from cold-rolled or hot-rolled steel sheet, with enamel finish, and with formed-bronze sheet laminated to steel frames using adhesive that fully bonds metal to metal without telegraphing or oil-canning.

Usually select from standard door finishes in first four subparagraphs below.  Custom door finishes can be expensive.  Delete all four if hoistway doors are included in the Elevator Car Allowance.

5. Enameled-Steel Doors[ and Transoms]:  Flush, hollow-metal construction; fabricated from cold-rolled steel sheet.  Provide with factory-applied enamel finish; colors as selected by Architect from manufacturer's full range.

6. Stainless-Steel Doors[ and Transoms]:  Flush, hollow-metal construction; fabricated [from stainless-steel sheet] [or] [by laminating stainless-steel sheet to exposed faces and edges of enameled cold-rolled steel doors using adhesive that fully bonds metal to metal without telegraphing or oil-canning].

7. Bronze Doors[ and Transoms]:  Flush, hollow-metal construction; fabricated by laminating bronze sheet to exposed faces and edges of enameled cold-rolled steel doors using adhesive that fully bonds metal to metal without telegraphing or oil-canning.

8. Plastic-Laminate Doors[ and Transoms]:  Flush, hollow-metal construction; fabricated by laminating plastic laminate to exposed faces of enameled cold-rolled steel doors and covering edges with protective edge trim[ matching door frames].  Plastic-laminate color, texture, and pattern as selected by Architect from [plastic-laminate] [elevator] manufacturer's full range.

9. Sight Guards:  Provide sight guards on doors matching door edges.

10. Sills:  Extruded metal, with grooved surface, 1/4 inch (6.4 mm) thick.

Retain subparagraph below for grouting door sills.

11. Nonshrink, Nonmetallic Grout:  Factory-packaged, nonstaining, noncorrosive, nongaseous grout complying with ASTM C 1107.

2.8 SIGNAL EQUIPMENT

A. General:  Provide hall-call and car-call buttons that light when activated and remain lit until call has been fulfilled.  Fabricate lighted elements with [long-life incandescent lamps and acrylic or other permanent, nonyellowing translucent plastic diffusers] [or] [LEDs].

Retain one of first two paragraphs and associated subparagraphs below.  Recessed control station in first paragraph usually fits into an opening in return panel with a faceplate covering opening and overlapping edges of opening.  Show details of signs and other surface-mounted items and coordinate with related work (in Part 1 and in other appropriate Sections) if not work of this Section.

B. Car Control Stations:  Provide manufacturer's standard [recessed] [or] [semirecessed] car control stations.  Mount in return panel adjacent to car door, unless otherwise indicated.

First paragraph below is an alternative available from elevator manufacturers.  Verify cost before retaining.

C. Swing-Return Car Control Stations:  Provide car control stations mounted on rear of hinged return panel adjacent to car door and with buttons, switches, controls, and indicator lights projecting through return panel but substantially flush with face of return panel.

Retain applicable subparagraphs below with either paragraph above.

1. Mark buttons and switches with standard identification for required use or function that complies with ASME A17.1.  Use both tactile symbols and Braille.

2. Provide "No Smoking" sign matching car control station, either integral with car control station or mounted adjacent to it, with text and graphics as required by authorities having jurisdiction.

D. Emergency Communication System:  Provide system that complies with ASME A17.1 and the U.S. Architectural & Transportation Barriers Compliance Board's "Americans with Disabilities Act (ADA), Accessibility Guidelines for Buildings and Facilities (ADAAG)." On activation, system dials preprogrammed number of monitoring station and identifies elevator location to monitoring station.  System provides two-way voice communication without using a handset and provides visible signals that indicate when system has been activated and when monitoring station has responded.  System is contained in flush-mounted cabinet, with identification, instructions for use, and battery backup power supply.

Retain first paragraph below where required by building code.

E. Firefighters' Two-Way Telephone Communication Service:  Provide [flush-mounted cabinet] [telephone jack] in each car and required conductors in traveling cable for firefighters' two-way telephone communication service specified in Division 13 Section "Fire Alarm."

F. Car Position Indicator:  Provide [illuminated, ]digital-type car position indicator, located above car door or above car control station.  Also provide audible signal to indicate to passengers that car is either stopping at or passing each of the floors served.

1. Include travel direction arrows if not provided in car control station.

G. Hall Push-Button Stations:  Provide one hall push-button station at each landing[ for each single elevator or group of elevators, but not less than one station for each four elevators in a group].

Delete paragraph above and retain paragraph and subparagraphs below if push-button stations are shown on plans.

H. Hall Push-Button Stations:  Provide hall push-button stations at each landing as indicated.

1. Provide manufacturer's standard wall-mounted units.

Retain subparagraph above or below with one of two "Hall Push-Button Stations" paragraphs above.

2. Provide units with flat faceplate for mounting with body of unit recessed in wall.

Retain subparagraph below with one of two "Hall Push-Button Stations" paragraphs above.

3. Equip units with buttons for calling elevator and for indicating desired direction of travel.

Retain subparagraph below if required by authorities having jurisdiction and jacks are to be integrated into hall push-button stations.

4. Provide telephone jack in each unit for firefighters' two-way telephone communication service specified in Division 13 Section "Fire Alarm."

Possibly insert a provision for either an "In Use" signal or a digital display of car position for single elevators.

I. Hall Lanterns:  Units with illuminated arrows; but provide single arrow at terminal landings.  Provide[ one of] the following:

Retain one or more of four subparagraphs below; fourth is generally least expensive.

1. Manufacturer's standard wall-mounted units, for mounting above entrance frames.

Feature in subparagraph below is no longer standard with most manufacturers for wall mounting.  Before retaining, verify availability and cost.

2. Units with flat faceplate for mounting with body of unit recessed in wall and with illuminated elements projecting from faceplate for ease of angular viewing.

Delete subparagraph below if jamb-mounted lanterns are not acceptable.  Jamb-mounted lanterns may not be visible from some locations in elevator lobbies.  Delete option if only one elevator.

3. Units mounted in both jambs of entrance frame[ for each elevator].

Car-mounted lanterns are even less visible than jamb-mounted lanterns but usually cost less and require less maintenance.  Delete subparagraph below if not acceptable.  Delete option if only one elevator.

4. Units mounted in both car door jambs[; may be used only for single elevators or for two-car groups].

J. Hall Annunciator:  With each hall lantern, provide audible signals indicating car arrival and direction of travel.  Signals sound once for up and twice for down.

Car-mounted audible signals usually cost less and require less maintenance than audible signals in each hall lantern.  Delete subparagraph below if not acceptable.  Delete option if only one elevator.

1. At manufacturer's option, audible signals may be placed on[ each] car.

Revise paragraph and subparagraph below if hall position indicators are desired at all floors.  Delete second option if only one elevator.

K. Hall Position Indicators:  Provide [illuminated, ]digital-display-type position indicators, located above[ each] hoistway entrance at ground floor.  Provide units with flat faceplate for mounting and with body of unit recessed in wall.

Delete subparagraph below if not required.

1. Integrate ground-floor hall lanterns with hall position indicators.

Retain one of first two paragraphs below for elevators with standby power operation.  Retain first paragraph if fire command center is not required; retain option if elevator doors cannot be seen from switch location.  Retain second paragraph if fire command center is required by building code.

L. Standby Power Elevator Selector Switches:  Provide switches, as required by ASME A17.1, where indicated. Adjacent to switches, provide illuminated signal that indicates when normal power supply has failed.[  For each elevator, provide illuminated signals that indicate when they are operational and when they are at the designated emergency return level with doors open.]

M. Fire Command Center Annunciator Panel:  Provide panel containing illuminated position indicators for each elevator, clearly labeled with elevator designation; include illuminated signal that indicates when elevator is operational and when it is at the designated emergency return level with doors open.  Provide standby power elevator selector switch(es), as required by ASME A17.1, adjacent to position indicators.  Provide illuminated signal that indicates when normal power supply has failed.

Delete paragraph below if signs are specified in another Section.

N. Corridor Call Station Pictograph Signs:  Provide signs matching hall push-button stations, with text and graphics as required by authorities having jurisdiction, indicating that in case of fire elevators are out of service and exits should be used instead.  Provide one sign at each hall push-button station, unless otherwise indicated.

Insert other signals and graphics ("No Smoking," etc.) as desired or required by authorities having jurisdiction.

2.9 ELEVATORS

Copy and edit paragraph and subparagraphs below for each elevator or group of elevators required.

A. Elevator Description:

1. Group Number:  <Insert a different number for each group of elevators that share a group operation system.>

2. Elevator Number(s):  <Insert elevator number(s) as shown on Drawings.>

Delete subparagraph below if no service elevators.

3. Service Elevator Number(s):  <Insert elevator number(s) as shown on Drawings.>

Select type from four subparagraphs below to correspond with products selected.  See Evaluations and manufacturers' product literature.  Consider using a holeless type where hard rock may be encountered in drilling hole for an in-ground cylinder.  Note that holeless, single-acting type can only be used for two stops (travel distance of one-story height).

4. Type:  Under-the-car single cylinder.

5. Type:  Holeless, beside-the-car, single-acting, [single] [dual] cylinder.

6. Type:  Holeless, beside-the-car, telescoping, [single] [dual] cylinder.

7. Type:  Holeless, beside-the-car, roped hydraulic, [single] [dual] cylinder.

Usually delete subparagraph below if net platform size is shown on Drawings or if inside-car dimensions are included in "Car Enclosures" Subparagraph.

8. Rated Load:  [2000 lb (908 kg)] [2100 lb (953 kg)] [2500 lb (1135 kg)] [3000 lb (1362 kg)] [3500 lb (1589 kg)] [4000 lb (1816 kg)] [4500 lb (2043 kg)] [5000 lb (2270 kg)] <Insert load>.

Delete subparagraph below if no service elevators.

9. Freight Loading Class for Service Elevators:  Class A.

Select speed from options in subparagraph below or revise to suit Project.  100 fpm (0.51 m/s) is typical.

10. Rated Speed:  [75 or 80 fpm (0.38 or 0.41 m/s)] [100 fpm (0.51 m/s)] [125 fpm (0.64 m/s)] [150 fpm (0.76 m/s)] [175 fpm (0.89 m/s)] [200 fpm (1.0 m/s)] <Insert speed>.

Retain applicable operation system in first subparagraph below or describe specific manufacturers' systems or performance requirements in "Operation Systems" Article.  First option is for two-stop single elevator; second is for single elevator with three or more stops; third is for two or more elevators in a group.

11. Operation System:  [Single automatic] [Selective collective automatic] [Group automatic] operation.

12. Auxiliary Operations:

a. Standby power operation.

b. Standby-powered lowering.

c. Battery-powered lowering.

d. Automatic dispatching of loaded car.

e. Nuisance call cancel.

Auxiliary operations in first three subparagraphs below are not applicable to single elevators.

f. [Emergency hospital] [Priority] service at [all] <Insert floor designations> floors.

Always retain first subparagraph below if group includes a service elevator.

g. Independent service for [service elevator] [all cars in group].

h. Loaded-car bypass.

13. Security Features:  [Card-reader operation] [Keyswitch operation] [Keypad operation] [Car-to-lobby feature].

Subparagraph below is an extra-cost feature that may be retained with center-opening doors for large cars with heavy peak traffic, such as in an office building, and for hospital elevators.  It may also be retained for service elevators with entrances at both front and rear.

14. Dual Car Control Stations:  Provide two car control stations[ in each elevator]; equip only one with required keyswitches, if any.

If standard cars are not acceptable, detail cars on Drawings and delete first subparagraph and associated subparagraphs below or use an allowance and retain only those subparagraphs specifying car dimensions and describing items not included in allowance.

15. Car Enclosures:

a. Inside Width:  [64 inches (1626 mm)] [68 inches (1727 mm)] [80 inches (2032 mm)] [92 inches (2337 mm)] <Insert width> from side wall to side wall.

Before retaining options in subparagraph above and first subparagraph below, verify that selected configuration complies with requirements for providing accessibility to people with disabilities and to emergency stretchers.  Revise descriptions of width and depth if car has more than one entrance.

b. Inside Depth:  [51 inches (1295 mm)] [53 inches (1346 mm)] [57 inches (1448 mm)] [65 inches (1651 mm)] [87-1/2 inches (2222 mm)] [90 inches (2286 mm)] [93 inches (2362 mm)] [93-1/2 inches (2375 mm)] [96 inches (2438 mm)] [101 inches (2565 mm)] [102 inches (2591 mm)] <Insert depth> from back wall to front wall (return panels).

c. Inside Height:  [88 inches (2235 mm)] [92 inches (2337 mm)] [94 inches (2388 mm)] [100 inches (2540 mm)] [104 inches (2642 mm)] [108 inches (2743 mm)] [112 inches (2845 mm)] <Insert height> to underside of ceiling.

d. Front Walls (Return Panels):  [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Polished bronze, lacquered] [Satin bronze, lacquered] with integral car door frames.

Delete first subparagraph below if "Swing-Return Car Control Stations" Paragraph is retained in "Signal Equipment" Article.

e. Car Fixtures:  [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Polished bronze, lacquered] [Satin bronze, lacquered].

f. Side and Rear Wall Panels:  [Enameled steel] [Plastic laminate] [Satin stainless steel, No. 4 finish] [Textured stainless steel].

g. Reveals:  [Enameled steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Polished bronze, lacquered] [Satin bronze, lacquered].

Plastic-laminate doors are about as expensive as stainless-steel doors but are not as durable.

h. Door Faces (Interior):  [Enameled steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Textured stainless steel] [Polished bronze, lacquered] [Satin bronze, lacquered] [Plastic laminate].

Nickel silver door sills are more durable than aluminum door sills but are as expensive as bronze.

i. Door Sills:  [Aluminum, mill finish] [Bronze, polished] [Nickel silver, polished].

j. Ceiling:  [Luminous ceiling] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Polished bronze, lacquered] [Reflective metallic-finish, plastic-laminate, stainless steel] [Reflective metallic-finish, plastic-laminate, bronze].

k. Handrails:  [1-1/2 inches (38 mm) round] [1/2 by 2 inches (13 by 50 mm) rectangular] <Insert description> [mirror-polished stainless steel, No. 8 finish] [satin stainless steel, No. 4 finish] [mirror-polished bronze, lacquered] [satin bronze, lacquered], at [sides] [and] [rear] of car.

l. Floor:  Manufacturer's standard carpet.

Retain last subparagraph above and delete first subparagraph below if elevator manufacturer's standard carpet is used.

m. Floor prepared to receive carpet (specified in Division 9 Section "Carpet").

n. Floor prepared to receive resilient tile (specified in Division 9 Section "Resilient Floor Tile").

Revise subparagraph below if linoleum is used.

o. Floor prepared to receive sheet vinyl (specified in Division 9 Section "Sheet Vinyl Floor Coverings").

If retaining subparagraph below, coordinate with setting method used for tile.  Both Sections referenced contain provisions for floor tile installation on cementitious backer units (included in tile Sections) over wood using thin-set mortar (TCA F144 and ANSI A108.5).  ASME A17.1 requires that elevator floors and floor members be designed to limit deflection to L/960, which should be stiff enough to eliminate cracking of tile.

p. Floor recessed and prepared to receive [dimension stone tile (specified in Division 9 Section "Dimension Stone Tile")] [ceramic tile (specified in Division 9 Section "Ceramic Tile")].

For floors thicker than the typical 1/4 to 5/8 inch (6 to 16 mm), manufacturer will have to know how much to raise the car door sill and doors above the car subfloor.

q. Floor Thickness, Including Setting Materials:  <Insert thickness> above plywood subfloor.

16. Hoistway Entrances:

a. Width:  [36 inches (914 mm)] [42 inches (1067 mm)] [48 inches (1219 mm)] [54 inches (1372 mm)] <Insert width>.

b. Height:  [84 inches (2134 mm)] [96 inches (2438 mm)] <Insert height>.

c. Type:  [Single-speed side sliding] [Two-speed side sliding] [Single-speed center opening] [Two-speed center opening].

Delete subparagraph below if not applicable, such as for elevators that are not within a fire-rated shaft.  Delete temperature-rise rating if not required.

d. Fire-Protection Rating:  [1 hour] [1-1/2 hours] <Insert rating>[ with 30-minute temperature rise of 450 deg F (250 deg C)].

Copy and edit subparagraph below to suit Project.

e. Frames [at First Floor] [at Basement Floors]:  [Enameled steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Polished bronze, lacquered] [Satin bronze, lacquered].

If frames are same at all floors, delete both options in title of subparagraph above and delete subparagraph below; otherwise, retain and edit both subparagraphs.

f. Frames at Other Floors:  [Enameled steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Polished bronze, lacquered] [Satin bronze, lacquered].

Copy and edit subparagraph below to suit Project.  Plastic-laminate doors are about as expensive as stainless-steel doors but are not as durable.

g. Doors [and Transoms] [at First Floor] [at Basement Floors]:  [Enameled steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Textured stainless steel] [Polished bronze, lacquered] [Satin bronze, lacquered] [Plastic laminate].

If doors are same at all floors, delete second and third options in title of subparagraph above and delete subparagraph below; otherwise, retain and edit both subparagraphs.

h. Doors[ and Transoms] at Other Floors:  [Enameled steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Textured stainless steel] [Polished bronze, lacquered] [Satin bronze, lacquered] [Plastic laminate].

Copy and edit subparagraph below to suit Project.  Nickel silver sills are more durable than aluminum sills but are as expensive as bronze.

i. Sills [at First Floor] [at Basement Floors]:  [Aluminum, mill finish] [Bronze, polished] [Nickel silver, polished].

If sills are same at all floors, delete both options in title of subparagraph above and delete subparagraph below; otherwise, retain and edit both subparagraphs.

j. Sills at Other Floors:  [Aluminum, mill finish] [Bronze, polished] [Nickel silver, polished].

Copy and edit subparagraph below to suit Project.

17. Hall Fixtures [at First Floor] [at Basement Floors]:  [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Polished bronze, lacquered] [Satin bronze, lacquered] [Recessed type with no exposed-metal surfaces].

If hall fixtures are same at all floors, delete both options in title of subparagraph above and delete first subparagraph below; otherwise, retain and edit both subparagraphs.

18. Hall Fixtures at Other Floors:  [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Polished bronze, lacquered] [Satin bronze, lacquered] [Recessed type with no exposed-metal surfaces].

19. Additional Requirements:

a. Provide inspection certificate in each car, mounted under acrylic cover with frame made from [polished stainless steel, No. 8 finish] [satin stainless steel, No. 4 finish] [polished bronze, lacquered] [satin bronze, lacquered].

Delete subparagraph below if not required.

b. Provide blanket hooks[ in all cars] and [one] [two] <Insert number> complete set(s) of full-height protective blankets.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine elevator areas, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance.  Verify critical dimensions and examine supporting structure and other conditions under which elevator work is to be installed.

Delete first subparagraph below if not required.

1. For the record, prepare a written report, endorsed by Installer, listing dimensional discrepancies and conditions detrimental to performance or indicating that dimensions and conditions were found to be satisfactory.

2. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Delete first four paragraphs and associated subparagraphs below for holeless elevators.

Delete paragraph below if excavation for cylinder is specified in Division 2 Section "Earthwork."

A. Excavation for Cylinder:  Drill well hole in[ each] elevator pit to accommodate installation of cylinder; comply with applicable requirements in Division 2 Section "Earthwork."

If retaining paragraph below, usually delete "waterproof" and retain "as necessary" option.  Well casing is essentially part of Contractor's means and methods unless required by authorities having jurisdiction, but requiring a well casing could help prevent disputes if cylinder well-hole excavation is not being provided by elevator Installer.

B. Provide[ waterproof] well casing[ as necessary] to retain walls of well hole.

Revise paragraph below if protective casing is deleted from Part 2.  Delete option if requirement for waterproof well casing is not retained in paragraph above.

C. Install cylinder in protective casing within well hole.  Before installing protective casing, remove water and debris from well hole[ and provide permanent waterproof seal at bottom of well casing].

Delete subparagraph below if corrosion protective filler is not used.

1. Fill void space between protective casing and cylinder with corrosion protective filler.

Delete subparagraph below if authorities having jurisdiction require a well casing with annular space left empty.

2. Align cylinders and fill space around protective casing with fine sand.

Select one of two options in paragraph below.  Usually select first option if waterproof well casing is required, and second if protective casing is used.

D. Install cylinder plumb and accurately centered for elevator car position and travel.  Anchor securely in place, supported at pit floor.  Seal between [well] [protective] casing and pit floor with 4 inches (100 mm) of nonshrink, nonmetallic grout.

Retain first paragraph below if aboveground cylinders are used.

E. Install cylinder plumb and accurately centered for elevator car position and travel.  Anchor securely in place, supported at pit floor and braced at intervals as needed to maintain alignment.  Anchor cylinder guides at spacing needed to maintain alignment and avoid overstressing guides.

F. Welded Construction:  Provide welded connections for installing elevator work where bolted connections are not required for subsequent removal or for normal operation, adjustment, inspection, maintenance, and replacement of worn parts.  Comply with AWS standards for workmanship and for qualifications of welding operators.

G. Sound Isolation:  Mount rotating and vibrating equipment on vibration-isolating mounts designed to effectively prevent transmission of vibrations to structure and thereby eliminate sources of structure-borne noise from elevator system.

H. Install piping above the floor, where possible.  Where not possible, install underground piping in Schedule 40 PVC pipe casing assembled with solvent-cemented fittings.

Retain paragraph above or first paragraph below, or use pipe trench with removable covers (detail on Drawings) if pipe must run under slab from pump room.  Method above provides better leak protection than below but costs more.

I. Install piping above the floor, where possible.  Where not possible, cover underground piping with permanent protective wrapping before backfilling.

J. Lubricate operating parts of systems as recommended by manufacturers.

K. Alignment:  Coordinate installation of hoistway entrances with installation of elevator guide rails for accurate alignment of entrances with car.  Where possible, delay installation of sills and frames until car is operable in shaft.  Reduce clearances to minimum, safe, workable dimension at each landing.

L. Leveling Tolerance:  1/4 inch (6 mm), up or down, regardless of load and direction of travel.

Possibly insert paragraphs for other tolerances, such as plumb tolerance for guide rails and entrance alignments.

M. Set sills flush with finished floor surface at landing.  Fill space under sill solidly with nonshrink, nonmetallic grout.

N. Locate hall signal equipment for elevators as follows, unless otherwise indicated:

Delete subparagraph below if push-button stations are shown on plans.

1. For groups of elevators, locate hall push-button stations between two elevators at center of group or at location most convenient for approaching passengers.

Delete first subparagraph below if jamb-mounted lanterns are used.

2. Place hall lanterns either above or beside each hoistway entrance.

3. Mount hall lanterns at a minimum of 72 inches (1829 mm) above finished floor.

3.3 FIELD QUALITY CONTROL

First paragraph below describes usual testing; additional tests may be specified at extra cost.

A. Acceptance Testing:  On completion of elevator installation and before permitting use (either temporary or permanent) of elevators, perform acceptance tests as required and recommended by ASME A17.1 and by governing regulations and agencies.

B. Advise Owner, Architect, and authorities having jurisdiction in advance of dates and times tests are to be performed on elevators.

3.4 PROTECTION

A. Temporary Use:  [Limit temporary use for construction purposes to one elevator.  ]Comply with the following requirements for[ each] elevator used for construction purposes:

1. Provide car with temporary enclosure, either within finished car or in place of finished car, to protect finishes from damage.

2. Provide strippable protective film on entrance and car doors and frames.

3. Provide padded wood bumpers on entrance door frames covering jambs and frame faces.

4. Provide other protective coverings, barriers, devices, signs, and procedures as needed to protect elevator and elevator equipment.

5. Do not load elevators beyond their rated weight capacity.

6. Engage elevator Installer to provide full maintenance service.  Include preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as necessary for proper elevator operation at rated speed and capacity.  Provide parts and supplies same as those used in the manufacture and installation of original equipment.

7. Engage elevator Installer to restore damaged work, if any, so no evidence remains of correction.  Return items that cannot be refinished in the field to the shop, make required repairs and refinish entire unit, or provide new units as required.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to operate[, adjust, and maintain] elevator(s).  Refer to Division 1 Section "Demonstration and Training."

B. Check operation of[ each] elevator with Owner's personnel present and before date of Substantial Completion.  Determine that operation systems and devices are functioning properly.

C. Check operation of[ each] elevator with Owner's personnel present not more than one month before end of warranty period.  Determine that operation systems and devices are functioning properly.

Insert a "Draft of Elevator Maintenance Agreement" here if Owner has a standard elevator service agreement.

END OF SECTION 14240END OF SECTION 14240

HYDRAULIC ELEVATORS
14240 - 1

