Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
02/03 (R 02/06)

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 14560 - CHUTES
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.

1. Waste chutes.

2. Laundry chutes.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 5 Section "Metal Fabrications" for metal supporting framework at floor penetrations.

2. Division 7 Section "Sheet Metal Flashing and Trim" for roof vent flashing and counterflashing.

3. Division 7 Section "Roof Accessories" for roof curbs.

4. Division 7 Section "Through-Penetration Firestop Systems" for annular spaces at doors, floors, or roofs.

5. Division 13 Section "Fire-Suppression Piping" for fire sprinklers.

6. Division 15 Sections for water-service connections.

7. Division 16 Sections for electrical-service connections.

1.3 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  Detail chute assemblies and indicate dimensions, weights, required clearances, method of field assembly, components, and location and size of each field connection.

1. Wiring Diagrams:  Power, signal and control wiring.

C. Product Certificates:  For each type of chute, signed by product manufacturer.

D. Operation and Maintenance Data:  For chutes to include in emergency, operation, and maintenance manuals.

Retain subparagraph below for waste recycling installations.

1. Include manufacturer's recycling plan guidelines.

1.4 QUALITY ASSURANCE

For discussion of NFPA 82 requirements, see the Evaluations.  Verify requirements of authorities having jurisdiction.

A. NFPA Compliance:  Provide chutes complying with NFPA 82.

NFPA 82 requires fire-rated door assemblies.

B. Fire-Rated Door Assemblies:  Assemblies complying with NFPA 80 that are listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction, for fire ratings indicated.

1. Test Pressure:  Test at atmospheric (neutral) pressure according to NFPA 252 or UL 10B.

Temperature-rise option is available from most manufacturers.  Verify requirements with authorities having jurisdiction.

2. Intake Door:  Class B labeled; [1] [1-1/2]-hour fire rated[ with 30-minute temperature rise of 250 deg F (140 deg C)].

3. Discharge Door:  Class B labeled; 1-hour fire rated[ with 30-minute temperature rise of 250 deg F (140 deg C)].

Delete subparagraph below if no access doors.

4. Access Door:  Class B labeled; [1] [1-1/2]-hour fire rated[ with 30-minute temperature rise of 250 deg F (140 deg C)].

C. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Midland Metalcraft Co.

2. U.S. Chutes.

3. Valiant Products, Inc.

4. Wilkinson Hi-Rise, LLC.

5. <Insert manufacturer.>

2.2 CHUTES

For aluminum-coated steel in first option below, revise coating designation to T1-25 (T1M-75) if a lighter coating is acceptable.

A. Chute Metal:  [Aluminum-coated, cold-rolled, commercial steel sheet; ASTM A 463/A 463M, Type 1 with not less than T1-40 (T1M-120) coating] [Type 430 stainless steel, ASTM A 240/A 240M] [Type 304 stainless steel, ASTM A 240/A 240M].

Retain one option in subparagraph below; the first option roughly corresponds to the obsolete 16 U.S. gage, the second to the obsolete 14 U.S. gage.  See the Evaluations.

1. Thickness:  [0.060 inch (1.6 mm)] [0.080 inch (2.0 mm)].

Retain first option in paragraph below for minimum diameter of linen chutes, second option for waste chutes according to NFPA 82.

B. Size:  [20-inch (508-mm) diameter] [24-inch (610-mm) diameter] [As indicated on Drawings] <Insert dimension>.

2.3 DOORS

NFPA 82 requires labeled fire-door assemblies at chute intakes.

A. Intake Door Assemblies:  ASTM A 240/A 240M, Type 304 stainless-steel, self-closing units with positive latch and latch handle; as required to provide fire-protection[ and temperature-rise] ratings indicated; and with frame suitable for enclosing chase construction.

Generally, retain hopper-type doors for rubbish chutes and hinged-type doors for laundry chutes.  NFPA 82 requires hopper type for general-access doors; limited-access doors (keyed) may be hopper or side-hinged type.  If more than one type is required, indicate types and locations on Drawings or insert description in first subparagraph below.

1. Door Type:  [Hopper] [Hopper, limited access] [Side hinged, limited access, 180-degree swing, square] [Type as indicated on Drawings] <Insert description>.

2. Size:  Manufacturer's standard size for door type, chute type, and diameter indicated.

3. Finish:  Manufacturer's standard satin or No. 3 directional polish.

Retain locks for limited-access hopper or side-hinged doors.  Chute door locks are required by NFPA 82 if door to chute compartment is not locked.

4. Locks:  Cylinder locks with keys that are removable only when cylinder is locked.  For each chute, key locks [alike] [to master key system].  For each door, furnish [four] <Insert number> keys.

Retain accessories in two subparagraphs below to suit Project.  Foot-operated, hopper-type doors usually do not have locks.

5. Foot Operators:  Hopper-type door operators that unlatch and open door when foot pedal is depressed.

6. Mechanical Interlocks:  Interlock system operated from discharge door to automatically lock intake doors.

Retain subparagraph above or below, or both, to close intake doors for system service or to limit intake to one door at a time.

7. Electrical Interlocks:  Interlock system that is energized by opening one intake door; remaining doors automatically lock when system is energized.

B. Discharge-Door Assemblies:  Aluminum-coated-steel doors as required to provide fire-protection[ and temperature-rise] ratings indicated; equipped with fusible links that cause doors to close in the event of fire.

Vertical-type discharge-door units are used for both waste and laundry chutes.

1. Direct Vertical Discharge:  Provide inclined, horizontally rolling, shutter-type unit.

Usually retain horizontal discharge doors for laundry chutes only.

2. Horizontal Discharge:  Provide top-hinged, self-closing, hopper door with self-latching hardware; floor-mounted leg brace designed to absorb impact of material dropping against chute; and minimum NPS 2 (DN 50) drain pipe connection.

C. Heat-[ and Smoke-]Detector System:  Interlock system with temperature-rise elements that locks chute doors when temperature in chute reaches a predetermined, adjustable temperature.

Retain option for smoke detector in paragraph above along with subparagraph below if required by authorities having jurisdiction or to suit Project.

1. Locate smoke detector outside discharge door with solenoid to close discharge door.

Retain paragraph below for access door in chase wall to service flushing spray unit or sanitizing unit located above highest intake door.

D. Access Door Assemblies:  Manufacturer's standard ASTM A 240/A 240M, Type 302/304 stainless-steel doors; as required to provide fire-protection[ and temperature-rise] ratings indicated; with frame suitable for enclosing chase construction; and in satin or No. 3 directional polish finish.

Indicate locations of manual control stations on Drawings.

E. Manual Control System:  Control system with manual switches that lock doors of chute during shutdown hours and service operations.

2.4 ACCESSORIES

A. Fire Sprinklers:  NPS 1/2 (DN 13) fire sprinklers ready for piping connections.

Flushing units are standard equipment but are probably inadequate for chutes that handle wet trash; consider specifying sanitizing units for these applications.

B. Flushing Spray Unit:  NPS 3/4 (DN 19) spray head unit located in chute above highest intake door, ready for hot-water piping connection, and with access for head and piping maintenance.

C. Sanitizing Unit:  NPS 3/4 (DN 19) disinfecting and sanitizing spray head unit located in chute above highest intake door, including 1-gal. (3.8-L) tank and adjustable proportioning valve with bypass for manual control of sanitizing and flushing operation, ready for hot-water piping connection, and with access for head and piping maintenance.

D. Intake Door Baffles:  Rubber baffles, 1/8 inch (3 mm) thick.

E. Sound Dampening:  Manufacturer's standard exterior mastic coating on chute.

1. Sound and vibration isolator pads at floor supporting frames.

If needed, insert other accessories including ADA-compliant automatic door operator, controls, recycling systems, and signs.

2.5 FABRICATION

A. General:  Factory-assemble chutes to greatest extent practical with continuously welded or lock-seamed joints without bolts, rivets, or clips projecting on chute interior.  Include intake-door assemblies and metal supporting framing at each floor, and chute expansion joints between each support point.

On high-security-risk buildings, consider inserting requirements for burglar-resistant grilles at roof-deck line.  Select vent height in first paragraph below to suit requirements of authorities having jurisdiction.  NFPA 82 requires a minimum vent height of 36 inches (910 mm) above the roof, and permits lower height for Type I or II buildings, subject to approval of authorities having jurisdiction.

B. Roof Vent:  Fabricate vent unit to extend [36 inches (910 mm)] [48 inches (1200 mm)] <Insert number> above roof with full-diameter, screened vent and metal safety cap or glass explosion-release cap.  Fabricate with roof-deck flange, counterflashing, and clamping ring of nonferrous metal compatible with chute metal.

C. Fire Sprinklers:  Comply with NFPA 13.  Locate fire sprinklers at or above the top service opening of chutes, within the chute at alternate floor levels in buildings more than two stories tall, and at the lowest service level.

D. Equipment Access:  Fabricate chutes with access for maintaining equipment located within the chute, such as flushing and sanitizing units, fire sprinklers, and plumbing and electrical connections.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. General:  Comply with NFPA 82 requirements and with chute manufacturer's written instructions.  Assemble components with tight, nonleaking joints.  Anchor securely to supporting structure to withstand impact and stresses on vent units.  Install chute and components to maintain fire-resistive construction of chute and enclosing chase.

B. Install chutes plumb, without offsets or obstructions that might prevent materials from free falling within chutes.

Generally, roof curbs are recommended by chute manufacturer.  Detail roof-curb requirements on Drawings or insert in first paragraph below.

C. Anchor roof flanges of chute vents before installing roofing and flashing.  Install chute-vent counterflashing after roofing and roof-penetration flashing are installed.

D. Intake and Discharge Doors:  Interface door units with throat sections of chutes for safe, snag-resistant, sanitary depositing of materials in chutes by users.

Delete foot-pedal requirement in subparagraph below if not applicable.

1. Coordinate installation of foot-pedal door operator with installation of door and chase.

Delete interconnection in subparagraph below if not applicable.

2. Interconnect sanitizer control with door interlock system.

E. Electrical Interlock System:  Comply with applicable NECA 1 recommendations.

F. Test chute components after installation.  Operate doors, locks, and interlock systems to demonstrate that hardware is adjusted and electrical wiring is connected correctly.  Complete test operations before installing chase enclosures.

G. Test fire sprinklers and heat- and smoke-sensing devices for proper operation.

Delete paragraph below if not applicable.

H. Operate sanitizing unit through one complete cycle of chute use and cleanup, and replenish chemicals or cleaning fluids in unit containers.

3.2 CLEANING

A. After completing chase enclosure, clean exposed surfaces of chute system's components.  Do not remove labels of independent testing and inspecting agencies.

3.3 DEMONSTRATION

A. Demonstrate use of chute and equipment to Owner's personnel.

Delete paragraph below if not applicable.

B. Demonstrate replenishment of sanitizing-unit chemicals or cleaning fluids.

END OF SECTION 14560

CHUTES
14560 - 1

