Copyright 2005 AIA
MASTERSPEC Full Length
09/05

Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15111 - GENERAL-DUTY VALVES FOR PLUMBING PIPING
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Bronze angle valves.

2. Brass ball valves.

3. Bronze ball valves.

4. Iron ball valves.

5. Iron, single-flange butterfly valves.

6. Iron, grooved-end butterfly valves.

7. Bronze lift check valves.

8. Bronze swing check valves.

9. Iron swing check valves.

10. Iron swing check valves with closure control.

11. Iron, grooved-end swing check valves.

12. Iron, center-guided check valves.

13. Iron, plate-type check valves.

14. Bronze gate valves.

15. Iron gate valves.

16. Bronze globe valves.

17. Iron globe valves.

18. Lubricated plug valves.

19. Chainwheels.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Division 2 water distribution piping Sections for general-duty and specialty valves for site construction piping.

2. Division 15 plumbing piping Sections for specialty valves applicable to those Sections only.

3. Division 15 Section "Identification for Plumbing Piping and Equipment" for valve tags and schedules.

1.3 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. CWP:  Cold working pressure.

B. EPDM:  Ethylene propylene copolymer rubber.

C. NBR:  Acrylonitrile-butadiene, Buna-N, or nitrile rubber.

D. NRS:  Nonrising stem.

E. OS&Y:  Outside screw and yoke.

F. RS:  Rising stem.

G. SWP:  Steam working pressure.

1.4 SUBMITTALS

Paragraph below is defined in Division 1 Section "Submittal Procedures" as an "Action Submittal."

A. Product Data:  For each type of valve indicated.

1.5 QUALITY ASSURANCE

A. Source Limitations for Valves:  Obtain each type of valve from single source from single manufacturer.

B. ASME Compliance:

1. ASME B16.10 and ASME B16.34 for ferrous valve dimensions and design criteria.

2. ASME B31.1 for power piping valves.

3. ASME B31.9 for building services piping valves.

C. NSF Compliance:  NSF 61 for valve materials for potable-water service.

1.6 DELIVERY, STORAGE, AND HANDLING

Information in this article is paraphrased from MSS.

A. Prepare valves for shipping as follows:

1. Protect internal parts against rust and corrosion.

2. Protect threads, flange faces, grooves, and weld ends.

3. Set angle, gate, and globe valves closed to prevent rattling.

4. Set ball and plug valves open to minimize exposure of functional surfaces.

5. Set butterfly valves closed or slightly open.

6. Block check valves in either closed or open position.

B. Use the following precautions during storage:

1. Maintain valve end protection.

2. Store valves indoors and maintain at higher than ambient dew point temperature.  If outdoor storage is necessary, store valves off the ground in watertight enclosures.

C. Use sling to handle large valves; rig sling to avoid damage to exposed parts.  Do not use handwheels or stems as lifting or rigging points.

PART 2 -  PRODUCTS

2.1 GENERAL REQUIREMENTS FOR VALVES

Plumbing valve applications specified in this Section are limited to NPS 12 (DN 300).  Many valves specified are available in larger sizes.

A. Refer to valve schedule articles for applications of valves.

Caution:  Revise pressure ratings and insert temperature ratings in valve articles if valves with higher ratings are required.  Valves larger than NPS 12 (DN 300) typically have a lower pressure rating than smaller valves.  Verify pressure requirements for large valves.

B. Valve Pressure and Temperature Ratings:  Not less than indicated and as required for system pressures and temperatures.

C. Valve Sizes:  Same as upstream piping unless otherwise indicated.

D. Valve Actuator Types:

1. Gear Actuator:  For quarter-turn valves NPS 8 (DN 200) and larger.

2. Handwheel:  For valves other than quarter-turn types.

3. Handlever:  For quarter-turn valves NPS 6 (DN 150) and smaller[ except plug valves].

4. Wrench:  For plug valves with square heads.  Furnish Owner with 1 wrench for every [5] [10] <Insert number> plug valves, for each size square plug-valve head.

5. Chainwheel:  Device for attachment to valve handwheel, stem, or other actuator; of size and with chain for mounting height, as indicated in the "Valve Installation" Article.

E. Valves in Insulated Piping:  With 2-inch (50-mm) stem extensions and the following features:

1. Gate Valves:  With rising stem.

2. Ball Valves:  With extended operating handle of non-thermal-conductive material, and protective sleeve that allows operation of valve without breaking the vapor seal or disturbing insulation.

3. Butterfly Valves:  With extended neck.

F. Valve-End Connections:

1. Flanged:  With flanges according to ASME B16.1 for iron valves.

2. Grooved:  With grooves according to AWWA C606.

Valve solder-joint connections are common in smaller sizes of plumbing piping.  Soldering and brazing methods used to achieve required pressure-temperature ratings may damage internal valve parts.  Special installation requirements for soldered valves may make threaded valves more cost-effective.

Caution:  Use solder with melting point below 840 deg F (454 deg C) for angle, check, gate, and globe valves and below 421 deg F (216 deg C) for ball valves.

3. Solder Joint:  With sockets according to ASME B16.18.

4. Threaded:  With threads according to ASME B1.20.1.

G. Valve Bypass and Drain Connections:  MSS SP-45.

2.2 BRONZE ANGLE VALVES

Retain one or more of four paragraphs in this article if bronze angle valves are required.  MSS SP-80 covers bronze angle valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

A. Class 125, Bronze Angle Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Hammond Valve.

b. Milwaukee Valve Company.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 1.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends:  Threaded.

e. Stem and Disc:  Bronze.

f. Packing:  Asbestos free.

g. Handwheel:  Malleable iron[, bronze, or aluminum].

B. Class 125, Bronze Angle Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. NIBCO INC.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 2.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends:  Threaded.

e. Stem:  Bronze.

f. Disc:  PTFE or TFE.

g. Packing:  Asbestos free.

h. Handwheel:  Malleable iron[, bronze, or aluminum].

C. Class 150, Bronze Angle Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Stockham Division.

b. Kitz Corporation.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 1.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and union-ring bonnet.

d. Ends:  Threaded.

e. Stem and Disc:  Bronze.

f. Packing:  Asbestos free.

g. Handwheel:  Malleable iron[, bronze, or aluminum].

D. Class 150, Bronze Angle Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Powell Valves.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 2.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and union-ring bonnet.

d. Ends:  Threaded.

e. Stem:  Bronze.

f. Disc:  PTFE or TFE.

g. Packing:  Asbestos free.

h. Handwheel:  Malleable iron[, bronze, or aluminum].

2.3 BRASS BALL VALVES

Retain one or more of seven paragraphs in this article if brass ball valves are required.  MSS SP-110 covers both brass and bronze, copper-alloy ball valves NPS 1/4 to NPS 4 (DN 8 to DN 100).  See the Evaluations and manufacturers' catalogs before selecting either brass or bronze ball valves or including both.

Caution:  Two-piece ball valves with a full or regular port are recommended for most services.  One-piece ball valves have a reduced port and one fewer leak path.  Three-piece ball valves are recommended if disassembly without removing valve from piping is required.

Where pressure drop is a concern, use full-port ball valves.  For corrosive or high-temperature applications, use stainless-steel-trim ball valves.

A. One-Piece, Reduced-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Kitz Corporation.

b. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Design:  One piece.

d. Body Material:  Forged brass.

e. Ends:  Threaded.

f. Seats:  PTFE or TFE.

g. Stem:  Brass.

h. Ball:  Chrome-plated brass.

i. Port:  Reduced.

B. Two-Piece, Full-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. DynaQuip Controls.

d. Flow-Tek, Inc.; a subsidiary of Bray International, Inc.

e. Hammond Valve.

f. Jamesbury; a subsidiary of Metso Automation.

g. Jomar International, LTD.

h. Kitz Corporation.

i. Legend Valve.

j. Marwin Valve; a division of Richards Industries.

k. Milwaukee Valve Company.

l. NIBCO INC.

m. Red-White Valve Corporation.

n. RuB Inc.

o. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Two piece.

e. Body Material:  Forged brass.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Brass.

i. Ball:  Chrome-plated brass.

j. Port:  Full.

C. Two-Piece, Full-Port, Brass Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Flow-Tek, Inc.; a subsidiary of Bray International, Inc.

d. Hammond Valve.

e. Jamesbury; a subsidiary of Metso Automation.

f. Kitz Corporation.

g. Marwin Valve; a division of Richards Industries.

h. Milwaukee Valve Company.

i. RuB Inc.

j. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Two piece.

e. Body Material:  Forged brass.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Stainless steel.

i. Ball:  Stainless steel, vented.

j. Port:  Full.

D. Two-Piece, Regular-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Hammond Valve.

b. Jamesbury; a subsidiary of Metso Automation.

c. Legend Valve.

d. Marwin Valve; a division of Richards Industries.

e. Milwaukee Valve Company.

f. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Two piece.

e. Body Material:  Forged brass.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Brass.

i. Ball:  Chrome-plated brass.

j. Port:  Regular.

E. Two-Piece, Regular-Port, Brass Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Jamesbury; a subsidiary of Metso Automation.

b. Marwin Valve; a division of Richards Industries.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Two piece.

e. Body Material:  Brass or bronze.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Stainless steel.

i. Ball:  Stainless steel, vented.

j. Port:  Regular.

F. Three-Piece, Full-Port, Brass Ball Valves with Brass Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Jomar International, LTD.

b. Kitz Corporation.

c. Red-White Valve Corporation.

d. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Three piece.

e. Body Material:  Forged brass.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Brass.

i. Ball:  Chrome-plated brass.

j. Port:  Full.

G. Three-Piece, Full-Port, Brass Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Jomar International, LTD.

b. Kitz Corporation.

c. Marwin Valve; a division of Richards Industries.

d. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Three piece.

e. Body Material:  Forged brass.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Stainless steel.

i. Ball:  Stainless steel, vented.

j. Port:  Full.

2.4 BRONZE BALL VALVES

Retain one or more of eight paragraphs in this article if bronze ball valves are required.  MSS SP-110 covers both brass and bronze, copper-alloy ball valves NPS 1/4 to NPS 4 (DN 8 to DN 100).  See the Evaluations and manufacturers' catalogs before selecting either brass or bronze ball valves or including both.

Caution:  Two-piece ball valves with a full or regular port are recommended for most services.  One-piece ball valves have a reduced port and one fewer leak path.  Three-piece ball valves are recommended if disassembly without removing valve from piping is required.

Where pressure drop is a concern, use full-port ball valves.  For corrosive or high-temperature applications, use stainless-steel-trim ball valves.

A. One-Piece, Reduced-Port, Bronze Ball Valves with Bronze Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. NIBCO INC.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Design:  One piece.

d. Body Material:  Bronze.

e. Ends:  Threaded.

f. Seats:  PTFE or TFE.

g. Stem:  Bronze.

h. Ball:  Chrome-plated brass.

i. Port:  Reduced.

B. One-Piece, Reduced-Port, Bronze Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Conbraco Industries, Inc.; Apollo Valves.

b. NIBCO INC.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. CWP Rating:  600 psig (4140 kPa).

c. Body Design:  One piece.

d. Body Material:  Bronze.

e. Ends:  Threaded.

f. Seats:  PTFE or TFE.

g. Stem:  Stainless steel.

h. Ball:  Stainless steel, vented.

i. Port:  Reduced.

C. Two-Piece, Full-Port, Bronze Ball Valves with Bronze Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Crane Co.; Crane Valve Group; Crane Valves.

d. Hammond Valve.

e. Lance Valves; a division of Advanced Thermal Systems, Inc.

f. Legend Valve.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Red-White Valve Corporation.

j. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

k. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Two piece.

e. Body Material:  Bronze.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Bronze.

i. Ball:  Chrome-plated brass.

j. Port:  Full.

D. Two-Piece, Full-Port, Bronze Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Conbraco Industries, Inc.; Apollo Valves.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Hammond Valve.

d. Lance Valves; a division of Advanced Thermal Systems, Inc.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Two piece.

e. Body Material:  Bronze.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Stainless steel.

i. Ball:  Stainless steel, vented.

j. Port:  Full.

E. Two-Piece, Regular-Port, Bronze Ball Valves with Bronze Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. DynaQuip Controls.

f. Hammond Valve.

g. Lance Valves; a division of Advanced Thermal Systems, Inc.

h. Milwaukee Valve Company.

i. NIBCO INC.

j. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Two piece.

e. Body Material:  Bronze.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Bronze.

i. Ball:  Chrome-plated brass.

j. Port:  Regular.

F. Two-Piece, Regular-Port, Bronze Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Conbraco Industries, Inc.; Apollo Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Hammond Valve.

d. Milwaukee Valve Company.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Two piece.

e. Body Material:  Bronze.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Stainless steel.

i. Ball:  Stainless steel, vented.

j. Port:  Regular.

G. Three-Piece, Full-Port, Bronze Ball Valves with Bronze Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Conbraco Industries, Inc.; Apollo Valves.

b. DynaQuip Controls.

c. Hammond Valve.

d. Milwaukee Valve Company.

e. NIBCO INC.

f. Red-White Valve Corporation.

g. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Three piece.

e. Body Material:  Bronze.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Bronze.

i. Ball:  Chrome-plated brass.

j. Port:  Full.

H. Three-Piece, Full-Port, Bronze Ball Valves with Stainless-Steel Trim:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Conbraco Industries, Inc.; Apollo Valves.

b. Hammond Valve.

c. Milwaukee Valve Company.

d. NIBCO INC.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-110.

b. SWP Rating:  150 psig (1035 kPa).

c. CWP Rating:  600 psig (4140 kPa).

d. Body Design:  Three piece.

e. Body Material:  Bronze.

f. Ends:  Threaded.

g. Seats:  PTFE or TFE.

h. Stem:  Stainless steel.

i. Ball:  Stainless steel, vented.

j. Port:  Full.

2.5 IRON BALL VALVES

Retain this article if iron ball valves are required.  MSS SP-72 covers iron ball valves NPS 1/2 to NPS 36 (DN 15 to DN 900).

A. Class 125, Iron Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Kitz Corporation.

d. Sure Flow Equipment Inc.

e. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

f. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-72.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Split body.

d. Body Material:  ASTM A 126, gray iron.

e. Ends:  Flanged.

f. Seats:  PTFE or TFE.

g. Stem:  Stainless steel.

h. Ball:  Stainless steel.

i. Port:  Full.

2.6 IRON, SINGLE-FLANGE BUTTERFLY VALVES

Retain one or more of six paragraphs in this article if iron, single-flange butterfly valves are required.  MSS SP-67 covers iron, single-flange butterfly valves NPS 1-1/2 to NPS 72 (DN 40 to DN 1800).

A. 200 CWP, Iron, Single-Flange Butterfly Valves with EPDM Seat and Aluminum-Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

d. Crane Co.; Crane Valve Group; Jenkins Valves.

e. Crane Co.; Crane Valve Group; Stockham Division.

f. DeZurik Water Controls.

g. Flo Fab Inc.

h. Hammond Valve.

i. Kitz Corporation.

j. Legend Valve.

k. Milwaukee Valve Company.

l. NIBCO INC.

m. Norriseal; a Dover Corporation company.

n. Red-White Valve Corporation.

o. Spence Strainers International; a division of CIRCOR International, Inc.

p. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

q. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-67, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material:  ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat:  EPDM.

f. Stem:  One- or two-piece stainless steel.

g. Disc:  Aluminum bronze.

B. 200 CWP, Iron, Single-Flange Butterfly Valves with NBR Seat and Aluminum-Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. Conbraco Industries, Inc.; Apollo Valves.

c. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

d. Crane Co.; Crane Valve Group; Jenkins Valves.

e. Crane Co.; Crane Valve Group; Stockham Division.

f. DeZurik Water Controls.

g. Flo Fab Inc.

h. Hammond Valve.

i. Kitz Corporation.

j. Legend Valve.

k. Milwaukee Valve Company.

l. NIBCO INC.

m. Norriseal; a Dover Corporation company.

n. Red-White Valve Corporation.

o. Spence Strainers International; a division of CIRCOR International, Inc.

p. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

q. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-67, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material:  ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat:  NBR.

f. Stem:  One- or two-piece stainless steel.

g. Disc:  Aluminum bronze.

C. 200 CWP, Iron, Single-Flange Butterfly Valves with EPDM Seat and Ductile-Iron Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. American Valve, Inc.

c. Conbraco Industries, Inc.; Apollo Valves.

d. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

e. Crane Co.; Crane Valve Group; Center Line.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. DeZurik Water Controls.

h. Flo Fab Inc.

i. Hammond Valve.

j. Kitz Corporation.

k. Legend Valve.

l. Milwaukee Valve Company.

m. Mueller Steam Specialty; a division of SPX Corporation.

n. NIBCO INC.

o. Norriseal; a Dover Corporation company.

p. Spence Strainers International; a division of CIRCOR International, Inc.

q. Sure Flow Equipment Inc.

r. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

s. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-67, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material:  ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat:  EPDM.

f. Stem:  One- or two-piece stainless steel.

g. Disc:  Nickel-plated[ or -coated] ductile iron.

D. 200 CWP, Iron, Single-Flange Butterfly Valves with NBR Seat and Ductile-Iron Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. American Valve, Inc.

c. Conbraco Industries, Inc.; Apollo Valves.

d. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

e. Crane Co.; Crane Valve Group; Center Line.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. DeZurik Water Controls.

h. Flo Fab Inc.

i. Hammond Valve.

j. Kitz Corporation.

k. Legend Valve.

l. Milwaukee Valve Company.

m. Mueller Steam Specialty; a division of SPX Corporation.

n. NIBCO INC.

o. Norriseal; a Dover Corporation company.

p. Spence Strainers International; a division of CIRCOR International, Inc.

q. Sure Flow Equipment Inc.

r. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

s. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-67, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material:  ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat:  NBR.

f. Stem:  One- or two-piece stainless steel.

g. Disc:  Nickel-plated[ or -coated] ductile iron.

E. 200 CWP, Iron, Single-Flange Butterfly Valves with EPDM Seat and Stainless-Steel Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valve and Controls; a division of ABZ Manufacturing, Inc.

b. American Valve, Inc.

c. Conbraco Industries, Inc.; Apollo Valves.

d. Cooper Cameron Valves; a division of Cooper Cameron Corporation.

e. Crane Co.; Crane Valve Group; Jenkins Valves.

f. Crane Co.; Crane Valve Group; Stockham Division.

g. DeZurik Water Controls.

h. Flo Fab Inc.

i. Hammond Valve.

j. Kitz Corporation.

k. Legend Valve.

l. Milwaukee Valve Company.

m. Mueller Steam Specialty; a division of SPX Corporation.

n. NIBCO INC.

o. Norriseal; a Dover Corporation company.

p. Red-White Valve Corporation.

q. Spence Strainers International; a division of CIRCOR International, Inc.

r. Sure Flow Equipment Inc.

s. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

t. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-67, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material:  ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat:  EPDM.

f. Stem:  One- or two-piece stainless steel.

g. Disc:  Stainless steel.

F. 200 CWP, Iron, Single-Flange Butterfly Valves with NBR Seat and Stainless-Steel Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. ABZ Valves and Controls; A div. of ABZ Manufacturing, Inc.

b. American Valve, Inc.

c. Conbraco Industries, Inc.; Apollo Valves.

d. Cooper Cameron Valves; A div. of Cooper Cameron Corp.

e. Crane Co.; Crane Valve Group; Jenkins Valves.

f. Crane Co.; Crane Valve Group; Stockham Div.

g. DeZurik Water Controls.

h. Flo Fab Inc.

i. Hammond Valve.

j. Kitz Corporation.

k. Legend Valve.

l. Milwaukee Valve Company.

m. Mueller Steam Specialty; a division of SPX Corporation.

n. NIBCO INC.

o. Norriseal; a Dover Corporation company.

p. Red-White Valve Corporation.

q. Spence Strainers International; a division of CIRCOR International, Inc.

r. Sure Flow Equipment Inc.

s. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

t. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-67, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Lug type; suitable for bidirectional dead-end service at rated pressure without use of downstream flange.

d. Body Material:  ASTM A 126, cast iron or ASTM A 536, ductile iron.

e. Seat:  NBR.

f. Stem:  One- or two-piece stainless steel.

g. Disc:  Stainless steel.

2.7 IRON, GROOVED-END BUTTERFLY VALVES

Retain one or both paragraphs in this article if iron, grooved-end butterfly valves are required.  MSS SP-67 covers iron, grooved-end butterfly valves NPS 1-1/2 to NPS 72 (DN 40 to DN 1800).

A. 175 CWP, Iron, Grooved-End Butterfly Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Kennedy Valve; a division of McWane, Inc.

b. Shurjoint Piping Products.

c. Tyco Fire Products LP; Grinnell Mechanical Products.

d. Victaulic Company.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-67, Type I.

b. CWP Rating:  175 psig (1200 kPa).

c. Body Material:  Coated, ductile iron.

d. Stem:  Two-piece stainless steel.

e. Disc:  Coated, ductile iron.

f. Seal:  EPDM.

B. 300 CWP, Iron, Grooved-End Butterfly Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. Kennedy Valve; a division of McWane, Inc.

c. Mueller Steam Specialty; a division of SPX Corporation.

d. NIBCO INC.

e. Shurjoint Piping Products.

f. Tyco Fire Products LP; Grinnell Mechanical Products.

g. Victaulic Company.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-67, Type I.

b. NPS 8 (DN 200) and Smaller CWP Rating:  300 psig (2070 kPa).

c. NPS 10 (DN 250) and Larger CWP Rating:  200 psig (1380 kPa).

d. Body Material:  Coated, ductile iron.

e. Stem:  Two-piece stainless steel.

f. Disc:  Coated, ductile iron.

g. Seal:  EPDM.

2.8 BRONZE LIFT CHECK VALVES

Retain one or both paragraphs in this article if bronze lift check valves are required.  MSS SP-80 covers bronze lift check valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

A. Class 125, Lift Check Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 1.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Vertical flow.

d. Body Material:  ASTM B 61 or ASTM B 62, bronze.

e. Ends:  Threaded.

f. Disc:  Bronze.

B. Class 125, Lift Check Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Flo Fab Inc.

b. Hammond Valve.

c. Kitz Corporation.

d. Milwaukee Valve Company.

e. Mueller Steam Specialty; a division of SPX Corporation.

f. NIBCO INC.

g. Red-White Valve Corporation.

h. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

i. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 2.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Vertical flow.

d. Body Material:  ASTM B 61 or ASTM B 62, bronze.

e. Ends:  Threaded.

f. Disc:  NBR, PTFE, or TFE.

2.9 BRONZE SWING CHECK VALVES

Retain one or more of four paragraphs in this article if bronze swing check valves are required.  MSS SP-80 covers bronze swing check valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

A. Class 125, Bronze Swing Check Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. Hammond Valve.

f. Kitz Corporation.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Powell Valves.

j. Red-White Valve Corporation.

k. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

l. Zy-Tech Global Industries, Inc.

m. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 3.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Horizontal flow.

d. Body Material:  ASTM B 62, bronze.

e. Ends:  Threaded.

f. Disc:  Bronze.

B. Class 125, Bronze Swing Check Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Kitz Corporation.

f. Milwaukee Valve Company.

g. NIBCO INC.

h. Red-White Valve Corporation.

i. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

j. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 4.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Horizontal flow.

d. Body Material:  ASTM B 62, bronze.

e. Ends:  Threaded.

f. Disc:  PTFE or TFE.

C. Class 150, Bronze Swing Check Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. Kitz Corporation.

f. Milwaukee Valve Company.

g. NIBCO INC.

h. Red-White Valve Corporation.

i. Zy-Tech Global Industries, Inc.

j. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 3.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Design:  Horizontal flow.

d. Body Material:  ASTM B 62, bronze.

e. Ends:  Threaded.

f. Disc:  Bronze.

D. Class 150, Bronze Swing Check Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Hammond Valve.

d. Milwaukee Valve Company.

e. NIBCO INC.

f. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

g. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 4.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Design:  Horizontal flow.

d. Body Material:  ASTM B 62, bronze.

e. Ends:  Threaded.

f. Disc:  PTFE or TFE.

2.10 IRON SWING CHECK VALVES

Retain one or more of three paragraphs in this article if iron swing check valves are required.  MSS SP-71 covers iron swing check valves NPS 2 to NPS 24 (DN 50 to DN 600).

A. Class 125, Iron Swing Check Valves with Metal Seats:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Kitz Corporation.

f. Legend Valve.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Powell Valves.

j. Red-White Valve Corporation.

k. Sure Flow Equipment Inc.

l. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

m. Zy-Tech Global Industries, Inc.

n. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-71, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Clear or full waterway.

d. Body Material:  ASTM A 126, gray iron with bolted bonnet.

e. Ends:  Flanged.

f. Trim:  Bronze.

g. Gasket:  Asbestos free.

B. Class 125, Iron Swing Check Valves with Nonmetallic-to-Metal Seats:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-71, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Clear or full waterway.

d. Body Material:  ASTM A 126, gray iron with bolted bonnet.

e. Ends:  Flanged.

f. Trim:  Composition.

g. Seat Ring:  Bronze.

h. Disc Holder:  Bronze.

i. Disc:  PTFE or TFE.

j. Gasket:  Asbestos free.

C. Class 250, Iron Swing Check Valves with Metal Seats:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-71, Type I.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Design:  Clear or full waterway.

d. Body Material:  ASTM A 126, gray iron with bolted bonnet.

e. Ends:  Flanged.

f. Trim:  Bronze.

g. Gasket:  Asbestos free.

2.11 IRON SWING CHECK VALVES WITH CLOSURE CONTROL

A. Class 125, Iron Swing Check Valves with Lever- and Spring-Closure Control:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. NIBCO INC.

b. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-71, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Clear or full waterway.

d. Body Material:  ASTM A 126, gray iron with bolted bonnet.

e. Ends:  Flanged.

f. Trim:  Bronze.

g. Gasket:  Asbestos free.

h. Closure Control:  Factory-installed, exterior lever and spring.

B. Class 125, Iron Swing Check Valves with Lever- and Weight-Closure Control:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-71, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Clear or full waterway.

d. Body Material:  ASTM A 126, gray iron with bolted bonnet.

e. Ends:  Flanged.

f. Trim:  Bronze.

g. Gasket:  Asbestos free.

h. Closure Control:  Factory-installed, exterior lever and weight.

2.12 IRON, GROOVED-END SWING CHECK VALVES

Retain this article if iron, grooved-end swing check valves are required.  No standard for these valves was located.  They are available in NPS 2 to NPS 12 (DN 50 to DN 300).

A. 300 CWP, Iron, Grooved-End Swing Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. Shurjoint Piping Products.

c. Tyco Fire Products LP; Grinnell Mechanical Products.

d. Victaulic Company.

e. <Insert manufacturer's name>.

2. Description:

a. CWP Rating:  300 psig (2070 kPa).

b. Body Material:  ASTM A 536, ductile iron.

c. Seal:  EPDM.

d. Disc:  Spring-operated, ductile iron or stainless steel.

2.13 IRON, CENTER-GUIDED CHECK VALVES

Retain one or more of 16 paragraphs in this article if iron, center-guided check valves are required.  MSS SP-125 covers iron, center-guided check valves NPS 2 to NPS 42 (DN 50 to DN 1050).

A. Class 125, Iron, Compact-Wafer, Center-Guided Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. APCO Willamette Valve and Primer Corporation.

c. Crispin Valve.

d. DFT Inc.

e. Flo Fab Inc.

f. GA Industries, Inc.

g. Hammond Valve.

h. Metraflex, Inc.

i. Milwaukee Valve Company.

j. Mueller Steam Specialty; a division of SPX Corporation.

k. NIBCO INC.

l. Spence Strainers International; a division of CIRCOR International, Inc.

m. Sure Flow Equipment Inc.

n. Val-Matic Valve & Manufacturing Corp.

o. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

p. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 126, gray iron.

d. Style:  Compact wafer.

e. Seat:  Bronze.

B. Class 125, Iron, Globe, Center-Guided Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. DFT Inc.

d. Flomatic Corporation.

e. Hammond Valve.

f. Metraflex, Inc.

g. Milwaukee Valve Company.

h. Mueller Steam Specialty; a division of SPX Corporation.

i. NIBCO INC.

j. Spence Strainers International; a division of CIRCOR International, Inc.

k. Sure Flow Equipment Inc.

l. Val-Matic Valve & Manufacturing Corp.

m. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

n. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 126, gray iron.

d. Style:  Globe, spring loaded.

e. Ends:  Flanged.

f. Seat:  Bronze.

C. Class 150, Iron, Compact-Wafer, Center-Guided Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. Val-Matic Valve & Manufacturing Corp.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

d. Style:  Compact wafer.

e. Seat:  Bronze.

D. Class 150, Iron, Globe, Center-Guided Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. Val-Matic Valve & Manufacturing Corp.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

d. Style:  Globe, spring loaded.

e. Ends:  Flanged.

f. Seat:  Bronze.

E. Class 250, Iron, Compact-Wafer, Center-Guided Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. DFT Inc.

d. Flo Fab Inc.

e. Hammond Valve.

f. Metraflex, Inc.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Sure Flow Equipment Inc.

j. Val-Matic Valve & Manufacturing Corp.

k. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Material:  ASTM A 126, gray iron.

d. Style:  Compact wafer, spring loaded.

e. Seat:  Bronze.

F. Class 250, Iron, Globe, Center-Guided Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. DFT Inc.

d. Flomatic Corporation.

e. Hammond Valve.

f. Metraflex, Inc.

g. Milwaukee Valve Company.

h. Mueller Steam Specialty; a division of SPX Corporation.

i. NIBCO INC.

j. Val-Matic Valve & Manufacturing Corp.

k. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Material:  ASTM A 126, gray iron.

d. Style:  Globe, spring loaded.

e. Ends:  Flanged.

f. Seat:  Bronze.

G. Class 300, Iron, Compact-Wafer, Center-Guided Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. Val-Matic Valve & Manufacturing Corp.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

d. Style:  Compact wafer, spring loaded.

e. Seat:  Bronze.

H. Class 300, Iron, Globe, Center-Guided Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. Val-Matic Valve & Manufacturing Corp.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

d. Style:  Globe, spring loaded.

e. Ends:  Flanged.

f. Seat:  Bronze.

I. Class 125, Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. DFT Inc.

d. Flo Fab Inc.

e. Hammond Valve.

f. Milwaukee Valve Company.

g. NIBCO INC.

h. Spence Strainers International; a division of CIRCOR International, Inc.

i. Sure Flow Equipment Inc.

j. Val-Matic Valve & Manufacturing Corp.

k. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 126, gray iron.

d. Style:  Compact wafer.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

J. Class 125, Iron, Globe, Center-Guided Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Anvil International, Inc.

b. APCO Willamette Valve and Primer Corporation.

c. Crispin Valve.

d. DFT Inc.

e. GA Industries, Inc.

f. Hammond Valve.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Sure Flow Equipment Inc.

j. Val-Matic Valve & Manufacturing Corp.

k. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 126, gray iron.

d. Style:  Globe, spring loaded.

e. Ends:  Flanged.

f. Seat:  [EPDM] [or] [NBR] <Insert material>.

K. Class 150, Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. Val-Matic Valve & Manufacturing Corp.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

d. Style:  Compact wafer.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

L. Class 150, Iron, Globe, Center-Guided Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. DFT Inc.

d. Val-Matic Valve & Manufacturing Corp.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

d. Style:  Globe, spring loaded.

e. Ends:  Flanged.

f. Seat:  [EPDM] [or] [NBR] <Insert material>.

M. Class 250, Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. DFT Inc.

d. Flo Fab Inc.

e. Hammond Valve.

f. Milwaukee Valve Company.

g. NIBCO INC.

h. Sure Flow Equipment Inc.

i. Val-Matic Valve & Manufacturing Corp.

j. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Material:  ASTM A 126, gray iron.

d. Style:  Compact wafer, spring loaded.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

N. Class 250, Iron, Globe, Center-Guided Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. DFT Inc.

d. Hammond Valve.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Val-Matic Valve & Manufacturing Corp.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Material:  ASTM A 126, gray iron.

d. Style:  Globe, spring loaded.

e. Ends:  Flanged.

f. Seat:  [EPDM] [or] [NBR] <Insert material>.

O. Class 300, Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. Val-Matic Valve & Manufacturing Corp.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

d. Style:  Compact wafer, spring loaded.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

P. Class 300, Iron, Globe, Center-Guided Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crispin Valve.

c. Val-Matic Valve & Manufacturing Corp.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-125.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

d. Style:  Globe, spring loaded.

e. Ends:  Flanged.

f. Seat:  [EPDM] [or] [NBR] <Insert material>.

2.14 IRON, PLATE-TYPE CHECK VALVES

Retain one or more of 10 paragraphs in this article if iron, plate-type check valves are required.  API 594 covers iron, plate-type check valves NPS 2 to NPS 60 (DN 50 to DN 1500).

A. Class 125, Iron, Dual-Plate Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Flomatic Corporation.

d. Mueller Steam Specialty; a division of SPX Corporation.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Wafer, spring-loaded plates.

d. Body Material:  ASTM A 126, gray iron.

e. Seat:  Bronze.

B. Class 150, Iron, Dual-Plate Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Mueller Steam Specialty; a division of SPX Corporation.

d. Val-Matic Valve & Manufacturing Corp.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Design:  Wafer, spring-loaded plates.

d. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

e. Seat:  Bronze.

C. Class 250, Iron, Dual-Plate Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Design:  Wafer, spring-loaded plates.

d. Body Material:  ASTM A 126, gray iron.

e. Seat:  Bronze.

D. Class 300, Iron, Dual-Plate Check Valves with Metal Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Mueller Steam Specialty; a division of SPX Corporation.

d. Val-Matic Valve & Manufacturing Corp.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Design:  Wafer, spring-loaded plates.

d. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

e. Seat:  Bronze.

E. Class 125, Iron, Single-Plate Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Flo Fab Inc.

b. Sure Flow Equipment Inc.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Wafer, spring-loaded plate.

d. Body Material:  ASTM A 126, gray iron.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

F. Class 125, Iron, Dual-Plate Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Cooper Cameron Valves TVB Techno.

c. Crane Co.; Crane Valve Group; Crane Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. NIBCO INC.

f. Spence Strainers International; a division of CIRCOR International, Inc.

g. Sure Flow Equipment Inc.

h. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

i. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Design:  Wafer, spring-loaded plates.

d. Body Material:  ASTM A 126, gray iron.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

G. Class 150, Iron, Dual-Plate Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Val-Matic Valve & Manufacturing Corp.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Design:  Wafer, spring-loaded plates.

d. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

H. Class 250, Iron, Wafer, Single-Plate Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Sure Flow Equipment Inc.

b. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Design:  Wafer, spring-loaded plate.

d. Body Material:  ASTM A 126, gray iron.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

I. Class 250, Iron, Dual-Plate Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Sure Flow Equipment Inc.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Design:  Wafer, spring-loaded plates.

d. Body Material:  ASTM A 126, gray iron.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

J. Class 300, Iron, Dual-Plate Check Valves with Resilient Seat:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. APCO Willamette Valve and Primer Corporation.

b. Val-Matic Valve & Manufacturing Corp.

c. <Insert manufacturer's name>.

2. Description:

a. Standard:  API 594.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Design:  Wafer, spring-loaded plates.

d. Body Material:  ASTM A 395/A 395M or ASTM A 536, ductile iron.

e. Seat:  [EPDM] [or] [NBR] <Insert material>.

2.15 BRONZE GATE VALVES

Retain one or more of four paragraphs in this article if bronze gate valves are required.  MSS SP-80 covers bronze gate valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

A. Class 125, NRS Bronze Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. Hammond Valve.

f. Kitz Corporation.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Powell Valves.

j. Red-White Valve Corporation.

k. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

l. Zy-Tech Global Industries, Inc.

m. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 1.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends:  Threaded[ or solder joint].

e. Stem:  Bronze.

f. Disc:  Solid wedge; bronze.

g. Packing:  Asbestos free.

h. Handwheel:  Malleable iron[, bronze, or aluminum].

B. Class 125, RS Bronze Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Valve, Inc.

b. Crane Co.; Crane Valve Group; Crane Valves.

c. Crane Co.; Crane Valve Group; Jenkins Valves.

d. Crane Co.; Crane Valve Group; Stockham Division.

e. Hammond Valve.

f. Kitz Corporation.

g. Milwaukee Valve Company.

h. NIBCO INC.

i. Powell Valves.

j. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

k. Zy-Tech Global Industries, Inc.

l. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 2.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends:  Threaded[ or solder joint].

e. Stem:  Bronze.

f. Disc:  Solid wedge; bronze.

g. Packing:  Asbestos free.

h. Handwheel:  Malleable iron[, bronze, or aluminum].

C. Class 150, NRS Bronze Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Hammond Valve.

b. Kitz Corporation.

c. Milwaukee Valve Company.

d. NIBCO INC.

e. Powell Valves.

f. Red-White Valve Corporation.

g. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 1.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and union-ring bonnet.

d. Ends:  Threaded.

e. Stem:  Bronze.

f. Disc:  Solid wedge; bronze.

g. Packing:  Asbestos free.

h. Handwheel:  Malleable iron[, bronze, or aluminum].

D. Class 150, RS Bronze Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. Hammond Valve.

d. Kitz Corporation.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Powell Valves.

h. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

i. Zy-Tech Global Industries, Inc.

j. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 2.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and union-ring bonnet.

d. Ends:  Threaded.

e. Stem:  Bronze.

f. Disc:  Solid wedge; bronze.

g. Packing:  Asbestos free.

h. Handwheel:  Malleable iron[, bronze, or aluminum].

2.16 IRON GATE VALVES

Retain one or more of four paragraphs in this article if iron gate valves are required.  MSS SP-70 covers iron gate valves NPS 2 to NPS 48 (DN 50 to DN 1200).

A. Class 125, NRS, Iron Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Flo Fab Inc.

e. Hammond Valve.

f. Kitz Corporation.

g. Legend Valve.

h. Milwaukee Valve Company.

i. NIBCO INC.

j. Powell Valves.

k. Red-White Valve Corporation.

l. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

m. Zy-Tech Global Industries, Inc.

n. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-70, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 126, gray iron with bolted bonnet.

d. Ends:  Flanged.

e. Trim:  Bronze.

f. Disc:  Solid wedge.

g. Packing and Gasket:  Asbestos free.

B. Class 125, OS&Y, Iron Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Flo Fab Inc.

e. Hammond Valve.

f. Kitz Corporation.

g. Legend Valve.

h. Milwaukee Valve Company.

i. NIBCO INC.

j. Powell Valves.

k. Red-White Valve Corporation.

l. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

m. Zy-Tech Global Industries, Inc.

n. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-70, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 126, gray iron with bolted bonnet.

d. Ends:  Flanged.

e. Trim:  Bronze.

f. Disc:  Solid wedge.

g. Packing and Gasket:  Asbestos free.

C. Class 250, NRS, Iron Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. NIBCO INC.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-70, Type I.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Material:  ASTM A 126, gray iron with bolted bonnet.

d. Ends:  Flanged.

e. Trim:  Bronze.

f. Disc:  Solid wedge.

g. Packing and Gasket:  Asbestos free.

D. Class 250, OS&Y, Iron Gate Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. Hammond Valve.

d. Milwaukee Valve Company.

e. NIBCO INC.

f. Powell Valves.

g. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-70, Type I.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Material:  ASTM A 126, gray iron with bolted bonnet.

d. Ends:  Flanged.

e. Trim:  Bronze.

f. Disc:  Solid wedge.

g. Packing and Gasket:  Asbestos free.

2.17 BRONZE GLOBE VALVES

Retain one or more of three paragraphs in this article if bronze globe valves are required.  MSS SP-80 covers bronze globe valves NPS 1/4 to NPS 3 (DN 8 to DN 80).

A. Class 125, Bronze Globe Valves with Bronze Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. Hammond Valve.

d. Kitz Corporation.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Powell Valves.

h. Red-White Valve Corporation.

i. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

j. Zy-Tech Global Industries, Inc.

k. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 1.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends:  Threaded[ or solder joint].

e. Stem and Disc:  Bronze.

f. Packing:  Asbestos free.

g. Handwheel:  Malleable iron[, bronze, or aluminum].

B. Class 125, Bronze Globe Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Stockham Division.

c. NIBCO INC.

d. Red-White Valve Corporation.

e. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 2.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and screw-in bonnet.

d. Ends:  Threaded[ or solder joint].

e. Stem:  Bronze.

f. Disc:  PTFE or TFE.

g. Packing:  Asbestos free.

h. Handwheel:  Malleable iron[, bronze, or aluminum].

C. Class 150, Bronze Globe Valves with Nonmetallic Disc:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Hammond Valve.

c. Kitz Corporation.

d. Milwaukee Valve Company.

e. NIBCO INC.

f. Powell Valves.

g. Red-White Valve Corporation.

h. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

i. Zy-Tech Global Industries, Inc.

j. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-80, Type 2.

b. CWP Rating:  300 psig (2070 kPa).

c. Body Material:  ASTM B 62, bronze with integral seat and union-ring bonnet.

d. Ends:  Threaded.

e. Stem:  Bronze.

f. Disc:  PTFE or TFE.

g. Packing:  Asbestos free.

h. Handwheel:  Malleable iron[, bronze, or aluminum].

2.18 IRON GLOBE VALVES

Retain one or both paragraphs in this article if iron globe valves are required.  MSS SP-85 covers iron globe valves NPS 2 to NPS 12 (DN 50 to DN 300).

A. Class 125, Iron Globe Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Kitz Corporation.

f. Milwaukee Valve Company.

g. NIBCO INC.

h. Powell Valves.

i. Red-White Valve Corporation.

j. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

k. Zy-Tech Global Industries, Inc.

l. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-85, Type I.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 126, gray iron with bolted bonnet.

d. Ends:  Flanged.

e. Trim:  Bronze.

f. Packing and Gasket:  Asbestos free.

B. Class 250, Iron Globe Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Crane Co.; Crane Valve Group; Crane Valves.

b. Crane Co.; Crane Valve Group; Jenkins Valves.

c. Crane Co.; Crane Valve Group; Stockham Division.

d. Hammond Valve.

e. Milwaukee Valve Company.

f. NIBCO INC.

g. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

h. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-85, Type I.

b. CWP Rating:  500 psig (3450 kPa).

c. Body Material:  ASTM A 126, gray iron with bolted bonnet.

d. Ends:  Flanged.

e. Trim:  Bronze.

f. Packing and Gasket:  Asbestos free.

2.19 LUBRICATED PLUG VALVES

Retain one or more of eight paragraphs in this article if lubricated plug valves are required.  MSS SP-78 covers lubricated plug valves NPS 1 to NPS 24 (DN 25 to DN 600).

A. Class 125, Regular-Gland, Lubricated Plug Valves with Threaded Ends:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Nordstrom Valves, Inc.

b. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-78, Type II.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

d. Pattern:  [Regular or short] [Venturi] <Insert pattern>.

e. Plug:  Cast iron or bronze with sealant groove.

B. Class 125, Regular-Gland, Lubricated Plug Valves with Flanged Ends:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Nordstrom Valves, Inc.

b. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-78, Type II.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

d. Pattern:  [Regular or short] [Venturi] <Insert pattern>.

e. Plug:  Cast iron or bronze with sealant groove.

C. Class 125, Cylindrical, Lubricated Plug Valves with Threaded Ends:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Homestead Valve; a division of Olson Technologies, Inc.

b. Milliken Valve Company.

c. R & M Energy Systems; a unit of Robbins & Myers, Inc.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-78, Type IV.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

d. Pattern:  [Regular or short] [Venturi] <Insert pattern>.

e. Plug:  Cast iron or bronze with sealant groove.

D. Class 125, Cylindrical, Lubricated Plug Valves with Flanged Ends:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Homestead Valve; a division of Olson Technologies, Inc.

b. Milliken Valve Company.

c. R & M Energy Systems; a unit of Robbins & Myers, Inc.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-78, Type IV.

b. CWP Rating:  200 psig (1380 kPa).

c. Body Material:  ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

d. Pattern:  [Regular or short] [Venturi] <Insert pattern>.

e. Plug:  Cast iron or bronze with sealant groove.

E. Class 250, Regular-Gland, Lubricated Plug Valves with Threaded Ends:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Nordstrom Valves, Inc.

b. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-78, Type II.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Material:  ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

d. Pattern:  [Regular or short] [Venturi] <Insert pattern>.

e. Plug:  Cast iron or bronze with sealant groove.

F. Class 250, Regular-Gland, Lubricated Plug Valves with Flanged Ends:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Nordstrom Valves, Inc.

b. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-78, Type II.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Material:  ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

d. Pattern:  [Regular or short] [Venturi] <Insert pattern>.

e. Plug:  Cast iron or bronze with sealant groove.

G. Class 250, Cylindrical, Lubricated Plug Valves with Threaded Ends:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Homestead Valve; a division of Olson Technologies, Inc.

b. Milliken Valve Company.

c. R & M Energy Systems; a unit of Robbins & Myers, Inc.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-78, Type IV.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Material:  ASTM A 48/A 48M or ASTM A 126, cast iron with lubrication-sealing system.

d. Pattern:  [Regular or short] [Venturi] <Insert pattern>.

e. Plug:  Cast iron or bronze with sealant groove.

H. Class 250, Cylindrical, Lubricated Plug Valves with Flanged Ends:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Homestead Valve; a division of Olson Technologies, Inc.

b. Milliken Valve Company.

c. R & M Energy Systems; a unit of Robbins & Myers, Inc.

d. <Insert manufacturer's name>.

2. Description:

a. Standard:  MSS SP-78, Type IV.

b. CWP Rating:  400 psig (2760 kPa).

c. Body Material:  ASTM A 48/A 48M or ASTM A 126, Grade 40 cast iron with lubrication-sealing system.

d. Pattern:  [Regular or short] [Venturi] <Insert pattern>.

e. Plug:  Cast iron or bronze with sealant groove.

2.20 CHAINWHEELS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 1 Section "Product Requirements."

A. Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Babbitt Steam Specialty Co.

2. Roto Hammer Industries.

3. Trumbull Industries.

4. <Insert manufacturer's name>.

B. Description:  Valve actuation assembly with sprocket rim, brackets, and chain.

1. Brackets:  Type, number, size, and fasteners required to mount actuator on valve.

Retain first subparagraph below for ball, butterfly, and plug valves.

2. Attachment:  For connection to [ball] [butterfly] [and] [plug] valve stems.

Retain only ductile iron in first subparagraph below unless another material is required.

3. Sprocket Rim with Chain Guides:  [Ductile iron] [Ductile or cast iron] [Cast iron] [Aluminum] [Bronze], of type and size required for valve.[  Include zinc coating.]

Retain only first option in subparagraph below unless another material is required.

4. Chain:  [Hot-dip, galvanized steel] [Brass] [Stainless steel], of size required to fit sprocket rim.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine valve interior for cleanliness, freedom from foreign matter, and corrosion.  Remove special packing materials, such as blocks, used to prevent disc movement during shipping and handling.

B. Operate valves in positions from fully open to fully closed.  Examine guides and seats made accessible by such operations.

C. Examine threads on valve and mating pipe for form and cleanliness.

D. Examine mating flange faces for conditions that might cause leakage.  Check bolting for proper size, length, and material.  Verify that gasket is of proper size, that its material composition is suitable for service, and that it is free from defects and damage.

E. Do not attempt to repair defective valves; replace with new valves.

3.2 VALVE INSTALLATION

A. Install valves with unions or flanges at each piece of equipment arranged to allow service, maintenance, and equipment removal without system shutdown.

B. Locate valves for easy access and provide separate support where necessary.

C. Install valves in horizontal piping with stem at or above center of pipe.

D. Install valves in position to allow full stem movement.

E. Install chainwheels on operators for [ball] [butterfly] [gate] [globe] [and] [plug] valves [NPS 4 (DN 100)] <Insert size> and larger and more than [96 inches (2400 mm)] <Insert dimension> above floor.  Extend chains to [60 inches (1520 mm)] <Insert dimension> above finished floor.

F. Install check valves for proper direction of flow and as follows:

Revise check valve installation requirements to suit Project; delete those not required.

1. Swing Check Valves:  In horizontal position with hinge pin level.

2. [Center-Guided] [and] [Plate-Type] Check Valves:  In horizontal or vertical position, between flanges.

3. Lift Check Valves:  With stem upright and plumb.

3.3 ADJUSTING

A. Adjust or replace valve packing after piping systems have been tested and put into service but before final adjusting and balancing.  Replace valves if persistent leaking occurs.

3.4 GENERAL REQUIREMENTS FOR VALVE APPLICATIONS

The Section Text is arranged to provide bronze or brass valves in NPS 2 (DN 50) and smaller and iron valves in NPS 2-1/2 to NPS 12 (DN 65 to DN 300).

Caution:  Verify that valve classes and pressure and temperature ratings are adequate for system fluid.  Repeat each category listing if necessary and insert required pressure range for each listing.  Indicate location of each different pressure system on Drawings.

Retain and revise valve applications in paragraphs and schedules below.  Coordinate with valves specified in Part 2.

A. If valve applications are not indicated, use the following:

1. Shutoff Service:  Ball, butterfly[, or gate] [, gate, or plug] valves.

2. Butterfly Valve Dead-End Service:  Single-flange (lug) type.

3. Throttling Service:  [Globe] [Globe or angle] [or ball] [or butterfly] [, ball, or butterfly] valves.

4. Pump-Discharge Check Valves:

a. NPS 2 (DN 50) and Smaller:  Bronze swing check valves with [bronze] [or] [nonmetallic] disc.

b. NPS 2-1/2 (DN 65) and Larger for Domestic Water:  Iron swing check valves with lever and weight or with spring or iron, center-guided, [metal] [or] [resilient]-seat check valves.

c. NPS 2-1/2 (DN 65) and Larger for Sanitary Waste and Storm Drainage:  Iron swing check valves with lever and weight or spring.

B. If valves with specified SWP classes or CWP ratings are not available, the same types of valves with higher SWP classes or CWP ratings may be substituted.

C. Select valves, except wafer types, with the following end connections:

1. For Copper Tubing, NPS 2 (DN 50) and Smaller:  Threaded ends except where solder-joint valve-end option is indicated in valve schedules below.

2. For Copper Tubing, NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Flanged ends except where threaded valve-end option is indicated in valve schedules below.

3. For Copper Tubing, NPS 5 (DN 125) and Larger:  Flanged ends.

4. For Steel Piping, NPS 2 (DN 50) and Smaller:  Threaded ends.

5. For Steel Piping, NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  Flanged ends except where threaded valve-end option is indicated in valve schedules below.

6. For Steel Piping, NPS 5 (DN 125) and Larger:  Flanged ends.

7. For Grooved-End [Copper Tubing] [and] [Steel Piping]:  Valve ends may be grooved.

3.5 LOW-PRESSURE, COMPRESSED-AIR VALVE SCHEDULE (150 PSIG (1035 kPa) OR LESS)

A. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

1. Bronze[ and Brass] Valves:  May be provided with solder-joint ends instead of threaded ends.

Retain only valve types, in four subparagraphs below, required for Project.

Caution:  No one-piece, reduced-port, brass ball valves with stainless-steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text.  Retain brass or stainless-steel trim with brass ball valves, or bronze or stainless-steel trim with bronze ball valves.

2. Ball Valves:  [One] [Two] [Three] piece, [full] [regular] [reduced] port, [brass] [or] [bronze] with [brass] [bronze] [stainless-steel] trim.

Retain one of first two subparagraphs below, or retain both and indicate location of each type on Drawings.

3. Bronze Lift Check Valves:  Class 125, [bronze] [nonmetallic] disc.

4. Bronze Swing Check Valves:  [Class 125] [Class 150], [bronze] [nonmetallic] disc.

5. Bronze Gate Valves:  [Class 125] [Class 150], [NRS] [RS].

B. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

1. Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  May be provided with threaded ends instead of flanged ends.

Retain only valve types, in seven subparagraphs below, required for Project.

Retain one of first two subparagraphs below, or retain both and indicate location of each type on Drawings.

2. Iron, Single-Flange Butterfly Valves:  200 CWP, NBR seat, [aluminum-bronze] [ductile-iron] [stainless-steel] disc.

3. Iron, Grooved-End Butterfly Valves:  [175] [300] CWP.

Retain one or more of first four subparagraphs below and indicate location of each type on Drawings.

4. Iron Swing Check Valves:  [Class 125] [Class 250], [metal] [nonmetallic-to-metal] seats.

5. Iron, Grooved-End Swing Check Valves:  300 CWP.

6. Iron, Center-Guided Check Valves:  [Class 125] [Class 150] [Class 250] [Class 300], [compact-wafer] [globe], [metal] [resilient] seat.

Caution:  No iron, single-plate, metal-seated check valves or Class 150 or Class 300, resilient-seated, single-plate check valves are included in this Section.

7. Iron, Plate-Type Check Valves:  [Class 125] [Class 150] [Class 250] [Class 300]; [single] [dual] plate; [metal] [resilient] seat.

8. Iron Gate Valves:  [Class 125] [Class 250], [NRS] [OS&Y].

3.6 HIGH-PRESSURE, COMPRESSED-AIR VALVE SCHEDULE (150 TO 200 PSIG (1035 TO 1380 kPa))

A. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

1. Bronze[ and Brass] Valves:  May be provided with solder-joint ends instead of threaded ends.

Caution:  No one-piece, reduced-port, brass ball valves with stainless-steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text.  Retain brass or stainless-steel trim with brass ball valves, or bronze or stainless-steel trim with bronze ball valves.

2. Ball Valves:  [One] [Two] [Three] piece, [full] [regular] [reduced] port, [brass] [or] [bronze] with [brass] [bronze] [stainless-steel] trim.

Retain one of first two subparagraphs below, or retain both and indicate location of each type on Drawings.

3. Bronze Lift Check Valves:  Class 125, [bronze] [nonmetallic] disc.

4. Bronze Swing Check Valves:  [Class 125] [Class 150], [bronze] [nonmetallic] disc.

5. Bronze Gate Valves:  [Class 125] [Class 150], [NRS] [RS].

B. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

1. Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  May be provided with threaded ends instead of flanged ends.

Retain only valve types, in seven subparagraphs below, required for Project.

Retain one of first two subparagraphs below, or retain both and indicate location of each type on Drawings.

2. Iron, Single-Flange Butterfly Valves:  200 CWP, NBR seat, [aluminum-bronze] [ductile-iron] [stainless-steel] disc.

3. Iron, Grooved-End Butterfly Valves:  [175] [300] CWP.

Retain one or more of first four subparagraphs below and indicate location of each type on Drawings.

4. Iron Swing Check Valves:  [Class 125] [Class 250], [metal] [nonmetallic-to-metal] seats.

5. Iron, Grooved-End Swing Check Valves:  300 CWP.

6. Iron, Center-Guided Check Valves:  [Class 125] [Class 150] [Class 250] [Class 300], [compact-wafer] [globe], [metal] [resilient] seat.

Caution:  No iron, single-plate, metal-seated check valves or Class 150 or Class 300, resilient-seated, single-plate check valves are included in this Section.

7. Iron, Plate-Type Check Valves:  [Class 125] [Class 150] [Class 250] [Class 300]; [single] [dual] plate; [metal] [resilient] seat.

8. Iron Gate Valves:  [Class 125] [Class 250], [NRS] [OS&Y].

3.7 DOMESTIC, HOT- AND COLD-WATER VALVE SCHEDULE

A. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

1. Bronze[ and Brass] Valves:  May be provided with solder-joint ends instead of threaded ends.

Retain only valve types, in five subparagraphs below, required for Project.

2. Bronze Angle Valves:  [Class 125] [Class 150], [bronze] [nonmetallic] disc.

Caution:  No one-piece, reduced-port, brass ball valves with stainless-steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text.  Retain brass or stainless-steel trim with brass ball valves, or bronze or stainless-steel trim with bronze ball valves.

3. Ball Valves:  [One] [Two] [Three] piece, [full] [regular] [reduced] port, [brass] [or] [bronze] with [brass] [bronze] [stainless-steel] trim.

4. Bronze Swing Check Valves:  [Class 125] [Class 150], [bronze] [nonmetallic] disc.

5. Bronze Gate Valves:  [Class 125] [Class 150], [NRS] [RS].

6. Bronze Globe Valves:  [Class 125] [Class 150], [bronze] [nonmetallic] disc.

B. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

1. Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  May be provided with threaded ends instead of flanged ends.

Retain only valve types, in 10 subparagraphs below, required for Project.

2. Iron Ball Valves:  Class 150.

Retain one of first two subparagraphs below, or retain both and indicate location of each type on Drawings.

3. Iron, Single-Flange Butterfly Valves:  200 CWP, [EPDM] [NBR] seat, [aluminum-bronze] [ductile-iron] [stainless-steel] disc.

4. Iron, Grooved-End Butterfly Valves:  [175] [300] CWP.

Retain one or more of first five subparagraphs below and indicate location of each type on Drawings.

5. Iron Swing Check Valves:  [Class 125] [Class 250], [metal] [nonmetallic-to-metal] seats.

6. Iron Swing Check Valves with Closure Control:  Class 125, lever and [spring] [weight].

7. Iron, Grooved-End Swing Check Valves:  300 CWP.

8. Iron, Center-Guided Check Valves:  [Class 125] [Class 150] [Class 250] [Class 300], [compact-wafer] [globe], [metal] [resilient] seat.

Caution:  No iron, single-plate, metal-seated check valves or Class 150 or Class 300, resilient-seated, single-plate check valves are included in this Section.

9. Iron, Plate-Type Check Valves:  [Class 125] [Class 150] [Class 250] [Class 300]; [single] [dual] plate; [metal] [resilient] seat.

10. Iron Gate Valves:  [Class 125] [Class 250], [NRS] [OS&Y].

11. Iron Globe Valves:  [Class 125] [Class 250].

3.8 [SANITARY-WASTE] [AND] [STORM-DRAINAGE] VALVE SCHEDULE

A. Pipe NPS 2 (DN 50) and Smaller:

Retain first subparagraph below if solder-joint valve ends are permitted for this application.

1. Bronze[ and Brass] Valves:  May be provided with solder-joint ends instead of threaded ends.

Retain only valve types, in five subparagraphs below, required for Project.

2. Bronze Angle Valves:  [Class 125] [Class 150], [bronze] [nonmetallic] [stainless-steel] disc.

Caution:  No one-piece, reduced-port, brass ball valves with stainless-steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text.  Retain brass or stainless-steel trim with brass ball valves, or bronze or stainless-steel trim with bronze ball valves.

3. Ball Valves:  [One] [Two] [Three] piece, [full] [regular] [reduced] port, [brass] [or] [bronze] with [brass] [bronze] [stainless-steel] trim.

4. Bronze Swing Check Valves:  [Class 125] [Class 150], [bronze] [nonmetallic] disc.

5. Bronze Gate Valves:  [Class 125] [Class 150], [NRS] [RS].

6. Bronze Globe Valves:  [Class 125] [Class 150], [bronze] [nonmetallic] disc.

B. Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

1. Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100):  May be provided with threaded ends instead of flanged ends.

Retain only valve types, in seven subparagraphs below, required for Project.

2. Iron Ball Valves:  Class 150.

Retain one or more of first three subparagraphs below and indicate location of each type on Drawings.

3. Iron Swing Check Valves:  [Class 125] [Class 250], [metal] [nonmetallic-to-metal] seats.

4. Iron Swing Check Valves with Closure Control:  Class 125, lever and [spring] [weight].

5. Iron, Grooved-End Swing Check Valves:  300 CWP.

6. Iron Gate Valves:  [Class 125] [Class 250], [NRS] [OS&Y].

7. Iron Globe Valves:  [Class 125] [Class 250].

8. Lubricated Plug Valves:  [Class 125] [Class 250], [regular gland] [cylindrical], [threaded] [flanged].

END OF SECTION 15111

GENERAL-DUTY VALVES FOR PLUMBING PIPING
15111 - 1

